## Thickness
2025 |  | RF - REFRACTORY; RT - RECESSED TUBE; | [67 empty] | OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. THICKNESS MEASUREMENTS ARE IN INCHES. | [67 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | AVG | MIN
B | POSITION A | L | 29: 0.208; 30: 0.203; 31: 0.212; 32: 0.201; 33: 0.202; 34: 0.202
0.099 | OF THE | C | 29: 0.207; 30: 0.212; 31: 0.206; 32: 0.205; 33: 0.205; 34: 0.209
| MANWAY | R | 29: 0.205; 30: 0.195; 31: 0.217; 32: 0.204; 33: 0.209; 34: 0.206
B | POSITION B | L | 29: 0.201; 30: 0.194; 31: 0.202; 32: 0.213; 33: 0.218; 34: 0.207
0.099 | OF THE | C | 29: 0.208; 30: 0.2; 31: 0.209; 32: 0.2; 33: 0.211; 34: 0.209
| MANWAY | R | 29: 0.205; 30: 0.207; 31: 0.213; 32: 0.208; 33: 0.212; 34: 0.193
B | POSITION C | L | 29: 0.197; 30: 0.198; 31: 0.201; 32: 0.211; 33: 0.212; 34: 0.214
0.099 | OF THE | C | 29: 0.203; 30: 0.198; 31: 0.21; 32: 0.204; 33: 0.217; 34: 0.208
| MANWAY | R | 29: 0.197; 30: 0.199; 31: 0.209; 32: 0.2; 33: 0.203; 34: 0.2
B | POSITION D | L | 29: 0.21; 30: 0.197; 31: 0.202; 32: 0.206; 33: 0.214; 34: 0.204
0.099 | OF THE | C | 29: 0.212; 30: 0.201; 31: 0.203; 32: 0.201; 33: 0.213; 34: 0.206
| MANWAY | R | 29: 0.209; 30: 0.201; 31: 0.207; 32: 0.192; 33: 0.213; 34: 0.196
B | POSITION E | L | 29: 0.18; 30: 0.205; 31: 0.215; 32: 0.199; 33: 0.205; 34: 0.197
0.099 | OF THE | C | 29: 0.211; 30: 0.196; 31: 0.216; 32: 0.212; 33: 0.211; 34: 0.203
| MANWAY | R | 29: 0.199; 30: 0.198; 31: 0.206; 32: 0.197; 33: 0.197; 34: 0.203
B | POSITION A | L | 18: 0.172; 19: 0.165; 20: 0.184; 21: 0.179; 22: 0.166; 23: 0.175; 40: 0.179; 41: 0.165; 42: 0.185; 43: 0.173; 44: 0.169; 45: 0.173
0.099 | OF THE | C | 18: 0.182; 19: 0.164; 20: 0.175; 21: 0.183; 22: 0.161; 23: 0.177; 40: 0.173; 41: 0.168; 42: 0.185; 43: 0.173; 44: 0.164; 45: 0.176
| TERTIARIES | R | 18: 0.176; 19: 0.17; 20: 0.174; 21: 0.177; 22: 0.165; 23: 0.174; 40: 0.176; 41: 0.17; 42: 0.177; 43: 0.179; 44: 0.168; 45: 0.181
B | POSITION B | L | 18: 0.179; 19: RT; 20: 0.175; 21: 0.174; 22: RT; 23: 0.173; 40: 0.178; 41: RT; 42: 0.178; 43: 0.176; 44: RT; 45: 0.193
0.099 | OF THE | C | 18: 0.171; 19: RT; 20: 0.182; 21: 0.174; 22: RT; 23: 0.176; 40: 0.181; 41: RT; 42: 0.178; 43: 0.178; 44: RT; 45: 0.18
| TERTIARIES | R | 18: 0.173; 19: RT; 20: 0.173; 21: 0.176; 22: RT; 23: 0.174; 40: 0.179; 41: RT; 42: 0.18; 43: 0.175; 44: RT; 45: 0.181
B | POSITION C | L | 18: 0.182; 19: 0.174; 20: 0.184; 21: 0.178; 22: 0.166; 23: 0.175; 40: 0.18; 41: 0.171; 42: 0.181; 43: 0.176; 44: 0.169; 45: 0.177
0.099 | OF THE | C | 18: 0.178; 19: 0.167; 20: 0.176; 21: 0.179; 22: 0.171; 23: 0.181; 40: 0.18; 41: 0.167; 42: 0.177; 43: 0.18; 44: 0.165; 45: 0.181
| TERTIARIES | R | 18: 0.174; 19: 0.166; 20: 0.175; 21: 0.181; 22: 0.169; 23: 0.175; 40: 0.185; 41: 0.169; 42: 0.175; 43: 0.178; 44: 0.167; 45: 0.177
A |  | L | 0.329 | 0.231 | 0.228 | 0.236 | 0.225 | 0.239 | 0.225 | 0.23 | 0.226 | 0.224 | 0.229 | 0.232 | 0.236 | 0.226 | 0.225 | 0.267 | 0.335 | 0.333 | 0.276 | 0.229 | 0.232 | 0.229 | 0.228 | 0.235 | 0.228 | 0.224 | 0.233 | 0.229 | 0.229 | 0.233 | 0.231 | 0.226 | 0.227 | 0.227 | 0.234 | 0.229 | 0.222 | 0.221 | 0.223 | 0.233 | 0.228 | 0.222 | 0.226 | 0.221 | 0.268 | 0.327 | 0.334 | 0.266 | 0.216 | 0.224 | 0.223 | 0.223 | 0.221 | 0.224 | 0.23 | 0.233 | 0.218 | 0.225 | 0.213 | 0.225 | 0.23 | RF | RF
0.083 | +16 FT 6 IN | C | 0.334 | 0.23 | 0.226 | 0.225 | 0.227 | 0.236 | 0.227 | 0.229 | 0.23 | 0.229 | 0.222 | 0.233 | 0.228 | 0.227 | 0.217 | 0.265 | 0.337 | 0.333 | 0.266 | 0.229 | 0.23 | 0.225 | 0.23 | 0.232 | 0.23 | 0.223 | 0.229 | 0.229 | 0.231 | 0.227 | 0.235 | 0.227 | 0.227 | 0.23 | 0.227 | 0.223 | 0.229 | 0.231 | 0.222 | 0.231 | 0.229 | 0.225 | 0.225 | 0.218 | 0.265 | 0.324 | 0.329 | 0.269 | 0.21 | 0.23 | 0.23 | 0.221 | 0.225 | 0.226 | 0.228 | 0.223 | 0.213 | 0.211 | 0.225 | 0.225 | 0.223 | RF | RF
|  | R | 0.326 | 0.232 | 0.227 | 0.222 | 0.224 | 0.234 | 0.226 | 0.231 | 0.228 | 0.232 | 0.221 | 0.229 | 0.228 | 0.229 | 0.213 | 0.267 | 0.34 | 0.354 | 0.269 | 0.236 | 0.232 | 0.229 | 0.224 | 0.229 | 0.233 | 0.226 | 0.226 | 0.229 | 0.225 | 0.229 | 0.227 | 0.214 | 0.228 | 0.229 | 0.227 | 0.23 | 0.228 | 0.233 | 0.226 | 0.231 | 0.231 | 0.223 | 0.226 | 0.229 | 0.269 | 0.328 | 0.329 | 0.272 | 0.211 | 0.226 | 0.227 | 0.222 | 0.226 | 0.228 | 0.227 | 0.229 | 0.225 | 0.225 | 0.229 | 0.231 | 0.231 | RF | RF
A |  | L | RF | RF | 0.229 | 0.22 | 0.223 | 0.222 | 0.228 | 0.229 | 0.227 | 0.225 | 0.217 | 0.226 | 0.223 | 0.224 | 0.226 | 0.268 | 0.335 | 0.339 | 0.269 | 0.224 | 0.229 | 0.226 | 0.225 | 0.226 | 0.23 | 0.222 | 0.226 | 0.228 | 0.224 | 0.23 | 0.229 | 0.238 | 0.222 | 0.224 | 0.229 | 0.229 | 0.227 | 0.227 | 0.224 | 0.228 | 0.226 | 0.228 | 0.227 | 0.223 | 0.265 | 0.329 | 0.326 | 0.263 | 0.224 | 0.22 | 0.229 | 0.221 | 0.22 | 0.226 | 0.227 | 0.227 | 0.226 | 0.218 | 0.227 | 0.226 | 0.224 | 0.233 | RF
0.083 | +15 FT | C | RF | 0.221 | 0.224 | 0.221 | 0.217 | 0.217 | 0.22 | 0.222 | 0.229 | 0.228 | 0.215 | 0.227 | 0.228 | 0.22 | 0.228 | 0.268 | 0.333 | 0.337 | 0.272 | 0.225 | 0.222 | 0.229 | 0.223 | 0.227 | 0.225 | 0.221 | 0.224 | 0.228 | 0.221 | 0.23 | 0.227 | 0.231 | 0.223 | 0.219 | 0.225 | 0.225 | 0.219 | 0.222 | 0.221 | 0.227 | 0.227 | 0.228 | 0.225 | 0.227 | 0.266 | 0.329 | 0.317 | 0.259 | 0.22 | 0.228 | 0.222 | 0.217 | 0.225 | 0.225 | 0.226 | 0.226 | 0.229 | 0.217 | 0.228 | 0.224 | 0.227 | 0.23 | RF
|  | R | RF | 0.221 | 0.229 | 0.223 | 0.22 | 0.216 | 0.217 | 0.228 | 0.226 | 0.221 | 0.214 | 0.226 | 0.226 | 0.218 | 0.226 | 0.269 | 0.327 | 0.337 | 0.272 | 0.223 | 0.226 | 0.225 | 0.23 | 0.222 | 0.228 | 0.212 | 0.225 | 0.229 | 0.219 | 0.229 | 0.231 | 0.233 | 0.224 | 0.225 | 0.223 | 0.224 | 0.221 | 0.228 | 0.22 | 0.226 | 0.226 | 0.228 | 0.228 | 0.224 | 0.267 | 0.33 | 0.319 | 0.262 | 0.216 | 0.224 | 0.219 | 0.224 | 0.213 | 0.228 | 0.221 | 0.225 | 0.219 | 0.219 | 0.224 | 0.228 | 0.231 | 0.229 | RF
A |  | L | 0.306 | 0.214 | 0.222 | 0.22 | 0.219 | 0.212 | 0.226 | 0.224 | 0.218 | 0.23 | 0.228 | 0.223 | 0.23 | 0.226 | 0.229 | 0.262 | 0.333 | 0.331 | 0.264 | 0.221 | 0.22 | 0.228 | 0.231 | 0.224 | 0.228 | 0.228 | 0.234 | 0.227 | 0.229 | 0.231 | 0.235 | 0.231 | 0.229 | 0.227 | 0.233 | 0.233 | 0.232 | 0.227 | 0.219 | 0.225 | 0.225 | 0.234 | 0.231 | 0.222 | 0.268 | 0.325 | 0.326 | 0.265 | 0.228 | 0.226 | 0.221 | 0.213 | 0.218 | 0.221 | 0.224 | 0.226 | 0.22 | 0.227 | 0.229 | 0.23 | 0.223 | 0.227 | RF
0.083 | +13 FT 6 IN | C | 0.305 | 0.21 | 0.227 | 0.229 | 0.221 | 0.229 | 0.227 | 0.223 | 0.217 | 0.226 | 0.223 | 0.229 | 0.227 | 0.221 | 0.234 | 0.271 | 0.34 | 0.339 | 0.272 | 0.225 | 0.222 | 0.227 | 0.228 | 0.22 | 0.23 | 0.227 | 0.233 | 0.226 | 0.228 | 0.227 | 0.232 | 0.23 | 0.225 | 0.221 | 0.23 | 0.221 | 0.229 | 0.221 | 0.225 | 0.226 | 0.224 | 0.226 | 0.23 | 0.218 | 0.266 | 0.327 | 0.324 | 0.268 | 0.223 | 0.222 | 0.228 | 0.213 | 0.223 | 0.225 | 0.228 | 0.221 | 0.222 | 0.228 | 0.23 | 0.216 | 0.225 | 0.226 | RF
|  | R | 0.309 | 0.212 | 0.224 | 0.224 | 0.217 | 0.228 | 0.224 | 0.222 | 0.219 | 0.224 | 0.216 | 0.227 | 0.224 | 0.221 | 0.231 | 0.263 | 0.333 | 0.33 | 0.268 | 0.23 | 0.222 | 0.223 | 0.22 | 0.215 | 0.228 | 0.223 | 0.224 | 0.229 | 0.231 | 0.225 | 0.234 | 0.229 | 0.224 | 0.228 | 0.225 | 0.219 | 0.229 | 0.225 | 0.227 | 0.223 | 0.233 | 0.227 | 0.23 | 0.224 | 0.274 | 0.331 | 0.321 | 0.268 | 0.232 | 0.23 | 0.22 | 0.218 | 0.22 | 0.224 | 0.221 | 0.22 | 0.224 | 0.229 | 0.225 | 0.223 | 0.226 | 0.227 | RF
A |  | L | 0.297 | 0.215 | 0.223 | 0.218 | 0.224 | 0.219 | 0.217 | 0.221 | 0.216 | 0.219 | 0.22 | 0.219 | 0.221 | 0.214 | 0.218 | 0.261 | 0.32 | 0.312 | 0.261 | 0.221 | 0.217 | 0.214 | 0.224 | 0.222 | 0.216 | 0.212 | 0.222 | 0.223 | 0.222 | 0.223 | 0.219 | 0.229 | 0.226 | 0.226 | 0.226 | 0.224 | 0.219 | 0.221 | 0.226 | 0.213 | 0.211 | 0.216 | 0.225 | 0.217 | 0.265 | 0.317 | 0.319 | 0.258 | 0.208 | 0.211 | 0.224 | 0.217 | 0.212 | 0.224 | 0.224 | 0.221 | 0.22 | 0.226 | 0.228 | 0.231 | 0.225 | 0.221 | RF
0.083 | +12 FT | C | 0.301 | 0.215 | 0.22 | 0.226 | 0.221 | 0.218 | 0.219 | 0.227 | 0.219 | 0.218 | 0.217 | 0.221 | 0.219 | 0.214 | 0.214 | 0.261 | 0.324 | 0.322 | 0.263 | 0.222 | 0.221 | 0.216 | 0.223 | 0.227 | 0.223 | 0.209 | 0.223 | 0.227 | 0.226 | 0.218 | 0.22 | 0.229 | 0.228 | 0.233 | 0.225 | 0.226 | 0.216 | 0.219 | 0.222 | 0.219 | 0.219 | 0.218 | 0.226 | 0.225 | 0.264 | 0.322 | 0.323 | 0.259 | 0.21 | 0.217 | 0.225 | 0.212 | 0.218 | 0.224 | 0.228 | 0.224 | 0.222 | 0.231 | 0.228 | 0.229 | 0.224 | 0.211 | RF
|  | R | 0.309 | 0.218 | 0.214 | 0.229 | 0.219 | 0.223 | 0.212 | 0.219 | 0.216 | 0.214 | 0.218 | 0.221 | 0.221 | 0.217 | 0.219 | 0.258 | 0.323 | 0.315 | 0.257 | 0.223 | 0.218 | 0.222 | 0.22 | 0.227 | 0.224 | 0.216 | 0.225 | 0.224 | 0.226 | 0.22 | 0.223 | 0.233 | 0.222 | 0.228 | 0.227 | 0.217 | 0.218 | 0.221 | 0.219 | 0.217 | 0.218 | 0.221 | 0.226 | 0.219 | 0.268 | 0.325 | 0.326 | 0.256 | 0.214 | 0.214 | 0.22 | 0.216 | 0.215 | 0.225 | 0.225 | 0.226 | 0.229 | 0.228 | 0.225 | 0.228 | 0.22 | 0.214 | RF
A | POSITION A | L | 3: 0.217; 4: 0.203; 5: 0.223; 6: 0.216; 58: 0.217; 59: 0.226; 60: 0.218; 61: 0.22
0.083 | OF THE | C | 3: 0.209; 4: 0.237; 5: 0.216; 6: 0.216; 58: 0.222; 59: 0.224; 60: 0.221; 61: 0.222
| OB PORTS | R | 3: 0.207; 4: 0.226; 5: 0.213; 6: 0.22; 58: 0.219; 59: 0.225; 60: 0.218; 61: 0.216
A | POSITION B | L | 3: 0.213; 4: 0.205; 5: 0.22; 6: 0.217; 58: 0.221; 59: 0.217; 60: 0.22; 61: 0.215
0.083 | OF THE | C | 3: 0.229; 4: 0.209; 5: 0.211; 6: 0.219; 58: 0.225; 59: 0.219; 60: 0.222; 61: 0.211
| OB PORTS | R | 3: 0.208; 4: 0.22; 5: 0.214; 6: 0.225; 58: 0.224; 59: 0.216; 60: 0.22; 61: 0.211
A | POSITION C | L | 3: 0.221; 4: 0.213; 5: 0.221; 6: 0.224; 58: 0.224; 59: 0.217; 60: 0.217; 61: 0.218
0.083 | OF THE | C | 3: 0.22; 4: 0.227; 5: 0.209; 6: 0.228; 58: 0.228; 59: 0.22; 60: 0.227; 61: 0.221
| OB PORTS | R | 3: 0.22; 4: 0.225; 5: 0.211; 6: 0.219; 58: 0.223; 59: 0.221; 60: 0.241; 61: 0.228
A |  | L | 0.325 | 0.214 | 0.22 | 0.22 | 0.22 | 0.219 | 0.214 | 0.207 | 0.213 | 0.214 | 0.21 | 0.214 | 0.211 | 0.212 | 0.207 | 0.245 | 0.312 | 0.318 | 0.259 | 0.222 | 0.218 | 0.213 | 0.21 | 0.216 | 0.212 | 0.221 | 0.221 | 0.218 | 0.223 | 0.226 | 0.224 | 0.223 | 0.221 | 0.223 | 0.22 | 0.222 | 0.21 | 0.218 | 0.217 | 0.215 | 0.216 | 0.217 | 0.224 | 0.221 | 0.259 | 0.327 | 0.324 | 0.265 | 0.22 | 0.227 | 0.219 | 0.222 | 0.219 | 0.224 | 0.22 | 0.223 | 0.224 | 0.229 | 0.227 | 0.226 | 0.228 | 0.228 | RF
0.083 | +10 FT 6 IN | C | 0.331 | 0.212 | 0.219 | 0.22 | 0.222 | 0.218 | 0.214 | 0.213 | 0.217 | 0.216 | 0.219 | 0.213 | 0.212 | 0.218 | 0.204 | 0.253 | 0.312 | 0.314 | 0.263 | 0.221 | 0.214 | 0.216 | 0.216 | 0.222 | 0.222 | 0.213 | 0.218 | 0.222 | 0.22 | 0.225 | 0.229 | 0.22 | 0.224 | 0.226 | 0.223 | 0.221 | 0.21 | 0.218 | 0.217 | 0.217 | 0.211 | 0.221 | 0.22 | 0.223 | 0.258 | 0.326 | 0.321 | 0.265 | 0.214 | 0.216 | 0.213 | 0.219 | 0.218 | 0.224 | 0.217 | 0.226 | 0.227 | 0.223 | 0.227 | 0.224 | 0.235 | 0.227 | RF
|  | R | 0.328 | 0.218 | 0.223 | 0.227 | 0.216 | 0.215 | 0.212 | 0.217 | 0.218 | 0.216 | 0.218 | 0.213 | 0.211 | 0.207 | 0.21 | 0.252 | 0.316 | 0.313 | 0.26 | 0.213 | 0.217 | 0.215 | 0.214 | 0.218 | 0.218 | 0.221 | 0.22 | 0.225 | 0.218 | 0.218 | 0.227 | 0.224 | 0.226 | 0.226 | 0.224 | 0.225 | 0.208 | 0.207 | 0.209 | 0.211 | 0.205 | 0.215 | 0.217 | 0.218 | 0.259 | 0.325 | 0.322 | 0.266 | 0.22 | 0.221 | 0.21 | 0.221 | 0.213 | 0.223 | 0.221 | 0.224 | 0.227 | 0.223 | 0.222 | 0.225 | 0.235 | 0.221 | RF
A |  | L | 0.311 | 0.21 | 0.222 | 0.219 | 0.216 | 0.219 | 0.223 | 0.217 | 0.215 | 0.212 | 0.208 | 0.215 | 0.209 | 0.214 | 0.203 | 0.241 | 0.315 | 0.312 | 0.252 | 0.206 | 0.207 | 0.204 | 0.209 | 0.208 | 0.198 | 0.217 | 0.213 | 0.209 | 0.214 | 0.224 | 0.222 | 0.225 | 0.216 | 0.219 | 0.215 | 0.214 | 0.212 | 0.22 | 0.22 | 0.216 | 0.219 | 0.222 | 0.202 | 0.215 | 0.258 | 0.312 | 0.316 | 0.256 | 0.227 | 0.216 | 0.22 | 0.217 | 0.219 | 0.218 | 0.22 | 0.224 | 0.227 | 0.229 | 0.227 | 0.216 | 0.225 | 0.211 | RF
0.083 | +9 FT | C | 0.311 | 0.205 | 0.218 | 0.221 | 0.219 | 0.225 | 0.229 | 0.221 | 0.219 | 0.22 | 0.215 | 0.214 | 0.211 | 0.214 | 0.207 | 0.249 | 0.314 | 0.309 | 0.254 | 0.204 | 0.21 | 0.211 | 0.205 | 0.21 | 0.207 | 0.211 | 0.202 | 0.216 | 0.215 | 0.22 | 0.222 | 0.221 | 0.225 | 0.216 | 0.219 | 0.218 | 0.218 | 0.216 | 0.215 | 0.224 | 0.209 | 0.224 | 0.213 | 0.214 | 0.259 | 0.317 | 0.322 | 0.259 | 0.226 | 0.218 | 0.223 | 0.218 | 0.22 | 0.219 | 0.222 | 0.224 | 0.227 | 0.227 | 0.218 | 0.22 | 0.225 | 0.205 | RF
|  | R | 0.314 | 0.21 | 0.221 | 0.214 | 0.215 | 0.22 | 0.223 | 0.215 | 0.22 | 0.217 | 0.214 | 0.213 | 0.208 | 0.213 | 0.204 | 0.25 | 0.315 | 0.31 | 0.251 | 0.205 | 0.206 | 0.209 | 0.205 | 0.205 | 0.207 | 0.209 | 0.203 | 0.217 | 0.215 | 0.218 | 0.224 | 0.218 | 0.218 | 0.219 | 0.215 | 0.215 | 0.214 | 0.216 | 0.214 | 0.214 | 0.212 | 0.216 | 0.208 | 0.206 | 0.254 | 0.321 | 0.319 | 0.25 | 0.219 | 0.223 | 0.217 | 0.218 | 0.221 | 0.225 | 0.223 | 0.227 | 0.231 | 0.227 | 0.218 | 0.225 | 0.227 | 0.202 | RF
A | POSITION A | L | 29: 0.225; 30: 0.223; 31: 0.224; 32: 0.221; 33: 0.219; 34: 0.224
0.083 | OF THE | C | 29: 0.219; 30: 0.222; 31: 0.221; 32: 0.226; 33: 0.216; 34: 0.219
| OSCILLATOR | R | 29: 0.219; 30: 0.208; 31: 0.218; 32: 0.23; 33: 0.228; 34: 0.221
A | POSTION B | L | 29: 0.229; 30: 0.223; 31: 0.225; 32: 0.223; 33: 0.219; 34: 0.219
0.083 | OF THE | C | 29: 0.221; 30: 0.216; 31: 0.226; 32: 0.214; 33: 0.217; 34: 0.224
| OSCILLATOR | R | 29: 0.219; 30: 0.214; 31: 0.228; 32: 0.222; 33: 0.218; 34: 0.225
A | POSITION C | L | 29: 0.217; 30: 0.23; 31: 0.216; 32: 0.222; 33: 0.22; 34: 0.224
0.083 | OF THE | C | 29: 0.216; 30: 0.223; 31: 0.225; 32: 0.225; 33: 0.216; 34: 0.221
| OSCILLATOR | R | 29: 0.219; 30: 0.216; 31: 0.225; 32: 0.217; 33: 0.215; 34: 0.221
A | POSITION D | L | 29: 0.226; 30: 0.216; 31: 0.225; 32: 0.232; 33: 0.214; 34: 0.22
0.083 | OF THE | C | 29: 0.213; 30: 0.22; 31: 0.224; 32: 0.222; 33: 0.216; 34: 0.211
| OSCILLATOR | R | 29: 0.212; 30: 0.216; 31: 0.222; 32: 0.218; 33: 0.222; 34: 0.214
A | POSITION E | L | 29: 0.216; 30: 0.216; 31: 0.233; 32: 0.216; 33: 0.218; 34: 0.216
0.083 | OF THE | C | 29: 0.211; 30: 0.219; 31: 0.224; 32: 0.219; 33: 0.221; 34: 0.222
| OSCILLATOR | R | 29: 0.213; 30: 0.22; 31: 0.217; 32: 0.224; 33: 0.221; 34: 0.219
A |  | L | 0.307 | 0.214 | 0.216 | 0.224 | 0.223 | 0.22 | 0.222 | 0.221 | 0.214 | 0.21 | 0.217 | 0.214 | 0.205 | 0.202 | 0.207 | 0.251 | 0.317 | 0.315 | 0.258 | 0.212 | 0.207 | 0.209 | 0.216 | 0.197 | 0.209 | 0.2 | 0.2 | 0.203 | 0.206 | 0.205 | 0.226 | 0.224 | 0.224 | 0.209 | 0.214 | 0.211 | 0.212 | 0.209 | 0.215 | 0.209 | 0.222 | 0.216 | 0.221 | 0.22 | 0.259 | 0.318 | 0.323 | 0.264 | 0.218 | 0.224 | 0.217 | 0.217 | 0.216 | 0.221 | 0.219 | 0.224 | 0.217 | 0.221 | 0.22 | 0.227 | 0.225 | 0.206 | 0.205
0.083 | +7 FT 6 IN | C | 0.314 | 0.214 | 0.216 | 0.221 | 0.225 | 0.217 | 0.221 | 0.222 | 0.214 | 0.217 | 0.218 | 0.215 | 0.21 | 0.209 | 0.214 | 0.254 | 0.315 | 0.318 | 0.256 | 0.216 | 0.213 | 0.211 | 0.214 | 0.207 | 0.209 | 0.199 | 0.205 | 0.21 | 0.208 | 0.207 | 0.224 | 0.226 | 0.22 | 0.209 | 0.219 | 0.215 | 0.216 | 0.209 | 0.213 | 0.208 | 0.217 | 0.211 | 0.219 | 0.213 | 0.257 | 0.31 | 0.326 | 0.263 | 0.217 | 0.227 | 0.215 | 0.215 | 0.215 | 0.212 | 0.218 | 0.224 | 0.215 | 0.216 | 0.225 | 0.223 | 0.217 | 0.225 | RF
|  | R | 0.309 | 0.211 | 0.216 | 0.219 | 0.221 | 0.21 | 0.217 | 0.22 | 0.212 | 0.21 | 0.212 | 0.21 | 0.205 | 0.212 | 0.214 | 0.248 | 0.317 | 0.315 | 0.253 | 0.207 | 0.212 | 0.207 | 0.207 | 0.2 | 0.212 | 0.203 | 0.205 | 0.208 | 0.21 | 0.209 | 0.223 | 0.225 | 0.217 | 0.208 | 0.215 | 0.204 | 0.216 | 0.206 | 0.21 | 0.213 | 0.218 | 0.215 | 0.216 | 0.215 | 0.257 | 0.314 | 0.32 | 0.265 | 0.224 | 0.217 | 0.221 | 0.213 | 0.215 | 0.214 | 0.219 | 0.221 | 0.214 | 0.217 | 0.229 | 0.223 | 0.219 | 0.226 | RF
A |  | L | 0.326 | 0.21 | 0.211 | 0.217 | 0.22 | 0.22 | 0.221 | 0.225 | 0.225 | 0.221 | 0.221 | 0.219 | 0.214 | 0.211 | 0.21 | 0.251 | 0.307 | 0.306 | 0.254 | 0.211 | 0.217 | 0.213 | 0.208 | 0.216 | 0.206 | 0.212 | 0.202 | 0.201 | 0.202 | 0.218 | 0.212 | 0.206 | 0.219 | 0.216 | 0.21 | 0.21 | 0.205 | 0.208 | 0.212 | 0.204 | 0.205 | 0.211 | 0.217 | 0.209 | 0.256 | 0.306 | 0.315 | 0.254 | 0.212 | 0.217 | 0.214 | 0.219 | 0.213 | 0.222 | 0.219 | 0.227 | 0.222 | 0.222 | 0.224 | 0.227 | 0.227 | 0.225 | 0.299
0.083 | +6 FT | C | 0.315 | 0.211 | 0.21 | 0.222 | 0.22 | 0.227 | 0.214 | 0.218 | 0.219 | 0.219 | 0.216 | 0.214 | 0.212 | 0.215 | 0.211 | 0.247 | 0.291 | 0.3 | 0.253 | 0.208 | 0.215 | 0.212 | 0.215 | 0.214 | 0.213 | 0.213 | 0.209 | 0.209 | 0.203 | 0.216 | 0.206 | 0.21 | 0.208 | 0.203 | 0.205 | 0.201 | 0.21 | 0.205 | 0.209 | 0.204 | 0.209 | 0.214 | 0.21 | 0.207 | 0.258 | 0.3 | 0.315 | 0.25 | 0.209 | 0.215 | 0.212 | 0.218 | 0.213 | 0.216 | 0.218 | 0.224 | 0.213 | 0.215 | 0.227 | 0.233 | 0.224 | 0.217 | 0.301
|  | R | 0.311 | 0.216 | 0.215 | 0.214 | 0.219 | 0.221 | 0.214 | 0.217 | 0.214 | 0.215 | 0.215 | 0.212 | 0.212 | 0.212 | 0.216 | 0.25 | 0.29 | 0.302 | 0.25 | 0.209 | 0.221 | 0.211 | 0.215 | 0.214 | 0.21 | 0.212 | 0.214 | 0.21 | 0.208 | 0.217 | 0.212 | 0.203 | 0.21 | 0.208 | 0.206 | 0.203 | 0.21 | 0.204 | 0.208 | 0.211 | 0.211 | 0.205 | 0.205 | 0.213 | 0.263 | 0.297 | 0.323 | 0.257 | 0.203 | 0.219 | 0.206 | 0.217 | 0.22 | 0.221 | 0.224 | 0.229 | 0.226 | 0.213 | 0.221 | 0.225 | 0.222 | 0.222 | 0.303
A |  | L | 0.292 | 0.206 | 0.219 | 0.227 | 0.221 | 0.22 | 0.233 | 0.222 | 0.229 | 0.21 | 0.221 | 0.216 | 0.219 | 0.221 | 0.213 | 0.255 | 0.277 | 0.309 | 0.258 | 0.215 | 0.219 | 0.218 | 0.216 | 0.216 | 0.215 | 0.216 | 0.212 | 0.218 | 0.212 | 0.214 | 0.213 | 0.213 | 0.207 | 0.204 | 0.21 | 0.211 | 0.205 | 0.202 | 0.209 | 0.209 | 0.214 | 0.209 | 0.209 | 0.21 | 0.249 | 0.298 | 0.309 | 0.255 | 0.212 | 0.212 | 0.216 | 0.219 | 0.212 | 0.223 | 0.217 | 0.219 | 0.218 | 0.227 | 0.217 | 0.221 | 0.229 | 0.225 | 0.319
0.083 | +4 FT 6 IN | C | 0.301 | 0.201 | 0.217 | 0.228 | 0.22 | 0.221 | 0.23 | 0.224 | 0.23 | 0.214 | 0.217 | 0.216 | 0.223 | 0.216 | 0.208 | 0.253 | 0.276 | 0.293 | 0.247 | 0.211 | 0.221 | 0.219 | 0.214 | 0.215 | 0.218 | 0.205 | 0.211 | 0.206 | 0.213 | 0.204 | 0.21 | 0.206 | 0.198 | 0.208 | 0.208 | 0.199 | 0.198 | 0.203 | 0.199 | 0.205 | 0.212 | 0.211 | 0.202 | 0.209 | 0.242 | 0.3 | 0.292 | 0.252 | 0.209 | 0.209 | 0.222 | 0.221 | 0.212 | 0.22 | 0.216 | 0.222 | 0.224 | 0.223 | 0.221 | 0.23 | 0.227 | 0.229 | 0.311
|  | R | 0.294 | 0.198 | 0.218 | 0.214 | 0.219 | 0.224 | 0.223 | 0.22 | 0.229 | 0.205 | 0.215 | 0.216 | 0.209 | 0.218 | 0.204 | 0.245 | 0.287 | 0.295 | 0.251 | 0.208 | 0.213 | 0.207 | 0.206 | 0.208 | 0.201 | 0.206 | 0.208 | 0.21 | 0.206 | 0.204 | 0.211 | 0.202 | 0.208 | 0.202 | 0.2 | 0.207 | 0.204 | 0.201 | 0.196 | 0.203 | 0.201 | 0.213 | 0.196 | 0.208 | 0.244 | 0.291 | 0.293 | 0.251 | 0.209 | 0.21 | 0.212 | 0.22 | 0.218 | 0.219 | 0.217 | 0.218 | 0.225 | 0.222 | 0.22 | 0.223 | 0.233 | 0.237 | 0.312
A |  | L | 0.296 | 0.205 | 0.218 | 0.218 | 0.214 | 0.216 | 0.216 | 0.216 | 0.222 | 0.22 | 0.219 | 0.22 | 0.216 | 0.213 | 0.217 | 0.255 | 0.314 | 0.325 | 0.259 | 0.218 | 0.22 | 0.218 | 0.212 | 0.207 | 0.221 | 0.222 | 0.224 | 0.217 | 0.217 | 0.226 | 0.214 | 0.208 | 0.207 | 0.214 | 0.218 | 0.21 | 0.22 | 0.215 | 0.202 | 0.204 | 0.213 | 0.207 | 0.206 | 0.198 | 0.235 | 0.282 | 0.276 | 0.239 | 0.213 | 0.212 | 0.213 | 0.218 | 0.204 | 0.211 | 0.214 | 0.216 | 0.214 | 0.206 | 0.22 | 0.22 | 0.222 | 0.237 | 0.303
0.083 | +3 FT | C | 0.305 | 0.225 | 0.212 | 0.214 | 0.224 | 0.215 | 0.219 | 0.22 | 0.222 | 0.217 | 0.22 | 0.22 | 0.217 | 0.211 | 0.21 | 0.248 | 0.303 | 0.303 | 0.256 | 0.224 | 0.217 | 0.232 | 0.195 | 0.208 | 0.214 | 0.206 | 0.209 | 0.2 | 0.211 | 0.206 | 0.215 | 0.21 | 0.195 | 0.214 | 0.218 | 0.207 | 0.196 | 0.199 | 0.192 | 0.197 | 0.193 | 0.183 | 0.186 | 0.182 | 0.223 | 0.256 | 0.26 | 0.226 | 0.202 | 0.201 | 0.212 | 0.206 | 0.202 | 0.208 | 0.217 | 0.211 | 0.219 | 0.214 | 0.223 | 0.218 | 0.222 | 0.223 | 0.312
|  | R | 0.31 | 0.214 | 0.212 | 0.223 | 0.213 | 0.211 | 0.221 | 0.223 | 0.221 | 0.202 | 0.216 | 0.206 | 0.23 | 0.202 | 0.216 | 0.23 | 0.298 | 0.288 | 0.249 | 0.213 | 0.219 | 0.204 | 0.207 | 0.205 | 0.195 | 0.218 | 0.199 | 0.197 | 0.201 | 0.195 | 0.198 | 0.2 | 0.188 | 0.192 | 0.204 | 0.203 | 0.188 | 0.18 | 0.191 | 0.186 | 0.187 | 0.176 | 0.196 | 0.181 | 0.212 | 0.273 | 0.235 | 0.234 | 0.2 | 0.209 | 0.208 | 0.212 | 0.205 | 0.211 | 0.218 | 0.215 | 0.221 | 0.209 | 0.223 | 0.218 | 0.226 | 0.224 | 0.305
A |  | L | 0.296 | 0.206 | 0.212 | 0.209 | 0.225 | 0.211 | 0.209 | 0.201 | 0.198 | 0.217 | 0.21 | 0.196 | 0.221 | 0.209 | 0.211 | 0.247 | 0.314 | 0.314 | 0.254 | 0.23 | 0.226 | 0.216 | 0.217 | 0.212 | 0.214 | 0.232 | 0.226 | 0.213 | 0.212 | 0.211 | 0.223 | 0.228 | 0.23 | 0.223 | 0.225 | 0.222 | 0.224 | 0.219 | 0.219 | 0.218 | 0.227 | 0.219 | 0.221 | 0.226 | 0.258 | 0.316 | 0.32 | 0.252 | 0.211 | 0.208 | 0.21 | 0.196 | 0.194 | 0.184 | 0.184 | 0.197 | 0.19 | 0.206 | 0.206 | 0.211 | 0.209 | 0.215 | 0.309
0.083 | +1 FT 6 IN | C | 0.286 | 0.211 | 0.218 | 0.22 | 0.216 | 0.228 | 0.218 | 0.215 | 0.219 | 0.214 | 0.209 | 0.213 | 0.215 | 0.218 | 0.218 | 0.25 | 0.321 | 0.321 | 0.269 | 0.214 | 0.245 | 0.21 | 0.224 | 0.215 | 0.22 | 0.215 | 0.216 | 0.233 | 0.217 | 0.218 | 0.22 | 0.223 | 0.212 | 0.23 | 0.22 | 0.222 | 0.229 | 0.221 | 0.221 | 0.217 | 0.22 | 0.219 | 0.225 | 0.231 | 0.264 | 0.307 | 0.304 | 0.249 | 0.214 | 0.217 | 0.199 | 0.188 | 0.195 | 0.195 | 0.191 | 0.22 | 0.201 | 0.195 | 0.223 | 0.214 | 0.217 | 0.222 | 0.314
|  | R | 0.294 | 0.208 | 0.217 | 0.232 | 0.218 | 0.224 | 0.217 | 0.214 | 0.22 | 0.207 | 0.206 | 0.221 | 0.214 | 0.204 | 0.208 | 0.243 | 0.301 | 0.305 | 0.243 | 0.217 | 0.224 | 0.216 | 0.202 | 0.201 | 0.211 | 0.204 | 0.212 | 0.21 | 0.207 | 0.216 | 0.217 | 0.211 | 0.211 | 0.202 | 0.204 | 0.192 | 0.196 | 0.204 | 0.197 | 0.196 | 0.192 | 0.186 | 0.206 | 0.186 | 0.202 | 0.246 | 0.242 | 0.202 | 0.178 | 0.172 | 0.157 | 0.173 | 0.175 | 0.183 | 0.196 | 0.186 | 0.187 | 0.199 | 0.232 | 0.219 | 0.208 | 0.216 | 0.305
A |  | L | 0.3 | 0.219 | 0.217 | 0.215 | 0.209 | 0.227 | 0.216 | 0.238 | 0.233 | 0.247 | 0.203 | 0.216 | 0.221 | 0.217 | 0.2 | 0.256 | 0.324 | 0.328 | 0.258 | 0.228 | 0.223 | 0.228 | 0.218 | 0.221 | 0.218 | 0.22 | 0.232 | 0.212 | 0.211 | 0.226 | 0.227 | 0.218 | 0.211 | 0.216 | 0.218 | 0.215 | 0.214 | 0.221 | 0.229 | 0.221 | 0.221 | 0.223 | 0.229 | 0.221 | 0.258 | 0.316 | 0.318 | 0.246 | 0.219 | 0.213 | 0.223 | 0.223 | 0.217 | 0.21 | 0.207 | 0.197 | 0.2 | 0.198 | 0.198 | 0.204 | 0.221 | 0.208 | 0.305
0.083 | 0 REFERENCE | C | 0.299 | 0.227 | 0.215 | 0.224 | 0.226 | 0.221 | 0.221 | 0.232 | 0.226 | 0.207 | 0.213 | 0.218 | 0.224 | 0.221 | 0.221 | 0.272 | 0.324 | 0.329 | 0.262 | 0.221 | 0.216 | 0.219 | 0.23 | 0.22 | 0.22 | 0.221 | 0.23 | 0.221 | 0.21 | 0.218 | 0.217 | 0.223 | 0.228 | 0.215 | 0.223 | 0.214 | 0.216 | 0.218 | 0.216 | 0.211 | 0.213 | 0.231 | 0.214 | 0.225 | 0.259 | 0.327 | 0.321 | 0.247 | 0.219 | 0.214 | 0.228 | 0.217 | 0.218 | 0.217 | 0.232 | 0.196 | 0.215 | 0.209 | 0.198 | 0.209 | 0.211 | 0.223 | 0.313
|  | R | 0.305 | 0.226 | 0.222 | 0.217 | 0.226 | 0.22 | 0.212 | 0.227 | 0.225 | 0.215 | 0.226 | 0.24 | 0.219 | 0.226 | 0.227 | 0.262 | 0.315 | 0.315 | 0.268 | 0.226 | 0.22 | 0.218 | 0.212 | 0.226 | 0.231 | 0.211 | 0.218 | 0.212 | 0.213 | 0.216 | 0.212 | 0.214 | 0.205 | 0.216 | 0.219 | 0.206 | 0.194 | 0.212 | 0.213 | 0.211 | 0.2 | 0.2 | 0.199 | 0.202 | 0.225 | 0.27 | 0.269 | 0.218 | 0.208 | 0.209 | 0.209 | 0.202 | 0.196 | 0.196 | 0.191 | 0.183 | 0.198 | 0.2 | 0.202 | 0.205 | 0.229 | 0.215 | 0.307
A |  | L | 0.314 | 0.232 | 0.223 | 0.224 | 0.224 | 0.21 | 0.208 | 0.221 | 0.237 | 0.226 | 0.224 | 0.238 | 0.21 | 0.221 | 0.216 | 0.25 | 0.322 | 0.315 | 0.258 | 0.221 | 0.217 | 0.219 | 0.217 | 0.215 | 0.231 | 0.222 | 0.207 | 0.22 | 0.227 | 0.229 | 0.222 | 0.23 | 0.219 | 0.216 | 0.221 | 0.212 | 0.217 | 0.217 | 0.22 | 0.218 | 0.212 | 0.214 | 0.216 | 0.211 | 0.249 | 0.306 | 0.312 | 0.244 | 0.209 | 0.223 | 0.202 | 0.203 | 0.199 | 0.203 | 0.206 | 0.207 | 0.222 | 0.217 | 0.215 | 0.222 | 0.226 | 0.219 | 0.314
0.083 | -9 IN | C | 0.324 | 0.225 | 0.213 | 0.223 | 0.231 | 0.22 | 0.23 | 0.237 | 0.226 | 0.221 | 0.224 | 0.223 | 0.221 | 0.226 | 0.228 | 0.261 | 0.34 | 0.325 | 0.264 | 0.213 | 0.221 | 0.216 | 0.23 | 0.225 | 0.24 | 0.214 | 0.207 | 0.211 | 0.214 | 0.217 | 0.218 | 0.223 | 0.212 | 0.232 | 0.22 | 0.212 | 0.222 | 0.224 | 0.211 | 0.2 | 0.22 | 0.213 | 0.216 | 0.229 | 0.255 | 0.303 | 0.299 | 0.247 | 0.205 | 0.221 | 0.213 | 0.204 | 0.204 | 0.22 | 0.208 | 0.209 | 0.206 | 0.232 | 0.226 | 0.218 | 0.208 | 0.218 | 0.314
|  | R | 0.323 | 0.222 | 0.22 | 0.228 | 0.223 | 0.22 | 0.216 | 0.219 | 0.214 | 0.217 | 0.218 | 0.218 | 0.212 | 0.216 | 0.215 | 0.247 | 0.313 | 0.304 | 0.259 | 0.208 | 0.209 | 0.211 | 0.223 | 0.204 | 0.213 | 0.211 | 0.201 | 0.21 | 0.209 | 0.21 | 0.23 | 0.217 | 0.213 | 0.207 | 0.213 | 0.207 | 0.208 | 0.211 | 0.211 | 0.196 | 0.206 | 0.219 | 0.201 | 0.192 | 0.242 | 0.28 | 0.289 | 0.238 | 0.203 | 0.204 | 0.213 | 0.188 | 0.205 | 0.211 | 0.211 | 0.209 | 0.211 | 0.227 | 0.223 | 0.22 | 0.21 | 0.232 | 0.313
A |  | L | 0.31 | 0.23 | 0.216 | 0.221 | 0.215 | 0.221 | 0.237 | 0.219 | 0.228 | 0.212 | 0.231 | 0.229 | 0.21 | 0.212 | 0.219 | 0.278 | 0.332 | 0.306 | 0.257 | 0.214 | 0.22 | 0.214 | 0.224 | 0.221 | 0.218 | 0.217 | 0.219 | 0.211 | 0.211 | 0.223 | 0.22 | 0.219 | 0.22 | 0.214 | 0.216 | 0.213 | 0.221 | 0.209 | 0.221 | 0.211 | 0.213 | 0.215 | 0.207 | 0.225 | 0.246 | 0.313 | 0.302 | 0.25 | 0.219 | 0.214 | 0.208 | 0.205 | 0.199 | 0.208 | 0.213 | 0.211 | 0.214 | 0.211 | 0.221 | 0.215 | 0.22 | 0.248 | 0.312
0.083 | -18 IN | C | 0.312 | 0.212 | 0.221 | 0.229 | 0.222 | 0.236 | 0.226 | 0.229 | 0.221 | 0.228 | 0.227 | 0.233 | 0.222 | 0.213 | 0.221 | 0.256 | 0.325 | 0.319 | 0.255 | 0.219 | 0.217 | 0.223 | 0.219 | 0.207 | 0.22 | 0.214 | 0.214 | 0.213 | 0.224 | 0.219 | 0.223 | 0.218 | 0.212 | 0.214 | 0.213 | 0.209 | 0.216 | 0.207 | 0.217 | 0.216 | 0.229 | 0.22 | 0.211 | 0.209 | 0.238 | 0.308 | 0.287 | 0.235 | 0.216 | 0.211 | 0.197 | 0.207 | 0.208 | 0.229 | 0.212 | 0.215 | 0.22 | 0.219 | 0.222 | 0.211 | 0.226 | 0.245 | 0.309
|  | R | 0.323 | 0.22 | 0.217 | 0.219 | 0.239 | 0.223 | 0.22 | 0.222 | 0.206 | 0.219 | 0.235 | 0.222 | 0.213 | 0.216 | 0.209 | 0.257 | 0.299 | 0.327 | 0.252 | 0.225 | 0.215 | 0.216 | 0.212 | 0.21 | 0.21 | 0.204 | 0.209 | 0.22 | 0.213 | 0.211 | 0.216 | 0.21 | 0.219 | 0.217 | 0.21 | 0.211 | 0.201 | 0.202 | 0.2 | 0.21 | 0.209 | 0.204 | 0.197 | 0.203 | 0.24 | 0.291 | 0.286 | 0.228 | 0.202 | 0.21 | 0.209 | 0.213 | 0.219 | 0.213 | 0.214 | 0.218 | 0.226 | 0.218 | 0.22 | 0.212 | 0.229 | 0.259 | 0.309
A |  | L | RF | 0.239 | 0.247 | 0.236 | 0.22 | 0.223 | 0.226 | 0.231 | 0.216 | 0.22 | 0.238 | 0.224 | 0.219 | 0.232 | 0.221 | 0.262 | 0.317 | 0.315 | 0.265 | 0.219 | 0.227 | 0.217 | 0.223 | 0.222 | 0.224 | 0.23 | 0.206 | 0.217 | 0.217 | 0.227 | 0.218 | 0.214 | 0.207 | 0.222 | 0.219 | 0.22 | 0.211 | 0.211 | 0.215 | 0.228 | 0.214 | 0.213 | 0.219 | 0.211 | 0.255 | 0.308 | 0.302 | 0.234 | 0.203 | 0.204 | 0.213 | 0.211 | 0.21 | 0.216 | 0.22 | 0.213 | 0.221 | 0.211 | 0.219 | 0.223 | 0.222 | 0.228 | RF
0.083 | -27 IN | C | RF | 0.233 | 0.218 | 0.223 | 0.214 | 0.216 | 0.225 | 0.224 | 0.222 | 0.223 | 0.226 | 0.219 | 0.23 | 0.226 | 0.222 | 0.255 | 0.335 | 0.318 | 0.27 | 0.216 | 0.216 | 0.219 | 0.223 | 0.222 | 0.22 | 0.217 | 0.221 | 0.209 | 0.208 | 0.217 | 0.224 | 0.219 | 0.214 | 0.221 | 0.217 | 0.214 | 0.217 | 0.214 | 0.21 | 0.213 | 0.216 | 0.205 | 0.22 | 0.21 | 0.245 | 0.296 | 0.302 | 0.24 | 0.204 | 0.219 | 0.215 | 0.218 | 0.212 | 0.214 | 0.215 | 0.209 | 0.218 | 0.212 | 0.212 | 0.219 | 0.218 | 0.219 | RF
|  | R | RF | 0.22 | 0.211 | 0.219 | 0.228 | 0.226 | 0.212 | 0.221 | 0.226 | 0.221 | 0.224 | 0.216 | 0.218 | 0.23 | 0.219 | 0.254 | 0.313 | 0.308 | 0.264 | 0.229 | 0.215 | 0.215 | 0.221 | 0.219 | 0.216 | 0.212 | 0.217 | 0.216 | 0.211 | 0.216 | 0.226 | 0.215 | 0.212 | 0.219 | 0.219 | 0.207 | 0.221 | 0.212 | 0.205 | 0.218 | 0.203 | 0.212 | 0.207 | 0.213 | 0.254 | 0.303 | 0.295 | 0.238 | 0.207 | 0.211 | 0.22 | 0.215 | 0.216 | 0.217 | 0.214 | 0.214 | 0.217 | 0.216 | 0.218 | 0.221 | 0.219 | 0.22 | RF
A |  | L | 0.294 | 0.239 | 0.215 | 0.229 | 0.219 | 0.212 | 0.24 | 0.244 | 0.227 | 0.232 | 0.229 | 0.238 | 0.225 | 0.234 | 0.236 | 0.27 | 0.323 | 0.297 | 0.256 | 0.225 | 0.22 | 0.222 | 0.228 | 0.214 | 0.225 | 0.214 | 0.219 | 0.219 | 0.219 | 0.218 | 0.237 | 0.229 | 0.223 | 0.213 | 0.216 | 0.219 | 0.217 | 0.213 | 0.214 | 0.211 | 0.212 | 0.209 | 0.21 | 0.212 | 0.255 | 0.325 | 0.295 | 0.247 | 0.217 | 0.22 | 0.207 | 0.213 | 0.207 | 0.212 | 0.217 | 0.212 | 0.214 | 0.222 | 0.213 | 0.22 | 0.219 | 0.224 | RF
0.083 | -36 IN | C | 0.294 | 0.236 | 0.221 | 0.215 | 0.221 | 0.215 | 0.236 | 0.243 | 0.246 | 0.234 | 0.227 | 0.227 | 0.236 | 0.229 | 0.22 | 0.265 | 0.318 | 0.3 | 0.264 | 0.23 | 0.216 | 0.223 | 0.228 | 0.232 | 0.217 | 0.219 | 0.215 | 0.22 | 0.228 | 0.219 | 0.239 | 0.228 | 0.209 | 0.212 | 0.217 | 0.204 | 0.218 | 0.208 | 0.212 | 0.209 | 0.213 | 0.225 | 0.215 | 0.21 | 0.247 | 0.309 | 0.313 | 0.251 | 0.214 | 0.221 | 0.218 | 0.215 | 0.209 | 0.212 | 0.219 | 0.213 | 0.216 | 0.219 | 0.229 | 0.211 | 0.219 | 0.234 | RF
|  | R | 0.315 | 0.229 | 0.223 | 0.215 | 0.217 | 0.218 | 0.232 | 0.229 | 0.225 | 0.237 | 0.231 | 0.225 | 0.219 | 0.228 | 0.217 | 0.269 | 0.323 | 0.302 | 0.27 | 0.214 | 0.219 | 0.221 | 0.223 | 0.216 | 0.212 | 0.226 | 0.216 | 0.22 | 0.214 | 0.221 | 0.23 | 0.224 | 0.21 | 0.21 | 0.228 | 0.219 | 0.209 | 0.22 | 0.219 | 0.218 | 0.213 | 0.223 | 0.21 | 0.215 | 0.256 | 0.329 | 0.316 | 0.251 | 0.215 | 0.218 | 0.212 | 0.214 | 0.224 | 0.217 | 0.225 | 0.219 | 0.221 | 0.22 | 0.223 | 0.227 | 0.219 | 0.216 | RF
A |  | L | 0.322 | 0.208 | 0.224 | 0.221 | 0.23 | 0.237 | 0.234 | 0.232 | 0.233 | 0.236 | 0.223 | 0.227 | 0.216 | 0.233 | 0.214 | 0.271 | 0.326 | 0.318 | 0.267 | 0.231 | 0.22 | 0.229 | 0.221 | 0.226 | 0.226 | 0.239 | 0.225 | 0.205 | 0.219 | 0.218 | 0.219 | 0.214 | 0.217 | 0.212 | 0.231 | 0.221 | 0.208 | 0.194 | 0.21 | 0.212 | 0.207 | 0.221 | 0.231 | 0.202 | 0.252 | 0.328 | 0.298 | 0.244 | 0.222 | 0.214 | 0.223 | 0.211 | 0.219 | 0.223 | 0.222 | 0.22 | 0.223 | 0.216 | 0.225 | 0.213 | 0.225 | 0.255 | 0.291
0.083 | -45 IN | C | 0.319 | 0.219 | 0.217 | 0.219 | 0.223 | 0.227 | 0.231 | 0.219 | 0.225 | 0.234 | 0.235 | 0.217 | 0.221 | 0.221 | 0.218 | 0.261 | 0.32 | 0.329 | 0.278 | 0.225 | 0.216 | 0.213 | 0.222 | 0.225 | 0.222 | 0.235 | 0.21 | 0.213 | 0.224 | 0.222 | 0.217 | 0.226 | 0.215 | 0.202 | 0.215 | 0.224 | 0.194 | 0.2 | 0.208 | 0.213 | 0.205 | 0.222 | 0.214 | 0.203 | 0.256 | 0.295 | 0.297 | 0.26 | 0.215 | 0.212 | 0.213 | 0.226 | 0.209 | 0.23 | 0.229 | 0.225 | 0.231 | 0.227 | 0.216 | 0.215 | 0.227 | 0.237 | 0.289
|  | R | 0.318 | 0.212 | 0.219 | 0.223 | 0.228 | 0.23 | 0.229 | 0.221 | 0.225 | 0.236 | 0.231 | 0.214 | 0.225 | 0.229 | 0.218 | 0.256 | 0.318 | 0.331 | 0.269 | 0.213 | 0.222 | 0.231 | 0.211 | 0.249 | 0.229 | 0.218 | 0.211 | 0.209 | 0.23 | 0.211 | 0.21 | 0.216 | 0.211 | 0.208 | 0.22 | 0.215 | 0.198 | 0.205 | 0.21 | 0.209 | 0.231 | 0.221 | 0.211 | 0.204 | 0.251 | 0.314 | 0.313 | 0.251 | 0.213 | 0.219 | 0.222 | 0.237 | 0.214 | 0.221 | 0.217 | 0.214 | 0.226 | 0.221 | 0.221 | 0.219 | 0.226 | 0.219 | 0.291
A |  | L | 0.32 | 0.212 | 0.21 | 0.219 | 0.224 | 0.22 | 0.215 | 0.208 | 0.225 | 0.217 | 0.217 | 0.222 | 0.219 | 0.219 | 0.223 | 0.266 | 0.335 | 0.307 | 0.266 | 0.212 | 0.22 | 0.217 | 0.219 | 0.216 | 0.224 | 0.218 | 0.221 | 0.21 | 0.211 | 0.222 | 0.226 | 0.218 | 0.221 | 0.208 | 0.22 | 0.219 | 0.216 | 0.208 | 0.202 | 0.217 | 0.208 | 0.212 | 0.216 | 0.211 | 0.241 | 0.312 | 0.315 | 0.237 | 0.21 | 0.222 | 0.208 | 0.221 | 0.226 | 0.22 | 0.224 | 0.219 | 0.226 | 0.214 | 0.222 | 0.224 | 0.224 | 0.231 | 0.314
0.083 | -54 IN | C | 0.329 | 0.217 | 0.207 | 0.21 | 0.233 | 0.221 | 0.219 | 0.219 | 0.225 | 0.219 | 0.224 | 0.213 | 0.213 | 0.216 | 0.227 | 0.254 | 0.326 | 0.302 | 0.263 | 0.22 | 0.219 | 0.219 | 0.226 | 0.217 | 0.228 | 0.217 | 0.211 | 0.21 | 0.215 | 0.226 | 0.211 | 0.214 | 0.216 | 0.216 | 0.216 | 0.219 | 0.21 | 0.217 | 0.212 | 0.219 | 0.214 | 0.215 | 0.225 | 0.217 | 0.262 | 0.31 | 0.296 | 0.246 | 0.213 | 0.214 | 0.22 | 0.215 | 0.218 | 0.217 | 0.221 | 0.219 | 0.228 | 0.221 | 0.219 | 0.232 | 0.228 | 0.228 | 0.316
|  | R | 0.32 | 0.22 | 0.213 | 0.219 | 0.222 | 0.217 | 0.219 | 0.215 | 0.228 | 0.227 | 0.22 | 0.222 | 0.208 | 0.22 | 0.228 | 0.261 | 0.321 | 0.319 | 0.269 | 0.21 | 0.219 | 0.215 | 0.225 | 0.223 | 0.224 | 0.22 | 0.226 | 0.214 | 0.223 | 0.229 | 0.213 | 0.213 | 0.219 | 0.215 | 0.215 | 0.211 | 0.213 | 0.22 | 0.206 | 0.221 | 0.216 | 0.209 | 0.217 | 0.211 | 0.255 | 0.309 | 0.308 | 0.258 | 0.216 | 0.211 | 0.225 | 0.221 | 0.217 | 0.221 | 0.221 | 0.236 | 0.217 | 0.221 | 0.222 | 0.226 | 0.224 | 0.229 | 0.316
A |  | L | 0.304 | 0.219 | 0.21 | 0.204 | 0.227 | 0.205 | 0.212 | 0.231 | 0.228 | 0.214 | 0.217 | 0.213 | 0.21 | 0.223 | 0.218 | 0.243 | 0.319 | 0.305 | 0.257 | 0.217 | 0.214 | 0.216 | 0.224 | 0.215 | 0.215 | 0.221 | 0.211 | 0.209 | 0.209 | 0.232 | 0.205 | 0.217 | 0.233 | 0.223 | 0.222 | 0.217 | 0.21 | 0.216 | 0.207 | 0.217 | 0.207 | 0.219 | 0.215 | 0.216 | 0.243 | 0.32 | 0.315 | 0.244 | 0.218 | 0.214 | 0.207 | 0.22 | 0.208 | 0.212 | 0.222 | 0.21 | 0.206 | 0.226 | 0.211 | 0.22 | 0.212 | 0.213 | 0.332
0.083 | -63 IN | C | 0.329 | 0.214 | 0.215 | 0.208 | 0.225 | 0.215 | 0.228 | 0.23 | 0.219 | 0.217 | 0.22 | 0.223 | 0.216 | 0.223 | 0.215 | 0.256 | 0.313 | 0.307 | 0.263 | 0.215 | 0.214 | 0.224 | 0.22 | 0.21 | 0.218 | 0.22 | 0.198 | 0.21 | 0.212 | 0.217 | 0.211 | 0.218 | 0.231 | 0.206 | 0.217 | 0.223 | 0.216 | 0.211 | 0.217 | 0.222 | 0.207 | 0.22 | 0.221 | 0.212 | 0.254 | 0.312 | 0.293 | 0.255 | 0.233 | 0.21 | 0.216 | 0.229 | 0.228 | 0.209 | 0.221 | 0.223 | 0.222 | 0.215 | 0.212 | 0.215 | 0.208 | 0.21 | 0.313
|  | R | 0.33 | 0.196 | 0.218 | 0.226 | 0.222 | 0.215 | 0.229 | 0.228 | 0.212 | 0.221 | 0.217 | 0.22 | 0.205 | 0.229 | 0.215 | 0.265 | 0.303 | 0.316 | 0.277 | 0.212 | 0.212 | 0.221 | 0.215 | 0.204 | 0.229 | 0.221 | 0.213 | 0.216 | 0.214 | 0.221 | 0.218 | 0.23 | 0.217 | 0.212 | 0.217 | 0.22 | 0.216 | 0.214 | 0.22 | 0.215 | 0.216 | 0.224 | 0.208 | 0.22 | 0.264 | 0.294 | 0.304 | 0.269 | 0.217 | 0.205 | 0.226 | 0.225 | 0.211 | 0.217 | 0.212 | 0.214 | 0.218 | 0.213 | 0.206 | 0.22 | 0.217 | 0.217 | 0.308
A |  | L | 0.221 | 0.21 | 0.213 | 0.209 | 0.204 | 0.204 | 0.212 | 0.22 | 0.204 | 0.22 | 0.213 | 0.209 | 0.207 | 0.212 | 0.214 | 0.247 | 0.302 | 0.293 | 0.248 | 0.203 | 0.21 | 0.217 | 0.205 | 0.203 | 0.214 | 0.216 | 0.206 | 0.207 | 0.208 | 0.207 | 0.213 | 0.205 | 0.217 | 0.209 | 0.209 | 0.223 | 0.209 | 0.221 | 0.203 | 0.198 | 0.211 | 0.212 | 0.213 | 0.202 | 0.231 | 0.276 | 0.294 | 0.249 | 0.201 | 0.216 | 0.208 | 0.209 | 0.194 | 0.202 | 0.209 | 0.209 | 0.225 | 0.21 | 0.22 | 0.216 | 0.212 | 0.219 | 0.299
0.083 | -72 IN | C | 0.223 | 0.232 | 0.207 | 0.213 | 0.201 | 0.196 | 0.209 | 0.195 | 0.195 | 0.211 | 0.206 | 0.211 | 0.214 | 0.213 | 0.205 | 0.248 | 0.299 | 0.297 | 0.247 | 0.203 | 0.208 | 0.209 | 0.207 | 0.209 | 0.219 | 0.216 | 0.208 | 0.215 | 0.227 | 0.208 | 0.214 | 0.214 | 0.207 | 0.209 | 0.219 | 0.207 | 0.216 | 0.205 | 0.204 | 0.202 | 0.212 | 0.214 | 0.212 | 0.208 | 0.23 | 0.273 | 0.288 | 0.239 | 0.203 | 0.206 | 0.204 | 0.211 | 0.199 | 0.214 | 0.206 | 0.201 | 0.223 | 0.217 | 0.2 | 0.205 | 0.209 | 0.215 | 0.292
|  | R | 0.229 | 0.224 | 0.218 | 0.2 | 0.216 | 0.219 | 0.215 | 0.203 | 0.199 | 0.211 | 0.209 | 0.208 | 0.208 | 0.215 | 0.221 | 0.254 | 0.319 | 0.297 | 0.264 | 0.208 | 0.207 | 0.205 | 0.212 | 0.21 | 0.226 | 0.203 | 0.209 | 0.216 | 0.219 | 0.214 | 0.212 | 0.203 | 0.213 | 0.211 | 0.208 | 0.217 | 0.2 | 0.215 | 0.204 | 0.216 | 0.209 | 0.21 | 0.215 | 0.202 | 0.232 | 0.282 | 0.307 | 0.233 | 0.21 | 0.207 | 0.2 | 0.212 | 0.204 | 0.206 | 0.203 | 0.208 | 0.214 | 0.206 | 0.202 | 0.213 | 0.211 | 0.205 | 0.295
A |  | L | 0.25 | 0.247 | 0.238 | 0.203 | 0.199 | 0.19 | 0.202 | 0.194 | 0.206 | 0.211 | 0.211 | 0.212 | 0.218 | 0.224 | 0.23 | 0.256 | 0.315 | 0.332 | 0.248 | 0.212 | 0.218 | 0.212 | 0.227 | 0.216 | 0.214 | 0.212 | 0.22 | 0.214 | 0.232 | 0.217 | 0.222 | 0.223 | 0.227 | 0.228 | 0.231 | 0.232 | 0.214 | 0.211 | 0.216 | 0.214 | 0.211 | 0.217 | 0.212 | 0.216 | 0.211 | 0.303 | 0.321 | 0.302 | 0.258 | 0.212 | 0.207 | 0.211 | 0.218 | 0.2 | 0.221 | 0.224 | 0.221 | 0.195 | 0.214 | 0.225 | 0.224 | 0.223 | 0.219
0.083 | -81 IN | C | 0.247 | 0.252 | 0.219 | 0.202 | 0.2 | 0.204 | 0.206 | 0.193 | 0.214 | 0.218 | 0.215 | 0.213 | 0.206 | 0.22 | 0.22 | 0.252 | 0.314 | 0.32 | 0.219 | 0.212 | 0.214 | 0.217 | 0.226 | 0.211 | 0.218 | 0.229 | 0.228 | 0.214 | 0.229 | 0.24 | 0.23 | 0.222 | 0.208 | 0.228 | 0.218 | 0.211 | 0.211 | 0.221 | 0.219 | 0.212 | 0.212 | 0.205 | 0.208 | 0.218 | 0.297 | 0.297 | 0.294 | 0.29 | 0.243 | 0.208 | 0.206 | 0.208 | 0.215 | 0.2 | 0.215 | 0.211 | 0.204 | 0.195 | 0.212 | 0.237 | 0.225 | 0.219 | 0.22
|  | R | 0.274 | 0.247 | 0.23 | 0.201 | 0.198 | 0.225 | 0.206 | 0.204 | 0.214 | 0.212 | 0.21 | 0.214 | 0.206 | 0.22 | 0.219 | 0.266 | 0.326 | 0.322 | 0.333 | 0.212 | 0.212 | 0.211 | 0.223 | 0.211 | 0.234 | 0.216 | 0.218 | 0.214 | 0.21 | 0.237 | 0.217 | 0.224 | 0.21 | 0.229 | 0.221 | 0.208 | 0.211 | 0.215 | 0.213 | 0.207 | 0.213 | 0.222 | 0.21 | 0.211 | 0.297 | 0.297 | 0.303 | 0.305 | 0.245 | 0.208 | 0.202 | 0.208 | 0.222 | 0.208 | 0.214 | 0.214 | 0.198 | 0.196 | 0.211 | 0.225 | 0.238 | 0.219 | 0.239
A | POSITION A | L |  |  |  | 0.222 | 0.215 |  | 0.236 | 0.224 |  | 0.23 | 0.219 |  | 0.224 | 0.214 |  | 0.252 | 0.33 |  | 0.265 | 0.216 |  | 0.218 | 0.215 |  | 0.22 | 0.214 |  |  | 0.22 | 0.221 |  | 0.221 | 0.222 |  | 0.227 | 0.232 |  |  | 0.212 | 0.214 |  | 0.215 | 0.219 |  | 0.261 | 0.312 |  | 0.247 | 0.216 |  | 0.216 | 0.22 |  | 0.226 | 0.218 |  | 0.232 | 0.213 |  | 0.225 | 0.228
0.083 | OF THE | C |  |  |  | 0.216 | 0.217 |  | 0.227 | 0.208 |  | 0.227 | 0.221 |  | 0.226 | 0.213 |  | 0.256 | 0.317 |  | 0.26 | 0.214 |  | 0.219 | 0.222 |  | 0.225 | 0.225 |  |  | 0.214 | 0.234 |  | 0.214 | 0.217 |  | 0.214 | 0.216 |  |  | 0.208 | 0.215 |  | 0.211 | 0.214 |  | 0.25 | 0.295 |  | 0.247 | 0.212 |  | 0.22 | 0.225 |  | 0.222 | 0.218 |  | 0.235 | 0.211 |  | 0.235 | 0.228
| PRIMARIES | R |  |  |  | 0.206 | 0.217 |  | 0.214 | 0.207 |  | 0.217 | 0.214 |  | 0.212 | 0.22 |  | 0.249 | 0.309 |  | 0.259 | 0.221 |  | 0.209 | 0.212 |  | 0.216 | 0.219 |  |  | 0.209 | 0.229 |  | 0.209 | 0.215 |  | 0.213 | 0.213 |  |  | 0.209 | 0.22 |  | 0.214 | 0.221 |  | 0.249 | 0.295 |  | 0.247 | 0.213 |  | 0.216 | 0.223 |  | 0.218 | 0.216 |  | 0.226 | 0.213 |  | 0.224 | 0.231
A | POSITION B | L |  |  |  | 0.218 | 0.215 |  | 0.22 | 0.22 |  | 0.218 | 0.22 |  | 0.208 | 0.209 |  | 0.246 | 0.32 |  | 0.253 | 0.212 |  | 0.211 | 0.217 |  | 0.217 | 0.207 |  |  | 0.209 | 0.223 |  | 0.212 | 0.221 |  | 0.219 | 0.219 |  |  | 0.204 | 0.212 |  | 0.216 | 0.224 |  | 0.236 | 0.307 |  | 0.236 | 0.207 |  | 0.205 | 0.211 |  | 0.214 | 0.214 |  | 0.223 | 0.212 |  | 0.221 | 0.207
0.083 | OF THE | C |  |  |  | 0.212 | 0.215 |  | 0.222 | 0.21 |  | 0.218 | 0.218 |  | 0.204 | 0.217 |  | 0.249 | 0.316 |  | 0.257 | 0.209 |  | 0.214 | 0.218 |  | 0.224 | 0.216 |  |  | 0.208 | 0.221 |  | 0.209 | 0.222 |  | 0.221 | 0.212 |  |  | 0.211 | 0.208 |  | 0.215 | 0.215 |  | 0.251 | 0.305 |  | 0.245 | 0.212 |  | 0.228 | 0.225 |  | 0.218 | 0.214 |  | 0.209 | 0.206 |  | 0.216 | 0.211
| PRIMARIES | R |  |  |  | 0.206 | 0.224 |  | 0.209 | 0.213 |  | 0.212 | 0.214 |  | 0.199 | 0.217 |  | 0.247 | 0.315 |  | 0.252 | 0.208 |  | 0.211 | 0.217 |  | 0.222 | 0.22 |  |  | 0.21 | 0.224 |  | 0.208 | 0.219 |  | 0.209 | 0.21 |  |  | 0.201 | 0.208 |  | 0.205 | 0.209 |  | 0.238 | 0.304 |  | 0.241 | 0.215 |  | 0.216 | 0.226 |  | 0.206 | 0.215 |  | 0.21 | 0.214 |  | 0.214 | 0.212
A | POSITION C | L |  |  |  | 0.207 | 0.217 |  | 0.203 | 0.229 |  | 0.219 | 0.217 |  | 0.215 | 0.22 |  | 0.254 | 0.321 |  | 0.27 | 0.208 |  | 0.216 | 0.214 |  | 0.224 | 0.217 |  |  | 0.208 | 0.215 |  | 0.218 | 0.227 |  | 0.21 | 0.216 |  |  | 0.216 | 0.209 |  | 0.215 | 0.203 |  | 0.244 | 0.304 |  | 0.254 | 0.204 |  | 0.209 | 0.219 |  | 0.209 | 0.224 |  | 0.205 | 0.216 |  | 0.211 | 0.218
0.083 | OF THE | C |  |  |  | 0.211 | 0.209 |  | 0.22 | 0.22 |  | 0.212 | 0.215 |  | 0.209 | 0.215 |  | 0.261 | 0.293 |  | 0.256 | 0.224 |  | 0.205 | 0.207 |  | 0.221 | 0.219 |  |  | 0.208 | 0.212 |  | 0.21 | 0.221 |  | 0.209 | 0.218 |  |  | 0.202 | 0.213 |  | 0.208 | 0.211 |  | 0.247 | 0.29 |  | 0.241 | 0.211 |  | 0.229 | 0.212 |  | 0.206 | 0.21 |  | 0.215 | 0.21 |  | 0.204 | 0.206
| PRIMARIES | R |  |  |  | 0.209 | 0.201 |  | 0.24 | 0.209 |  | 0.206 | 0.211 |  | 0.208 | 0.21 |  | 0.242 | 0.306 |  | 0.248 | 0.207 |  | 0.209 | 0.207 |  | 0.212 | 0.214 |  |  | 0.225 | 0.214 |  | 0.221 | 0.226 |  | 0.209 | 0.216 |  |  | 0.212 | 0.206 |  | 0.216 | 0.202 |  | 0.232 | 0.327 |  | 0.225 | 0.207 |  | 0.213 | 0.222 |  | 0.226 | 0.22 |  | 0.22 | 0.22 |  | 0.206 | 0.214
A |  | L | 0.32 | 0.306 | 0.227 | 0.223 | 0.226 | 0.236 | 0.242 | 0.215 | 0.208 | 0.215 | 0.227 | 0.238 | 0.205 | 0.216 | 0.236 | 0.303 | 0.328 | 0.299 | 0.279 | 0.236 | 0.238 | 0.209 | 0.244 | 0.214 | 0.226 | 0.213 | 0.242 | 0.243 | 0.216 | 0.236 | 0.212 | 0.235 | 0.214 | 0.236 | 0.224 | 0.221 | 0.226 | 0.228 | 0.22 | 0.245 | 0.239 | 0.238 | 0.214 | 0.236 | 0.263 | 0.219 | 0.307 | 0.301 | 0.233 | 0.227 | 0.219 | 0.209 | 0.216 | 0.2 | 0.212 | 0.226 | 0.209 | 0.214 | 0.229 | 0.202 | 0.216 | 0.22 | 0.302
0.083 | -90 IN | C | 0.203 | 0.248 | 0.247 | 0.214 | 0.223 | 0.224 | 0.221 | 0.209 | 0.22 | 0.218 | 0.223 | 0.206 | 0.208 | 0.236 | 0.219 | 0.281 | 0.305 | 0.33 | 0.272 | 0.218 | 0.24 | 0.239 | 0.218 | 0.218 | 0.241 | 0.224 | 0.213 | 0.193 | 0.212 | 0.224 | 0.21 | 0.225 | 0.217 | 0.225 | 0.212 | 0.246 | 0.239 | 0.225 | 0.221 | 0.239 | 0.229 | 0.21 | 0.209 | 0.247 | 0.254 | 0.223 | 0.296 | 0.317 | 0.233 | 0.223 | 0.236 | 0.218 | 0.209 | 0.194 | 0.235 | 0.245 | 0.208 | 0.213 | 0.239 | 0.243 | 0.198 | 0.218 | 0.314
|  | R | 0.231 | 0.229 | 0.247 | 0.239 | 0.213 | 0.242 | 0.232 | 0.216 | 0.218 | 0.213 | 0.231 | 0.224 | 0.22 | 0.236 | 0.231 | 0.271 | 0.308 | 0.362 | 0.276 | 0.218 | 0.241 | 0.225 | 0.236 | 0.222 | 0.227 | 0.215 | 0.242 | 0.203 | 0.221 | 0.229 | 0.206 | 0.228 | 0.216 | 0.22 | 0.239 | 0.225 | 0.235 | 0.234 | 0.228 | 0.215 | 0.237 | 0.221 | 0.237 | 0.247 | 0.265 | 0.297 | 0.283 | 0.342 | 0.238 | 0.214 | 0.225 | 0.212 | 0.22 | 0.214 | 0.218 | 0.223 | 0.202 | 0.213 | 0.202 | 0.236 | 0.205 | 0.212 | 0.272
A | POSITION A | L | 16: 0.267; 17: 0.323; 18: 0.301; 19: 0.267; 45: 0.252; 46: 0.319; 47: 0.235; 48: 0.237
0.083 | OF THE | C | 16: 0.246; 17: 0.301; 18: 0.319; 19: 0.268; 45: 0.235; 46: 0.287; 47: 0.298; 48: 0.231
| SMELTS | R | 16: 0.274; 17: 0.222; 18: 0.347; 19: 0.27; 45: 0.252; 46: 0.26; 47: 0.309; 48: 0.255
A | POSITION B | L | 16: RF; 17: 0.337; 18: 0.313; 19: RF; 45: RF; 46: 0.269; 47: 0.33; 48: RF
0.083 | OF THE | C | 16: 0.263; 17: 0.305; 18: 0.324; 19: 0.279; 45: 0.294; 46: 0.32; 47: 0.339; 48: 0.277
| SMELTS | R | 16: RF; 17: 0.323; 18: 0.317; 19: RF; 45: RF; 46: 0.338; 47: 0.324; 48: RF
A | POSITION C | L | bar: 16 to 19; 45 to 48
0.083 | OF THE | C | bar: 16 to 19; 45 to 48
| SMELTS | R | bar: 16 to 19; 45 to 48
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | AVG | MIN
B | 0.001-0.099 | 0.141-0.150 | 10: OUTSIDE DIAMETER:; RF 23: 2.969; RF 30: INSPECTION RESULTS
LEGEND | 0.100-0.110 | 0.151-0.160 | 10: TUBE MATERIAL:; RF 23: SA-178A; RF 35: MAX. THICKNESS
| 0.111-0.120 | 0.161-0.170 | 10: NOMINAL WALL:; RF 23: 0.18; RF 35: AVG. THICKNESS
| 0.121-0.130 | 0.171-0.180 | 10: ASME MIN:; RF 23: 0.099; RF 35: MIN. THICKNESS
| 0.131-0.140 | 0.181-0.999 | 10: MILL FLAG:; RF 23: 0.11; RF 35: STD DEV.
A | 0.001-0.083 | 0.131-0.140 | 10: OUTSIDE DIAMETER:; RF 23: 3; RF 30: INSPECTION RESULTS |  |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com | EXAMPLE PAPER
LEGEND | 0.084-0.100 | 0.141-0.150 | 10: TUBE MATERIAL:; RF 23: SA210A1; RF 35: MAX. THICKNESS |  |  |  | RIVERDALE MILL
| 0.101-0.110 | 0.151-0.160 | 10: NOMINAL WALL:; RF 23: 0.203; RF 35: AVG. THICKNESS |  |  |  | TUBE WALL THICKNESS SURVEY
| 0.111-0.120 | 0.161-0.170 | 10: ASME MIN:; RF 23: 0.083; RF 35: MIN. THICKNESS |  |  |  | NO. 1 RECOVERY BOILER
| 0.121-0.130 | 0.171-0.999 | 10: MILL FLAG:; RF 23: 0.1; RF 35: STD DEV.; RF 46: Job # H449364 P.O. # 0018342455 W.O. # N/A Date: 5/05/2025 |  |  |  | 02 FRONT WALL W/ PORTS
THICKNESS
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Corrosion
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. CORROSION RATE MEASUREMENTS ARE IN MILS. | [67 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | AVG | MAX
B | POSITION A | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.68 | 1.98 | 1.06 | ND | 2.35 | 0.733 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.53 | 1.23 | ND | 0.125 | 3.65 | 0.937 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| MANWAY | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.246 | 1.54 | ND | 0.572 | 0.823 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B | POSITION B | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.442 | 3.15 | 2.16 | 0.194 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.675 | 0.776 | ND | ND | ND | 1.86 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| MANWAY | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.55 | 2.44 | ND | 1.31 | 3.54 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B | POSITION C | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.08 | 2.05 | 2.6 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.37 | 1 | 0.682 | ND | 1.65 | 1.65 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| MANWAY | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.7 | 3.58 | ND | 1.1 | 1.92 | 1.37 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B | POSITION D | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.11 | 0.394 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.46 | 2.21 | 0.148 | 0.349 | 0.149 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| MANWAY | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.66 | 0.49 | 0.938 | ND | 2.55 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B | POSITION E | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 8.15 | 2.43 | 0.505 | 1.2 | 0.706 | 1.99 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.379 | 2.51 | ND | 0.675 | 0.487 | 1.79 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| MANWAY | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.96 | 0.36 | 1.68 | 3.45 | 4.12 | 0.704 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B | POSITION A | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 13.1 | ND | 1.28 | 9.01 | 0.981 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.14 | ND | 4.49 | 0.347 | 1.56 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 12.8 | 0.433 | ND | 15.2 | 0.027 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.865 | ND | 0.412 | 3.76 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| TERTIARIES | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.19 | 11.3 | 0.328 | ND | 16.4 | 0.195 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.34 | 1.55 | 1.27 | ND | 0.582 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B | POSITION B | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.005 | ND | ND | 0.906 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.559 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.22 | ND | ND | 0.313 | ND | 0.839 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| TERTIARIES | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.703 | ND | ND | 0.006 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.448 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B | POSITION C | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 10.9 | ND | 2.01 | 7.21 | 1.66 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 6.59 | ND | 2.77 | 6.09 | 1.62 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.631 | 13 | ND | 0.835 | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 9.04 | ND | ND | 6.99 | 0.73 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| TERTIARIES | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.73 | 14 | 2.71 | ND | 4.05 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.584 | 10.6 | 1.63 | ND | 6.99 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A |  | L | ND | 8.92 | 0.27 | ND | ND | ND | 0.917 | ND | ND | ND | 1.85 | 1.26 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4.6 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.07 | ND | ND | ND | ND | ND | 0.237 | 0.173 | ND | 0.532 | ND | ND | ND | ND | ND | 0.399 | 1.52 | 0.001 | 3.19 | 6.33 | 2.28 | ND | 6.61 | ND | 4.1 | 6.81 | 1.38 | ND | ND | ND | ND
| +16 FT 6 IN | C | ND | 5.44 | ND | 0.131 | ND | 2.98 | ND | ND | ND | ND | 3.69 | 0.576 | ND | ND | 0.708 | ND | ND | ND | ND | ND | 0.251 | ND | 0.196 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.05 | ND | 0.03 | ND | ND | ND | 0.709 | 0.152 | ND | 0.639 | ND | 0.854 | ND | ND | 3.89 | ND | 2.36 | ND | 1.25 | 1.98 | 1.53 | ND | 1.44 | 1.42 | 5.36 | 7.67 | 0.162 | ND | ND | ND | ND
|  | R | ND | ND | 0.841 | 0.528 | ND | 3.18 | ND | ND | ND | ND | 3.23 | 0.202 | 0.007 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 13.3 | ND | 0.698 | ND | ND | ND | ND | ND | ND | ND | ND | 0.265 | 0.703 | ND | ND | ND | ND | 3.44 | ND | 0.363 | ND | 1.25 | 2.18 | 1.15 | ND | 1.77 | 2.35 | 2.41 | 3.68 | 1.1 | 0.203 | ND | 16.7 | ND
A |  | L | 5.78 | ND | 0.584 | 1.35 | 0.191 | 5.11 | 2.81 | ND | 0.217 | ND | 6.11 | 5.59 | 0.973 | ND | 0.213 | ND | ND | ND | ND | 6.5 | ND | 0.053 | ND | 7.45 | ND | 0.199 | 0.842 | 0.955 | ND | ND | ND | ND | 0.413 | ND | ND | ND | ND | ND | ND | ND | ND | 0.453 | ND | ND | 0.9 | ND | 1.63 | ND | 3.69 | 1.36 | 0.111 | ND | 0.15 | ND | ND | ND | 4.1 | ND | ND | 3.56 | 0.142 | 1.69 | 4.18
| +15 FT | C | ND | 1.4 | 0.994 | 0.408 | 0.336 | 5.14 | ND | 0.165 | ND | ND | ND | ND | ND | ND | ND | 0.884 | 1.29 | ND | ND | ND | ND | 0.266 | 0.423 | ND | ND | ND | ND | ND | 0.161 | ND | 0.255 | ND | ND | ND | 0.246 | ND | 0.728 | 0.223 | ND | ND | ND | ND | ND | ND | ND | ND | 3.17 | ND | 4.32 | 0.383 | 0.87 | ND | 0.357 | ND | ND | ND | ND | ND | ND | 0.37 | ND | 0.056 | ND
|  | R | ND | 2.15 | 5.91 | ND | ND | 6.37 | 0.534 | ND | 3.86 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.059 | 0.356 | ND | 1.44 | ND | ND | ND | ND | 0.309 | ND | ND | ND | 0.722 | ND | ND | ND | ND | ND | ND | 0.448 | ND | ND | ND | ND | 3.3 | ND | 4.87 | 1.93 | 1.07 | ND | 4.17 | ND | 0.118 | ND | ND | ND | ND | ND | ND | ND | ND
A |  | L | 7.01 | 1.37 | 0.472 | 0.857 | 3.03 | 1.5 | 0.519 | 0.412 | 0.713 | ND | ND | 1.07 | ND | ND | ND | 2.85 | ND | 4.66 | 1.86 | 2.24 | 0.804 | 0.712 | 4.31 | 2.46 | 0.656 | ND | ND | 0.978 | ND | ND | ND | ND | ND | ND | ND | 0.56 | ND | ND | ND | ND | ND | 0.03 | ND | ND | 0.259 | 1.85 | 0.414 | ND | ND | ND | 0.353 | 3.23 | ND | ND | 0.939 | 0.482 | ND | ND | ND | ND | 0.751 | ND | ND
| +13 FT 6 IN | C | 4.79 | 11.2 | 2.62 | ND | 1.59 | 0.451 | 0.28 | 1.25 | 4 | ND | 0.173 | ND | ND | ND | ND | 0.251 | ND | 0.323 | ND | 5.09 | 15.3 | ND | 0.137 | ND | ND | 0.455 | 0.221 | ND | ND | 0.098 | ND | ND | ND | ND | ND | 0.066 | 1.64 | 2 | ND | 0.7 | ND | 0.392 | ND | 1.77 | 0.359 | 1.56 | 0.496 | ND | ND | ND | ND | 3.37 | ND | ND | 0.142 | 1.71 | ND | ND | ND | 1.43 | 0.272 | ND | ND
|  | R | 5.97 | 3.14 | 0.394 | 1.58 | 0.813 | 0.527 | ND | 0.729 | 1.41 | ND | 1.71 | ND | 0.744 | ND | ND | 0.02 | 0.288 | 1.29 | ND | 0.696 | ND | 1.3 | 2.86 | 1.7 | 0.189 | ND | ND | 0.208 | ND | ND | ND | 0.242 | ND | ND | 1.42 | 0.29 | ND | 1.04 | ND | 0.567 | ND | ND | ND | ND | 0.855 | ND | ND | 0.008 | ND | ND | 0.606 | 3.55 | ND | 3.21 | 0.837 | 0.154 | 0.276 | ND | ND | ND | 0.727 | ND | ND
A |  | L | 1.53 | 0.056 | 1.82 | 0.44 | ND | ND | 2.55 | ND | 0.164 | 0.996 | ND | 1.2 | ND | 0.244 | 0.598 | 2.45 | 0.702 | 3.69 | ND | 0.437 | 2.41 | 1.72 | 0.663 | 1.61 | 0.504 | 1.2 | 1.09 | 1.02 | 2.02 | 1.23 | 1.16 | ND | 0.084 | ND | 0.576 | ND | 2.14 | 0.395 | ND | 0.933 | 2.46 | 1.11 | 1.21 | 20.3 | 0.834 | 1.6 | 3.04 | 3.45 | 2.12 | 0.327 | 0.321 | ND | 1.37 | 0.263 | 0.175 | 0.162 | ND | 1.41 | ND | ND | ND | 1.79 | ND
| +12 FT | C | 3.55 | 0.328 | 1.54 | ND | ND | 0.55 | 2.43 | 0.205 | ND | 1.55 | 0.91 | 0.298 | ND | 2.18 | 1.78 | 2.33 | 0.334 | 1.59 | 0.873 | 1.14 | 0.495 | 0.224 | 1.35 | ND | 1.08 | 1.04 | ND | ND | ND | 1.19 | 1.05 | ND | ND | ND | ND | ND | 2.86 | 0.153 | 0.481 | 0.929 | 1.93 | 0.041 | 0.922 | 18.9 | 0.417 | 1 | 0.716 | 1.87 | 1.1 | 2.03 | 1.26 | ND | 0.761 | ND | ND | ND | ND | ND | ND | ND | ND | 1.05 | ND
|  | R | 2.2 | 2.71 | 2.48 | ND | 1.84 | ND | 4.14 | ND | 1.03 | 1.94 | 1.03 | 0.142 | ND | 0.866 | 1.69 | 0.892 | 1.52 | 4.22 | 1.29 | 1 | 2.3 | ND | 1.18 | ND | 0.787 | 1.05 | 0.565 | 1.57 | 1.15 | 0.792 | 1.64 | ND | 0.19 | ND | ND | ND | 1.71 | 0.452 | 0.735 | 1.37 | 0.578 | 0.393 | 2.26 | 21.6 | 1.09 | 1.29 | ND | 3.48 | 3.24 | 2.24 | 0.315 | ND | 2.84 | ND | ND | ND | ND | 1.56 | ND | ND | ND | 0.609 | ND
A | POSITION A | L | ND | ND | 1.26 | 2.76 | 2.73 | 0.411 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.05 | 0.593 | 1.33 | ND | ND | ND
| OF THE | C | ND | ND | 2.81 | ND | 1.83 | 0.837 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.802 | 1.64 | 2.04 | ND | ND | ND
| OB PORTS | R | ND | ND | 1.16 | 0.288 | 2.49 | 1.13 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.745 | 1.75 | 3.66 | 0.366 | ND | ND
A | POSITION B | L | ND | ND | 1.79 | 3.54 | 2.58 | 1.17 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.12 | 0.919 | 2.4 | ND | ND
| OF THE | C | ND | ND | ND | 2.12 | 3.63 | 0.576 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.925 | 0.541 | 0.475 | 2.07 | ND | ND
| OB PORTS | R | ND | ND | 1.89 | 1 | 1.95 | 0.213 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.01 | 1.76 | ND | 0.685 | ND | ND
A | POSITION C | L | ND | ND | ND | 1.38 | 0.994 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.41 | 1.46 | 1.01 | ND | ND | ND
| OF THE | C | ND | ND | 1.05 | ND | 2.22 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.11 | 2.56 | 0.14 | 0.393 | ND | ND
| OB PORTS | R | ND | ND | 0.057 | 2.34 | 0.447 | 0.958 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3 | 1.35 | ND | ND | ND | ND
A |  | L | ND | 1.85 | 3.3 | 1.93 | 1.24 | 1.21 | 1.09 | 4.02 | 0.815 | 2.37 | 1.91 | 1.26 | 1.74 | 1.47 | 2.09 | 3.5 | 2.13 | ND | ND | 1.42 | 1.03 | 1.47 | 4.35 | 2.07 | 2.54 | ND | 1.07 | 0.809 | ND | ND | 1.84 | 1.43 | ND | 1.53 | 1.44 | 2.13 | 0.599 | 2.45 | 0.446 | 1.64 | 0.684 | 1.16 | 0.095 | ND | ND | 2.97 | 0.961 | ND | ND | ND | 0.093 | 0.254 | ND | 0.661 | 0.114 | 2.82 | ND | ND | 2.87 | 0.633 | ND | ND | ND
| +10 FT 6 IN | C | ND | 1.53 | 1.5 | 2.62 | 2.45 | 1.24 | 1.3 | 3.49 | 0.631 | 0.503 | 0.041 | 1.61 | 3.41 | ND | 2.42 | 2.12 | 1.95 | 0.602 | 0.118 | 1.41 | 0.852 | 1.12 | 3.27 | 2.12 | ND | 0.325 | 1.11 | 1.01 | 0.073 | 0.949 | 0.524 | 1.69 | 0.124 | 0.918 | 0.875 | ND | 0.343 | 2.91 | 0.378 | 1.79 | 0.53 | 0.197 | 2.67 | 0.984 | 1.28 | ND | 0.059 | ND | ND | ND | 0.76 | 0.016 | ND | 0.106 | 0.683 | ND | ND | ND | 2.09 | 0.733 | ND | ND | ND
|  | R | ND | 2.44 | 0.51 | 1.25 | 1.43 | 1.39 | 0.432 | 2 | ND | 0.338 | 0.547 | 1.57 | 0.738 | 1.12 | 1.03 | 4.5 | 2.09 | 2.36 | 0.648 | 2.41 | 2.62 | 1.64 | 2.32 | 0.482 | 2.51 | 0.545 | 0.905 | 0.591 | 0.371 | ND | ND | 1.29 | 0.815 | 1.97 | 0.862 | ND | 2.21 | 2.78 | 1.46 | 0.057 | 2.32 | 0.994 | 1.91 | 0.47 | 2.32 | ND | 0.983 | ND | ND | ND | 1.83 | ND | 0.411 | 0.476 | ND | ND | ND | 1.32 | 1.14 | 0.797 | ND | ND | ND
A |  | L | 4.73 | 1.12 | 0.653 | ND | 0.685 | 1.19 | ND | 0.773 | 0.015 | 0.94 | 2.68 | ND | 1.04 | ND | 3.19 | 3.67 | 0.775 | 1.99 | 1.53 | 3.8 | 3.13 | 2.74 | 2.66 | 2.94 | 3.28 | 0.061 | 2.34 | 3.97 | 1.25 | 2.56 | ND | ND | ND | 2 | 1.85 | 1.22 | ND | 3.52 | ND | 0.212 | ND | 1.65 | 1.58 | ND | 0.915 | 3.55 | ND | 2.29 | ND | 2.81 | 1.39 | 1.83 | ND | 2.06 | 0.351 | ND | 0.27 | 0.4 | 0.215 | 0.988 | 3.36 | 1.93 | ND
| +9 FT | C | 4.76 | 4.15 | 0.84 | 0.124 | ND | ND | ND | ND | ND | 0.51 | 1.02 | ND | 1.46 | 0.097 | ND | 2.57 | ND | 0.803 | 3.4 | 2.25 | 0.726 | 2.01 | 3.08 | 1.93 | 1.25 | 0.532 | 2.45 | 1.95 | 0.66 | 1.01 | 2.22 | 0.581 | 0.485 | 1.94 | 0.906 | 0.227 | ND | 1.49 | ND | 0.131 | 1.25 | 0.206 | 0.749 | ND | 1.22 | 2.16 | ND | 2.52 | 0.011 | 1.74 | 0.14 | 1.57 | ND | 1.1 | ND | ND | 0.893 | ND | 0.362 | 1.46 | 3.28 | 5.26 | 9.74
|  | R | 2.24 | 3.13 | 0.279 | 2.65 | 0.428 | ND | ND | 1.46 | 0.899 | 0.36 | 1.1 | ND | 0.643 | ND | 1.22 | 2.6 | 1.33 | 1.16 | 3.56 | 2.81 | 3.15 | 0.583 | 4.12 | 4.14 | 2.13 | 2.13 | 3.84 | 3.23 | 1.25 | 1.98 | 2.37 | 1.18 | 2.94 | 1.19 | 2.07 | 2.46 | ND | 1.8 | 0.57 | ND | ND | 2.18 | 2.28 | 1.95 | 3.33 | 0.975 | ND | 5.06 | ND | ND | 0.338 | 0.921 | ND | ND | ND | 0.25 | ND | ND | 1.03 | ND | 3.03 | 5.02 | ND
A | POSITION A | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.855 | 1.78 | ND | 4.27 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.755 | 1.2 | 2.05 | 0.01 | 1.23 | 1.01 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.78 | 3.16 | ND | 0.039 | 1.54 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSTION B | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.304 | 0.212 | 0.768 | ND | 0.264 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.06 | 1.54 | 2.87 | 0.966 | 1.02 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.41 | 0.098 | ND | 0.898 | 0.534 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION C | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.87 | ND | 1.54 | 1.14 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.18 | 0.405 | 1.23 | ND | 1.23 | 2.14 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.11 | 0.476 | 1.16 | 0.836 | 1.6 | 0.347 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION D | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.885 | 0.752 | 0.366 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.68 | 1.49 | 0.938 | 0.421 | 2.05 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.977 | ND | ND | 2.08 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION E | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.02 | 0.64 | 1.05 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.835 | 0.294 | ND | 1.8 | 0.263 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.27 | ND | 1.14 | ND | ND | 0.512 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A |  | L | 2.28 | 2.91 | 1.81 | ND | ND | 0.701 | 0.959 | ND | ND | 0.759 | ND | 1.53 | ND | 2.89 | 1 | ND | 1.67 | 1.12 | 0.537 | ND | 1.36 | 0.635 | ND | 5.07 | 2.64 | 2.35 | 3.38 | 2.22 | ND | 2.52 | 2.91 | ND | ND | 2.14 | ND | 1.18 | ND | 1.71 | 3.87 | 1.85 | 0.521 | 1.08 | ND | 0.909 | ND | 3 | 0.984 | ND | 1.86 | ND | 0.42 | ND | 0.703 | 0.464 | ND | 0.845 | 0.986 | 1.33 | ND | ND | 0.837 | 1.4 | 11.6
| +7 FT 6 IN | C | 1.9 | 2.01 | 1.67 | 0.152 | ND | 1.36 | 1.25 | ND | 1 | 0.445 | 0.461 | 1.91 | 0.571 | 1.82 | ND | ND | 1.44 | 0.902 | 0.759 | ND | 0.62 | 0.481 | 0.919 | 3.47 | 2.38 | 2.22 | 1.85 | 2.3 | 0.872 | 3.21 | 1.27 | ND | ND | 1.39 | ND | 1.89 | ND | 1.91 | 2.43 | 1.98 | 0.98 | 1.17 | ND | 1.5 | ND | 3.91 | 0.336 | ND | 3.05 | ND | 0.189 | 1.26 | 1.76 | 0.373 | ND | ND | 0.965 | 1.52 | ND | ND | 0.934 | ND | 111
|  | R | 4.19 | 1.41 | 1.72 | 0.042 | ND | 2.49 | 2.43 | ND | 1.49 | 0.458 | 0.895 | 2.13 | 1.2 | 2 | ND | 0.39 | 0.629 | ND | 1.07 | 1.06 | 0.565 | 0.054 | ND | 4.4 | 3.6 | 3.21 | 4.21 | 3.62 | 1.7 | 3.82 | ND | ND | 0.376 | 1.79 | ND | 3.46 | ND | 1.1 | 1.07 | ND | 0.069 | ND | 0.269 | 1.54 | 0.109 | 1.5 | ND | ND | 1.16 | ND | ND | 1.77 | ND | 2 | 0.166 | 0.777 | 2.45 | 2.16 | ND | ND | 3.32 | ND | ND
A |  | L | 0.99 | 3.6 | 0.673 | 1.31 | ND | 0.047 | ND | ND | ND | ND | ND | 0.599 | 1.78 | ND | 2.56 | 2.12 | ND | 7.41 | 1.53 | 0.935 | ND | 1.48 | 4.2 | ND | 2.27 | ND | 2.17 | 1.49 | 5.58 | ND | 4.45 | 5.11 | 0.908 | 2.21 | 1.39 | ND | 0.697 | 2 | 2.7 | ND | 0.445 | ND | ND | 0.076 | 0.77 | 2.36 | 2.38 | 3.12 | ND | ND | 1.42 | ND | ND | ND | 0.538 | ND | ND | 0.003 | ND | ND | ND | ND | ND
| +6 FT | C | 0.252 | 3.87 | 1.16 | 1.14 | ND | ND | ND | 1.76 | ND | 0.677 | ND | ND | ND | ND | 1.44 | 1.65 | 6.3 | 4.14 | 1.55 | 2.26 | 0.503 | 0.765 | ND | 0.213 | 0.548 | ND | 2.53 | 0.771 | 1.4 | 1.82 | 3.93 | 3.88 | 4.76 | 3.38 | 1.97 | 0.611 | 1.04 | 5.69 | 3.62 | ND | ND | ND | 1.45 | 0.341 | 0.7 | 3.62 | 2.07 | 3.44 | 1.17 | ND | 0.581 | ND | 0.144 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.68
|  | R | 0.253 | 1.67 | 0.144 | 1.01 | ND | ND | 0.417 | 2.13 | 0.889 | ND | ND | 0.256 | 0.726 | ND | 2.35 | 2.3 | ND | 5.2 | 3.09 | 2.64 | ND | 1.57 | 2 | ND | 2.69 | ND | ND | ND | 0.516 | 0.681 | 1.83 | 3.68 | 3.64 | 2.22 | 2.21 | 4.23 | ND | 2.25 | 2.17 | 0.044 | 0.212 | 0.581 | 1.16 | ND | ND | 4.92 | ND | 0.181 | 1 | ND | 2.08 | ND | ND | ND | ND | ND | ND | 0.168 | ND | ND | ND | ND | 4.42
A |  | L | 9.17 | 1.14 | ND | ND | ND | 1.82 | ND | ND | ND | 2.82 | 1.23 | 0.661 | 0.13 | ND | 1.24 | 0.329 | 7.98 | 7.17 | 1.71 | ND | ND | ND | ND | 0.333 | 5.85 | 0.705 | 1.79 | ND | 2.28 | ND | 0.077 | 0.82 | 2.26 | 1.44 | 0.864 | 0.068 | ND | 0.936 | 0.562 | 0.681 | ND | 2.52 | 3.01 | ND | 3.58 | 3.64 | 1.59 | 0.387 | 1.12 | 2.57 | 0.471 | 0.428 | 3.01 | ND | ND | 1.22 | 1.66 | 0.859 | 1.64 | 1.78 | 0.574 | ND | ND
| +4 FT 6 IN | C | 5.11 | 2.06 | ND | ND | ND | 1.68 | ND | ND | ND | 2.4 | 1.25 | 0.722 | ND | ND | 1.05 | 0.793 | 4.46 | 1.64 | 2.78 | 0.6 | 0.132 | ND | ND | 1.09 | 1.47 | 2.4 | 1.34 | 1.9 | ND | 2.28 | 0.038 | 1.05 | 2.16 | 3.28 | 4.2 | 3.14 | 2.71 | 0.28 | 2.2 | 1.62 | 1.75 | 1.82 | 3.03 | ND | 2.76 | 2.08 | 4.16 | 0.451 | 0.588 | 1.55 | ND | 0.398 | 0.669 | 0.193 | ND | 0.638 | 0.285 | 0.466 | 0.601 | 0.481 | 0.446 | ND | 1.86
|  | R | 4.39 | 3.44 | ND | 1.58 | 0.541 | ND | ND | ND | ND | 1.94 | ND | ND | 0.57 | ND | 2.44 | 0.638 | 4.76 | 2.37 | 4.03 | 2.18 | 1.16 | ND | 1.26 | 0.838 | ND | 1.6 | 2.41 | 1.71 | ND | 2.84 | 1.44 | 1.3 | 0.879 | 2.8 | 3.67 | 0.752 | 4.13 | 0.708 | 1.93 | 1.35 | 1.8 | 1.5 | 1.85 | 0.655 | 2.61 | 1.97 | 5.38 | 1.09 | ND | 1.68 | ND | ND | ND | ND | ND | ND | ND | 0.017 | 0.442 | 0.364 | ND | ND | 3.25
A |  | L | 6.69 | 2.95 | ND | ND | 0.097 | 0.07 | 0.892 | 0.94 | ND | ND | 0.26 | 1.64 | ND | 2.31 | ND | ND | 2.16 | ND | 0.601 | ND | ND | 0.774 | 0.622 | 2.68 | ND | ND | ND | ND | ND | ND | ND | ND | 1.63 | ND | ND | 0.03 | ND | ND | 1.7 | 2.76 | 1.38 | 1.8 | 2.06 | 2.61 | 5.17 | 5.53 | 15.2 | 4.5 | 0.54 | ND | 0.31 | 0.685 | 2.1 | 0.754 | 0.379 | ND | 1.71 | 1.5 | ND | 0.195 | 0.36 | 0.192 | 0.487
| +3 FT | C | 6.95 | ND | 1.24 | 1.5 | ND | 1.99 | 2.06 | 0.016 | ND | ND | 0.16 | 0.26 | ND | 2 | ND | 0.022 | ND | ND | ND | ND | ND | ND | 2.83 | 0.166 | ND | 1.38 | 1.6 | 2.17 | 0.285 | 0.67 | ND | ND | ND | 0.307 | ND | ND | 0.936 | 3.17 | 4.91 | 1.96 | 3.51 | 6.09 | 3.65 | 5.65 | 6.34 | 10.7 | 12.1 | 11.1 | 2.16 | 0.834 | 0.253 | 2.36 | 2.86 | 1.75 | ND | 1.92 | 1.95 | 1.13 | ND | 1.09 | ND | ND | 2.68
|  | R | 6.75 | ND | 0.747 | 1.23 | 2.31 | 0.594 | 1.04 | ND | 0.184 | 1.55 | ND | 0.952 | ND | 2.4 | ND | 1.93 | ND | 1.62 | ND | ND | ND | 1.08 | 1.1 | 1.03 | 1.72 | ND | 1.5 | 1.15 | 0.474 | 3.19 | ND | ND | 0.519 | 2.75 | 1.6 | 0.161 | 2.06 | 3.58 | 3.73 | 5.23 | 5.79 | 6.39 | 6.38 | 5.39 | 11.8 | 10.6 | 15 | 8.27 | 0.22 | 0.81 | ND | 2.19 | 1.51 | 1.55 | ND | ND | 1.24 | 2.21 | ND | 2.49 | 1.05 | ND | 4.31
A |  | L | ND | 0.616 | 1.51 | 0.852 | ND | 0.916 | 1.28 | 2.34 | 2.81 | 2.18 | 1.41 | 0.67 | ND | 2.04 | ND | 3.95 | 4.26 | 9 | 3.15 | ND | 0.748 | ND | 0.225 | 0.644 | 0.038 | ND | ND | 0.368 | 0.569 | 1.12 | ND | ND | ND | 0.763 | ND | ND | ND | ND | 0.629 | ND | ND | 0.461 | ND | 8.82 | ND | ND | ND | 8.22 | ND | 3.05 | 1 | 6.51 | 1.76 | 5.01 | 8.62 | 4.31 | 1.34 | 0.253 | ND | ND | 1.62 | 1.09 | 8.08
| +1 FT 6 IN | C | ND | 1.17 | ND | 0.053 | ND | ND | ND | 0.625 | ND | 1.02 | 1.08 | ND | ND | ND | ND | 5.64 | 0.606 | 2.89 | 1.33 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4.62 | ND | ND | ND | 9.92 | ND | 2.55 | 0.816 | 5.2 | ND | 3.6 | 5.64 | 2.09 | 0.004 | ND | ND | ND | 2.1 | 0.188 | 2.44
|  | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.478 | ND | ND | ND | ND | 2.79 | ND | 0.296 | 0.137 | ND | ND | ND | 0.457 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.35 | ND | ND | ND | 14.8 | ND | 2.93 | 9.2 | 15.6 | 4.66 | 12.1 | 4.68 | 12.6 | ND | 6.76 | 3.56 | 7.13 | 0.729 | 0.645 | ND | ND | 4.48 | 0.928 | 3.89
A |  | L | ND | ND | 1.63 | ND | 5.06 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.107 | ND | ND | ND | ND | ND | ND | ND | ND | 3.16 | ND | ND | ND | 1 | 0.537 | 1.42 | ND | ND | 0.08 | 0.826 | 1.48 | 0.762 | 0.867 | ND | ND | 0.025 | ND | ND | ND | ND | 0.519 | 1.87 | 0.71 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 8.4 | ND
| 0 REFERENCE | C | 1.8 | ND | ND | ND | 2.54 | ND | ND | ND | ND | 1.3 | ND | ND | ND | ND | ND | ND | 0.8 | 0.188 | 0.36 | 0.71 | 2.43 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.111 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.02 | ND | 3.94
|  | R | 3.7 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4.66 | 1.91 | 2.38 | ND | ND | ND | 2.39 | 0.97 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.24 | 1.63 | 2.55 | ND | ND | 5.7
A |  | L | 1.99 | 0.523 | ND | ND | ND | ND | 0.246 | ND | ND | ND | ND | ND | ND | ND | ND | 2.82 | 1.22 | 3.27 | 0.046 | 0.321 | ND | ND | 1.8 | 0.868 | ND | ND | 1.93 | ND | ND | ND | ND | ND | ND | 1.48 | ND | 0.128 | 0.691 | ND | ND | 0.791 | ND | ND | ND | 1.67 | 1.44 | 3.81 | 2.72 | ND | 0.74 | ND | ND | 0.82 | 1.77 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| -9 IN | C | 1.81 | 0.793 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.203 | 0.052 | 0.119 | 0.878 | ND | 1.05 | 1.33 | 1.8 | ND | 4.75 | ND | ND | ND | 0.197 | 2.52 | 0.005 | ND | ND | 0.065 | ND | ND | ND | ND | 0.628 | ND | ND | 0.031 | 2.97 | ND | ND | ND | ND | 1.34 | 1.47 | 0.957 | ND | ND | ND | ND | ND | ND | ND | 1.6 | ND | 1.48 | ND | ND | ND | 0.963 | 0.476 | 2.51
|  | R | 0.411 | ND | ND | ND | ND | 0.199 | ND | ND | ND | ND | 0.664 | 1.32 | 2.58 | 0.501 | 1.86 | 0.786 | ND | 0.125 | 0.514 | ND | ND | 1.49 | ND | ND | ND | 0.529 | 0.425 | 4.42 | ND | 1.14 | ND | 0.04 | 1.15 | ND | ND | ND | 1.11 | ND | ND | 0.357 | ND | ND | ND | 0.281 | ND | 1.05 | 3.71 | 0.404 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.97 | ND | 0.581
A |  | L | 5.79 | ND | 2.08 | 6.27 | ND | 1.32 | 0.756 | 3.79 | ND | 1.4 | ND | ND | ND | 1.31 | 0.224 | 0.41 | 2.01 | 2.01 | 12.2 | 7.95 | ND | 1.07 | 0.691 | 0.52 | ND | ND | ND | 0.448 | 1.24 | ND | ND | 0.247 | ND | ND | ND | ND | ND | 0.848 | ND | 0.817 | ND | 0.977 | 1.8 | ND | 3.22 | 3.4 | 2.8 | 1.58 | 1.82 | ND | 0.328 | ND | 2.41 | ND | ND | 0.252 | 1.26 | 1.42 | ND | 1.36 | ND | ND | ND
| -18 IN | C | 2.05 | 0.871 | 0.145 | ND | ND | ND | 0.802 | ND | 0.084 | ND | ND | ND | 0.102 | 0.764 | ND | 3.69 | 3.1 | ND | 11.2 | 5.1 | ND | ND | ND | 0.745 | ND | 0.354 | ND | 0.979 | ND | ND | ND | 0.288 | ND | ND | 1.72 | 0.662 | 0.029 | ND | ND | 0.211 | ND | ND | ND | ND | 5.8 | 0.813 | 1.36 | 3.74 | ND | ND | 2.86 | 0.352 | 0.615 | ND | ND | 0.563 | ND | 1.24 | ND | 1.46 | 0.184 | ND | 11.7
|  | R | 9.79 | ND | ND | ND | ND | ND | 0.048 | ND | 1.31 | 3.08 | ND | ND | 0.913 | ND | 2.7 | 1.32 | 1.29 | ND | 0.932 | 0.188 | 1.17 | 1.03 | 2.68 | 1.35 | 1.83 | 3.15 | 4.47 | ND | 0.018 | 2.61 | 1.23 | 7.97 | ND | ND | 1.35 | 0.545 | 2.84 | 3.43 | 3.68 | 3.5 | 1.48 | 1.14 | 1.08 | 2.5 | ND | ND | 4.43 | ND | ND | 0.269 | ND | 3.72 | ND | ND | 0.999 | ND | ND | ND | 0.514 | 1.65 | ND | ND | ND
A |  | L | ND | 0.11 | ND | ND | ND | 1.89 | 2.05 | ND | 0.482 | 1.29 | ND | ND | 1.08 | 0.029 | ND | 0.857 | 1.05 | 1.61 | ND | 1.62 | ND | 0.456 | ND | ND | ND | ND | 2.16 | ND | 0.204 | ND | ND | ND | 2.75 | 1.63 | 0.811 | 0.462 | 0.464 | 1.84 | 1.94 | ND | 0.205 | 1.01 | 3.09 | 0.588 | 1.65 | 3.91 | 3.29 | 2.99 | 2.76 | 0.352 | ND | 0.45 | 2.11 | ND | ND | ND | ND | 1.05 | ND | ND | 4.22 | ND | ND
| -27 IN | C | 6.05 | ND | ND | 0.657 | 0.062 | 1 | 0.21 | ND | ND | 0.835 | 0.203 | 0.459 | ND | ND | ND | 0.36 | ND | 0.99 | 0.521 | 0.915 | 1.32 | ND | 0.41 | 0.23 | 1.2 | 1.15 | ND | 3.18 | 0.783 | 3.05 | 1.73 | ND | 0.079 | 1.91 | ND | ND | 1.02 | 0.808 | 0.604 | 1.15 | ND | 0.595 | ND | ND | 1.44 | 1.75 | 2.43 | 3.2 | 0.059 | ND | 1.12 | 1.57 | ND | 0.701 | 0.701 | 0.937 | 0.296 | 0.559 | ND | 2.46 | 1.02 | 2.2 | ND
|  | R | ND | ND | 3.1 | 2.58 | ND | ND | 2.38 | ND | ND | ND | 0.125 | 0.374 | ND | ND | 0.768 | 0.344 | 3.75 | ND | 0.138 | ND | 0.133 | 1.23 | ND | ND | 1.1 | 0.652 | ND | 1.74 | 1.86 | 2.5 | ND | ND | 2.84 | 0.311 | 1.83 | 0.964 | ND | ND | 1.24 | ND | 0.79 | ND | ND | ND | 1.65 | ND | 2 | ND | 0.688 | 0.108 | ND | 0.206 | 1.21 | 0.6 | 1.34 | 1.02 | 1.77 | 0.082 | 0.023 | 0.965 | 7.58 | ND | ND
A |  | L | 9.88 | ND | 0.62 | 0.973 | 1.76 | 3.31 | ND | ND | 0.135 | ND | 0.057 | ND | ND | ND | ND | ND | 3.6 | 4.64 | 0.385 | 0.116 | 0.738 | 0.701 | 0.799 | 0.619 | ND | 1.33 | 0.095 | ND | ND | 2.8 | ND | 0.006 | 1.73 | 2.67 | 1.71 | 0.441 | 1.96 | 1.36 | 3.45 | 3.77 | 1.42 | 1.59 | 1.37 | 1.82 | 0.511 | 0.438 | 2.4 | 1.2 | 0.273 | ND | 3.02 | 0.787 | 1.9 | 0.219 | 0.592 | 1.16 | 0.83 | 0.866 | 1.64 | 0.032 | 3.48 | 2.81 | ND
| -36 IN | C | 4.06 | ND | ND | 2.73 | 0.539 | 1.16 | ND | ND | ND | ND | ND | ND | ND | ND | 0.959 | ND | 2.66 | 3.28 | 1 | 1.23 | 1.86 | ND | ND | ND | 0.688 | 1.57 | ND | ND | ND | ND | ND | ND | 2.48 | 0.89 | 1.88 | 1.36 | 0.112 | 0.598 | ND | 8.91 | 1.32 | ND | 0.304 | 0.836 | 1.24 | 0.304 | ND | 2.11 | ND | 0.028 | ND | 0.808 | ND | 0.743 | ND | 0.849 | 1.16 | 0.415 | ND | 2.66 | 0.147 | 0.056 | ND
|  | R | ND | 0.598 | 0.73 | 0.674 | 0.449 | 1.24 | 2.04 | ND | 0.3 | ND | ND | ND | 1.32 | 0.6 | 1.15 | ND | 0.697 | 2.37 | ND | 0.249 | 1.04 | 0.007 | ND | 0.464 | 0.01 | ND | ND | 1.87 | 1.2 | 0.915 | ND | 0.64 | 1.8 | 0.355 | ND | 0.554 | 1.26 | ND | 0.534 | ND | 4.96 | ND | 0.9 | 1.92 | 1.74 | ND | 2.22 | 2.75 | 1.61 | 1.95 | 1.1 | 0.545 | ND | 0.467 | ND | 1.35 | 2.64 | 1.3 | 0.066 | 0.888 | ND | ND | ND
A |  | L | ND | 0.996 | ND | 1.9 | ND | 0.602 | 4.38 | ND | ND | ND | 1.48 | ND | 1.88 | ND | 2.13 | ND | 0.717 | 0.836 | 1.49 | 0.508 | 1.48 | ND | 2.1 | ND | ND | 6.29 | ND | 3.01 | ND | 0.551 | 0.451 | 1.06 | 1.74 | 0.816 | 2.22 | 1.56 | 1.36 | 4.55 | 0.758 | 1.03 | 1.62 | ND | ND | 0.849 | 6.5 | ND | 4.84 | 0.486 | 1.72 | 1.39 | ND | 1.53 | 0.348 | ND | ND | ND | 1.22 | 0.804 | 0.612 | 2.03 | 1.58 | ND | ND
| -45 IN | C | ND | ND | 1.64 | 0.306 | ND | ND | ND | 1.7 | ND | ND | 0.755 | 0.916 | 0.641 | 0.732 | ND | 1.13 | 0.944 | 0.91 | 0.245 | ND | 2.03 | 1.46 | ND | ND | 0.763 | ND | 0.275 | 0.941 | ND | ND | ND | ND | 0.058 | 2.62 | 5.55 | ND | 8.14 | 2.33 | 0.474 | 0.149 | 3.1 | 0.876 | 0.552 | 2.83 | 0.495 | 0.447 | 2.51 | 0.571 | 1.51 | 1.06 | ND | 0.389 | ND | ND | ND | ND | 1.23 | 0.26 | 1.35 | 6.84 | 1.57 | 7.21 | ND
|  | R | ND | 1.65 | ND | 3.25 | 6.19 | 1.45 | ND | ND | ND | 0.45 | 0.444 | 2.17 | 0.518 | ND | ND | 0.408 | 0.114 | 0.808 | 1.22 | 2.77 | 0.527 | ND | 2.72 | ND | ND | 1.1 | ND | 2.94 | ND | 2.06 | 0.809 | 0.906 | 1.03 | 2.85 | ND | 1.67 | 2.47 | 2.7 | 0.413 | 1.88 | ND | 0.498 | 0.947 | 2.63 | 2 | 1.78 | 3.24 | 2.65 | 1.06 | 1.57 | ND | ND | 3.23 | 0.676 | ND | 1.76 | 2.44 | 1.43 | 3.76 | 5.75 | ND | 6 | ND
A |  | L | 17 | 1.71 | 1.69 | ND | 1 | 2.52 | ND | 3.04 | 1.44 | ND | 0.136 | ND | 2.56 | 1.55 | 2.8 | ND | ND | 0.621 | ND | 0.788 | 0.839 | 0.246 | 0.64 | 0.602 | 0.986 | 5.65 | 1.15 | 5.4 | ND | ND | ND | ND | ND | 4.19 | ND | 0.514 | 0.218 | 2.79 | 0.724 | 3.57 | 2.04 | 1.64 | 1.34 | 5.89 | 2.24 | 1.87 | 1.81 | ND | 1.01 | ND | 0.387 | 1.24 | ND | ND | ND | ND | 0.026 | 0.646 | 0.859 | 0.191 | ND | 3.09 | 3.87
| -54 IN | C | 0.148 | 0.84 | 1.71 | 2.71 | 0.786 | 1.96 | ND | ND | 0.77 | ND | 0.692 | 1.43 | 1.96 | 0.821 | 0.579 | 1.99 | 4.05 | 2.37 | 0.322 | 8.51 | 0.342 | 1.43 | ND | ND | 1.46 | 0.612 | 1.71 | 6.68 | 1.46 | ND | 0.092 | 0.963 | 0.9 | 1.38 | 1.14 | ND | 5.39 | ND | 1.21 | 0.993 | 0.184 | 1.96 | ND | 0.691 | 1.39 | 0.918 | 1.57 | 1.33 | 1.11 | 0.796 | 0.28 | 1.17 | 0.385 | 1.78 | 1.02 | 1.81 | 3.18 | 0.293 | 2.16 | 1.17 | ND | ND | 4.06
|  | R | 2.89 | 4.08 | ND | 1.8 | 2.56 | ND | ND | 1.22 | ND | 0.966 | 1.33 | ND | 1.62 | 0.079 | 1.04 | 0.788 | 1.11 | 2.5 | 0.435 | 1.22 | 0.773 | 2.37 | 3.71 | 1.66 | 1.5 | 4.03 | ND | 0.91 | 1.02 | ND | 1.25 | 1.54 | 0.07 | 0.666 | 2.59 | 1.53 | 3.3 | ND | 3.19 | ND | ND | 2.08 | ND | 0.455 | ND | 1.57 | 3.01 | ND | ND | 1.79 | ND | ND | 0.53 | 1.96 | 0.895 | 1.39 | ND | 3.34 | 1.34 | 1.85 | ND | ND | 4.45
A |  | L | 3.72 | ND | 3.92 | 2.77 | 0.805 | 4.38 | 10.1 | 0.448 | 1.03 | 1.64 | 1.83 | 2.66 | 0.06 | 1.41 | 2.48 | 3.5 | ND | 2.69 | 10.8 | 12.6 | 1.4 | 0.395 | 3.11 | 1.98 | 3.97 | 4.07 | 0.984 | 5.36 | 1.99 | ND | 2.43 | 3.97 | 0.489 | 0.447 | ND | 0.104 | 5.39 | 2.97 | 2.26 | ND | 1.58 | 0.292 | 1.08 | 0.061 | 4.08 | 0.525 | 2.94 | 13.7 | ND | 2.06 | 4.91 | 2.48 | 4.65 | 5.33 | 1.6 | 4.48 | 6.05 | ND | 0.041 | 2.82 | 4.5 | 0.618 | ND
| -63 IN | C | 2.05 | 1.5 | 2.51 | 1.87 | ND | 1.56 | 3.23 | 0.481 | 2.65 | 2.44 | 1.23 | 1.88 | 1.77 | 0.786 | 1.68 | 4.52 | ND | 2.94 | 13.6 | 12.5 | 2.89 | 0.521 | 1.85 | 1.32 | 4.42 | 2.91 | 0.566 | 2.82 | 3.18 | 1.36 | 2.12 | 1.37 | ND | 1.43 | 1.61 | 0.421 | 2.53 | 3.2 | 1.58 | 0.981 | 2.71 | 2.7 | ND | 0.018 | 4.02 | 0.475 | 4.15 | 10.6 | 6.33 | 1.67 | 0.264 | ND | ND | 3.93 | ND | 2.05 | 1.95 | 2.96 | 0.232 | 4.25 | 2.93 | 25.1 | 2.06
|  | R | 4.23 | 3.16 | 0.736 | 0.96 | ND | 3.56 | 1.96 | 0.369 | 1.77 | 0.605 | 0.824 | 0.385 | 3.01 | 1.48 | 3.08 | 1.8 | 5.64 | 0.846 | ND | 2.05 | 7.68 | 1.59 | 4.63 | 3.09 | 2.01 | 1.71 | 3.32 | 0.072 | 1.16 | 3.6 | 5.66 | ND | 4.84 | 4.98 | 2.71 | 0.154 | ND | 3.49 | 4.94 | 0.053 | 1.03 | ND | 0.14 | 0.692 | ND | 1.74 | 3.1 | 13.1 | 2.46 | 2.75 | ND | ND | 2.32 | 3.44 | 2.57 | 2.92 | 10.1 | 0.98 | 3.2 | 3.05 | 0.826 | 26.3 | 5.33
A |  | L | 22.8 | 1.86 | ND | 2.52 | 1.99 | 0.166 | 2.97 | ND | 2.57 | 10.1 | 4.17 | 3.59 | 0.54 | 0.945 | 0.193 | 3.2 | 2.81 | 3.7 | 1.47 | 2.65 | 2.54 | 0.788 | 4.53 | 4.94 | 10.3 | 0.033 | 4.37 | 8.56 | 2.31 | 1.84 | 5.67 | 2.94 | 0.204 | 0.817 | 0.244 | ND | 6.96 | 8.71 | 3.74 | 4.3 | 1.1 | 2.42 | 0.959 | 2.94 | 11.2 | 9.12 | 4.09 | ND | 5.82 | 2.56 | 11.4 | 1.28 | 6.43 | 1.4 | 11.8 | 1.51 | 2.88 | 2.46 | ND | 1.25 | 6.54 | 1.18 | 10.7
| -72 IN | C | 24.9 | ND | ND | ND | 2.99 | 2.25 | ND | 1.43 | 3.67 | 4.71 | 1.26 | 0.544 | ND | ND | 0.962 | 0.791 | 4.12 | 1.88 | 1.88 | 2.69 | 3.83 | 0.573 | 3.97 | 2.62 | 2.39 | ND | 2.63 | 2.87 | ND | 1.44 | 0.589 | ND | 3.4 | 0.381 | ND | 3.32 | 2.48 | 1.44 | 1.27 | 4.29 | 1.02 | 0.447 | 1.62 | 1.27 | ND | 6.54 | 4.85 | 0.368 | 2.02 | 1.93 | 3.34 | 4.58 | 0.884 | 0.376 | 6.25 | 1.6 | 2.09 | 0.647 | 5.54 | 1.93 | 2.09 | 0.358 | 14
|  | R | 30.8 | ND | 0.619 | 2.52 | 4.38 | 2.59 | 7.52 | 2.13 | 4.45 | 10.7 | 0.628 | 0.888 | 3.42 | 0.915 | 2.4 | 2.4 | 2.79 | 5.48 | 1.26 | 5.62 | 3.33 | 3.99 | ND | 3.62 | 0.66 | 3.25 | 3.91 | ND | 2.22 | 0.906 | 1.72 | 2.37 | 0.833 | 1.01 | 3.11 | 17.2 | 10.1 | 1.57 | 3.1 | 2.74 | 3.08 | 2.37 | 1.38 | 1.57 | 5.03 | 4.15 | 0.716 | 6.36 | 1.8 | 6.71 | 2.94 | 1.57 | 2.34 | 3.99 | 3.58 | 2.55 | 2.7 | 2.71 | 2 | 2.02 | 3.37 | 2.39 | 9.27
A |  | L | ND | 16.2 | 1.16 | 3.38 | 1.61 | 8.45 | 5.77 | 1.88 | 3.35 | 9.81 | 3.15 | 3.13 | 0.167 | 1.24 | ND | 0.516 | 3.82 | 0.493 | 8.74 | 3.75 | 2.61 | 7.61 | ND | 3.83 | 5.73 | 0.819 | 3.55 | 3.53 | ND | 1.71 | 0.703 | 0.031 | 1.01 | 0.698 | 2.44 | 1.69 | 9.82 | 6.61 | 1.8 | 3.93 | 0.689 | 0.176 | 1.42 | 1.73 | 2.24 | 3.15 | 3.33 | ND | ND | 1.35 | 1.55 | 5.22 | 0.696 | 1.55 | ND | ND | 4.63 | 3.76 | 4.6 | 2.67 | ND | ND | 32.3
| -81 IN | C | 22.6 | 2.38 | ND | 0.422 | 0.578 | 1.28 | 2.86 | 2.47 | ND | 1.38 | 1.89 | 1.5 | 2.02 | ND | 0.898 | 1.75 | 1.04 | 5.8 | 11.9 | 6.63 | 3.75 | 6.02 | ND | 1.15 | 0.258 | 1.98 | ND | ND | ND | ND | ND | ND | ND | ND | 1.08 | 4.36 | 9.16 | 3.41 | ND | 0.62 | 1.34 | 1.19 | 3.09 | ND | ND | 2.05 | 13.8 | ND | ND | 1.44 | 1.5 | 1.86 | 0.862 | 1.73 | 1.92 | 1.9 | 1.46 | 3.69 | 1.6 | ND | ND | 3.43 | 28.2
|  | R | ND | ND | 3.06 | 2.68 | 5.13 | 0.217 | 6.85 | 5.06 | ND | 3.89 | 1.93 | 0.529 | 4.65 | 1.78 | 2.34 | 1.08 | ND | 9.44 | ND | 0.735 | 2.42 | 2.16 | ND | 2.67 | 0.611 | 2.22 | 6.25 | 0.097 | 2.9 | ND | ND | ND | 0.727 | ND | 0.552 | 4.82 | 4.13 | 1.87 | 0.692 | 6.13 | 1.03 | 3.18 | 3.72 | ND | ND | 1.74 | 5.18 | ND | ND | 2.68 | 4.4 | 7.21 | 4.3 | 3.12 | 2.44 | 1.72 | 2.4 | 3.81 | 9.35 | ND | ND | ND | ND
A | POSITION A | L | ND | ND | ND | ND | 1.88 | ND | ND | ND | ND | ND | 2.52 | ND | ND | 3.06 | ND | 4.27 | 2.73 | ND | 0.799 | 1.8 | ND | 0.807 | 2.5 | ND | 2.05 | 1.17 | ND | ND | 0.195 | 1.28 | ND | ND | ND | ND | ND | ND | ND | ND | 0.586 | 3.36 | ND | ND | 0.65 | ND | ND | 4.67 | ND | 2.62 | 1.58 | ND | ND | 1.35 | ND | ND | 1.07 | ND | 1.19 | 1.1 | ND | 0.105 | 0.024 | ND | ND
| OF THE | C | ND | ND | ND | 1.09 | 2.27 | ND | 0.564 | 0.696 | ND | 0.668 | ND | ND | ND | 3.38 | ND | 0.481 | 2.67 | ND | 3.54 | 3.06 | ND | 3.6 | 1.59 | ND | 2.41 | ND | ND | ND | 1.89 | ND | ND | ND | 1.42 | ND | 0.707 | 1.55 | ND | ND | 1.66 | 1.92 | ND | 0.816 | 1.63 | ND | 3.24 | 4.23 | ND | 0.918 | 0.993 | ND | 3.64 | ND | ND | ND | 1.93 | ND | ND | 1.96 | ND | 0.046 | 1.55 | ND | ND
| PRIMARIES | R | ND | ND | ND | 3.07 | 2.16 | ND | 0.653 | 3.24 | ND | 3.21 | 1.32 | ND | 0.454 | 3.02 | ND | 3.02 | 3.21 | ND | 2.09 | 2.27 | ND | 3.7 | 3.37 | ND | 3.03 | 1.46 | ND | ND | 4.2 | 0.362 | ND | 1.94 | 1.99 | ND | ND | 2.93 | ND | ND | 2.24 | 0.952 | ND | ND | ND | ND | 3.15 | 4.01 | ND | 4.71 | 0.225 | ND | 0.549 | ND | ND | ND | 1.27 | ND | ND | 0.708 | ND | 2.94 | ND | ND | ND
A | POSITION B | L | ND | ND | ND | 2.44 | 3.11 | ND | 1.43 | 4.58 | ND | 2.16 | 1.16 | ND | 2.59 | 4.68 | ND | 3.36 | 4.48 | ND | 2.64 | 3.01 | ND | 3.91 | 2.53 | ND | 1.47 | 2.84 | ND | ND | 2.28 | 0.299 | ND | 0.308 | 1.72 | ND | ND | 0.281 | ND | ND | 2.12 | 4.01 | ND | ND | 0.269 | ND | 3.76 | 3.47 | ND | 4.18 | 2.42 | ND | 3.18 | 2.42 | ND | 1.33 | 1.98 | ND | 3.68 | 3.43 | ND | 1.37 | 1.1 | ND | ND
| OF THE | C | ND | ND | ND | 4.28 | 2.32 | ND | 1.85 | 2.58 | ND | 0.167 | 1.6 | ND | 2.57 | 3.44 | ND | 3.7 | 3.84 | ND | 2.1 | 2.07 | ND | 2.7 | 2.86 | ND | 0.175 | 3.22 | ND | ND | 0.733 | 1.94 | ND | 0.68 | 0.639 | ND | ND | 2.05 | ND | ND | ND | 3.19 | ND | 0.642 | 1.09 | ND | 2.32 | 2.49 | ND | 2.11 | 1.34 | ND | 0.195 | 0.047 | ND | ND | 2.38 | ND | 3.3 | 1.35 | ND | 2.67 | 0.611 | ND | ND
| PRIMARIES | R | ND | ND | ND | 3.28 | 0.522 | ND | 2.46 | 2.9 | ND | 0.103 | 3.34 | ND | 4.77 | 2.23 | ND | 1.11 | 3.51 | ND | 2.56 | 2.49 | ND | 1.25 | 2.6 | ND | 0.213 | 1.68 | ND | ND | 0.365 | 0.261 | ND | 1.92 | 1.48 | ND | 1.59 | 0.824 | ND | ND | 2.09 | 1.71 | ND | 2.03 | 0.445 | ND | 4.84 | 0.599 | ND | 2.24 | 2.09 | ND | 2.51 | 1.47 | ND | 2.35 | 2.06 | ND | 1.45 | 0.915 | ND | 1.92 | 1.25 | ND | ND
A | POSITION C | L | ND | ND | ND | 2.64 | 3.44 | ND | 4.36 | 2.13 | ND | 0.52 | 2.32 | ND | ND | 1.24 | ND | 1.59 | 4.71 | ND | 1.34 | 2.42 | ND | 4.51 | 4.24 | ND | 0.951 | 1.03 | ND | ND | 1.99 | 2.5 | ND | ND | 1.11 | ND | 1.31 | 3.12 | ND | ND | 1.28 | 2.82 | ND | 0.183 | 3.11 | ND | 3.68 | 8.97 | ND | 1.68 | 5.65 | ND | 1.96 | 0.124 | ND | 0.19 | 2.23 | ND | 2.41 | 3.19 | ND | 0.512 | 1.1 | ND | ND
| OF THE | C | ND | ND | ND | 4.05 | 4.56 | ND | 0.483 | 3.19 | ND | 2.04 | 1.52 | ND | 5.28 | 4.01 | ND | 0.851 | 5.78 | ND | 3.91 | 0.644 | ND | 3.55 | 3.47 | ND | 2.33 | 1.06 | ND | ND | 3.2 | 2 | ND | 2.28 | 0.689 | ND | 2.37 | 1.68 | ND | ND | 3.99 | 1.62 | ND | 4.01 | 2.41 | ND | 5.41 | 5.64 | ND | 5.44 | 3.28 | ND | ND | 1.29 | ND | 1.76 | 3 | ND | 1.64 | 2.81 | ND | 5.05 | 0.409 | ND | ND
| PRIMARIES | R | ND | ND | ND | 2.59 | 5.5 | ND | ND | 3.09 | ND | 2.64 | 2.43 | ND | 3.98 | 3.07 | ND | 2.79 | 1.96 | ND | 5.94 | 1.71 | ND | 1.7 | 5.61 | ND | 2.96 | 2.01 | ND | ND | ND | 2 | ND | 0.215 | ND | ND | 1.57 | 3.1 | ND | ND | 2.08 | 1.76 | ND | 1.48 | 2.7 | ND | 9.24 | 1.23 | ND | 9.07 | 4.95 | ND | 2.82 | 1.64 | ND | ND | 2.3 | ND | 0.55 | 0.991 | ND | 3.7 | ND | ND | ND
A |  | L | ND | ND | 0.315 | 1.96 | 0.705 | 6.78 | ND | ND | 7.5 | 3.95 | ND | 4.44 | 4.11 | 2.07 | ND | ND | ND | 2.89 | 2.24 | 7.43 | ND | 1.82 | ND | 8.48 | 0.955 | 3.47 | ND | ND | 2.23 | ND | 6.62 | ND | 11.9 | ND | 1.32 | 1.6 | 0.455 | 2.79 | 2.02 | ND | ND | 5.38 | 3.61 | ND | ND | 14.7 | 1.6 | ND | 0.414 | 0.574 | 0.015 | 2.18 | 1.68 | 4.71 | 2.2 | 0.078 | 2.7 | 2.35 | ND | 5.66 | 14.2 | ND | ND
| -90 IN | C | 8.28 | ND | 0.337 | ND | ND | ND | ND | 0.391 | 0.42 | 1.45 | ND | 3.01 | 2.05 | ND | ND | 2.46 | 4.34 | 0.278 | 2.98 | 9.56 | ND | ND | ND | 2.32 | ND | 0.691 | 2.59 | 7.19 | 1.99 | ND | 1.94 | ND | ND | 0.21 | 0.54 | ND | ND | 2.57 | 0.677 | ND | ND | 3.07 | 1.46 | ND | ND | 10 | ND | ND | ND | 1.28 | ND | 2.74 | 1.09 | 1.51 | ND | ND | 1.92 | 5.33 | ND | 1.74 | 7.08 | 7.7 | ND
|  | R | ND | ND | ND | ND | 3.27 | 6.98 | ND | ND | 0.986 | 0.841 | ND | 0.017 | 1.56 | ND | ND | ND | 1.94 | ND | 2.02 | ND | ND | ND | 3.67 | 1.56 | ND | 5.24 | ND | 1.25 | 0.767 | 0.1 | 3.63 | ND | 2.08 | 0.086 | ND | ND | ND | ND | 3.71 | 0.332 | ND | ND | ND | ND | ND | 9.57 | 4.14 | ND | ND | 3.92 | 9.9 | 5.75 | 1.14 | 0.93 | 1.69 | 2.12 | 4.77 | 4 | 14.1 | ND | 3.34 | ND | ND
A | POSITION A | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.388 | 2.19 | 4.45 | 1.98 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5.93 | 6.41 | 11.4 | 7.17 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 7.53 | 3.34 | 1.25 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 6.35 | 4.42 | 2.99 | 6.47 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| SMELTS | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 15 | ND | 1.22 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5.3 | 4.02 | 6.24 | 6.85 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION B | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.79 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 9.17 | 4.52 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4.75 | 2.28 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.39 | 0.115 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| SMELTS | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.88 | 3.14 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.19 | 5.62 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION C | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 7.3 | 4.58 | 0.972 | 4.12 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 12.9 | ND | 6.4 | 9.25 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4.13 | ND | 0.538 | 3.92 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 10.4 | 4.78 | 6.26 | 7.3 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| SMELTS | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5.85 | 0.481 | 3.64 | 2.67 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 7.54 | 4.54 | 11.7 | 8.27 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | AVG | MAX
| CORROSION RATE (mpy): |  | 10: NOTE: CORROSION RATES ARE BASED ON COMPARISON OF; 30: TEST RESULTS |  |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | < 0 mpy (LOSS) or no data |  | 30: OVERALL CORROSION RATE (mils per year):
| 0-10 mpy (LOSS) |  | 10: 2020, 2022, 2023, 2024, 2025 |  |  |  | CALCULATED CORROSION RATE
| 10-20 mpy (LOSS) |  | 10: INSPECTION DATA; 30: 2.319
| > 20 mpy (LOSS) |  | 10: ND; 15: NO COMPARISON DATA
CORROSION
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Projection
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. PROJECTED THICKNESS MEASUREMENTS ARE IN INCHES. | [67 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | AVG | MIN
B | POSITION A | L | 29: 0.184; 30: 0.192; 31: 0.199; 32: 0.201; 33: 0.187; 34: 0.202
0.099 | OF THE | C | 29: 0.19; 30: 0.2; 31: 0.206; 32: 0.205; 33: 0.181; 34: 0.203
| MANWAY | R | 29: 0.195; 30: 0.191; 31: 0.217; 32: 0.204; 33: 0.201; 34: 0.206
B | POSITION B | L | 29: 0.201; 30: 0.18; 31: 0.19; 32: 0.208; 33: 0.218; 34: 0.207
0.099 | OF THE | C | 29: 0.207; 30: 0.2; 31: 0.209; 32: 0.2; 33: 0.211; 34: 0.196
| MANWAY | R | 29: 0.205; 30: 0.188; 31: 0.191; 32: 0.208; 33: 0.195; 34: 0.18
B | POSITION C | L | 29: 0.191; 30: 0.189; 31: 0.187; 32: 0.211; 33: 0.212; 34: 0.214
0.099 | OF THE | C | 29: 0.197; 30: 0.196; 31: 0.201; 32: 0.204; 33: 0.199; 34: 0.202
| MANWAY | R | 29: 0.191; 30: 0.179; 31: 0.209; 32: 0.198; 33: 0.192; 34: 0.196
B | POSITION D | L | 29: 0.21; 30: 0.188; 31: 0.196; 32: 0.206; 33: 0.214; 34: 0.204
0.099 | OF THE | C | 29: 0.212; 30: 0.196; 31: 0.189; 32: 0.201; 33: 0.201; 34: 0.206
| MANWAY | R | 29: 0.209; 30: 0.19; 31: 0.202; 32: 0.192; 33: 0.213; 34: 0.188
B | POSITION E | L | 29: 0.138; 30: 0.194; 31: 0.202; 32: 0.199; 33: 0.199; 34: 0.193
0.099 | OF THE | C | 29: 0.2; 30: 0.187; 31: 0.216; 32: 0.209; 33: 0.199; 34: 0.197
| MANWAY | R | 29: 0.181; 30: 0.198; 31: 0.193; 32: 0.179; 33: 0.174; 34: 0.2
B | POSITION A | L | 18: 0.172; 19: 0.095; 20: 0.184; 21: 0.168; 22: 0.127; 23: 0.168; 40: 0.179; 41: 0.158; 42: 0.185; 43: 0.147; 44: 0.167; 45: 0.168
0.099 | OF THE | C | 18: 0.182; 19: 0.094; 20: 0.172; 21: 0.183; 22: 0.083; 23: 0.175; 40: 0.173; 41: 0.168; 42: 0.185; 43: 0.172; 44: 0.145; 45: 0.176
| TERTIARIES | R | 18: 0.171; 19: 0.109; 20: 0.174; 21: 0.177; 22: 0.076; 23: 0.173; 40: 0.174; 41: 0.16; 42: 0.169; 43: 0.179; 44: 0.168; 45: 0.181
B | POSITION B | L | 18: 0.179; 19: RT; 20: 0.175; 21: 0.174; 22: RT; 23: 0.168; 40: 0.178; 41: RT; 42: 0.178; 43: 0.171; 44: RT; 45: 0.193
0.099 | OF THE | C | 18: 0.163; 19: RT; 20: 0.182; 21: 0.173; 22: RT; 23: 0.17; 40: 0.181; 41: RT; 42: 0.178; 43: 0.178; 44: RT; 45: 0.18
| TERTIARIES | R | 18: 0.168; 19: RT; 20: 0.173; 21: 0.176; 22: RT; 23: 0.174; 40: 0.179; 41: RT; 42: 0.18; 43: 0.173; 44: RT; 45: 0.181
B | POSITION C | L | 18: 0.182; 19: 0.113; 20: 0.184; 21: 0.164; 22: 0.13; 23: 0.164; 40: 0.18; 41: 0.136; 42: 0.181; 43: 0.159; 44: 0.135; 45: 0.169
0.099 | OF THE | C | 18: 0.173; 19: 0.094; 20: 0.176; 21: 0.174; 22: 0.142; 23: 0.181; 40: 0.18; 41: 0.116; 42: 0.177; 43: 0.18; 44: 0.128; 45: 0.175
| TERTIARIES | R | 18: 0.161; 19: 0.085; 20: 0.16; 21: 0.181; 22: 0.147; 23: 0.175; 40: 0.177; 41: 0.107; 42: 0.169; 43: 0.178; 44: 0.129; 45: 0.177
A |  | L | 0.329 | 0.165 | 0.218 | 0.236 | 0.225 | 0.239 | 0.218 | 0.23 | 0.226 | 0.224 | 0.212 | 0.218 | 0.236 | 0.226 | 0.225 | 0.267 | 0.335 | 0.333 | 0.276 | 0.229 | 0.232 | 0.229 | 0.199 | 0.235 | 0.228 | 0.224 | 0.233 | 0.229 | 0.229 | 0.233 | 0.231 | 0.226 | 0.207 | 0.227 | 0.234 | 0.229 | 0.222 | 0.221 | 0.219 | 0.224 | 0.228 | 0.219 | 0.226 | 0.221 | 0.268 | 0.327 | 0.334 | 0.266 | 0.207 | 0.223 | 0.202 | 0.183 | 0.206 | 0.224 | 0.186 | 0.233 | 0.195 | 0.181 | 0.21 | 0.225 | 0.23 | RF | RF
0.083 | +16 FT 6 IN | C | 0.334 | 0.187 | 0.226 | 0.219 | 0.227 | 0.207 | 0.227 | 0.229 | 0.23 | 0.229 | 0.199 | 0.222 | 0.228 | 0.227 | 0.217 | 0.265 | 0.337 | 0.333 | 0.266 | 0.229 | 0.22 | 0.225 | 0.226 | 0.232 | 0.23 | 0.223 | 0.229 | 0.229 | 0.231 | 0.227 | 0.235 | 0.227 | 0.215 | 0.23 | 0.223 | 0.223 | 0.229 | 0.231 | 0.217 | 0.226 | 0.229 | 0.22 | 0.225 | 0.211 | 0.265 | 0.324 | 0.304 | 0.269 | 0.2 | 0.23 | 0.216 | 0.211 | 0.209 | 0.226 | 0.214 | 0.218 | 0.182 | 0.178 | 0.222 | 0.225 | 0.223 | RF | RF
|  | R | 0.326 | 0.232 | 0.215 | 0.216 | 0.224 | 0.203 | 0.226 | 0.231 | 0.228 | 0.232 | 0.2 | 0.222 | 0.222 | 0.229 | 0.213 | 0.267 | 0.34 | 0.354 | 0.269 | 0.236 | 0.232 | 0.229 | 0.224 | 0.229 | 0.233 | 0.226 | 0.226 | 0.229 | 0.225 | 0.142 | 0.227 | 0.214 | 0.228 | 0.229 | 0.227 | 0.23 | 0.228 | 0.233 | 0.226 | 0.231 | 0.226 | 0.219 | 0.226 | 0.229 | 0.269 | 0.328 | 0.306 | 0.272 | 0.211 | 0.226 | 0.216 | 0.208 | 0.208 | 0.228 | 0.214 | 0.212 | 0.209 | 0.211 | 0.216 | 0.224 | 0.231 | 0.089 | RF
A |  | L | 0.176 | RF | 0.22 | 0.21 | 0.22 | 0.189 | 0.204 | 0.229 | 0.222 | 0.225 | 0.177 | 0.186 | 0.213 | 0.224 | 0.224 | 0.268 | 0.335 | 0.339 | 0.269 | 0.185 | 0.229 | 0.223 | 0.225 | 0.181 | 0.23 | 0.221 | 0.22 | 0.219 | 0.224 | 0.23 | 0.229 | 0.238 | 0.215 | 0.224 | 0.229 | 0.229 | 0.227 | 0.227 | 0.224 | 0.228 | 0.226 | 0.221 | 0.227 | 0.223 | 0.257 | 0.329 | 0.308 | 0.263 | 0.194 | 0.21 | 0.221 | 0.221 | 0.212 | 0.226 | 0.227 | 0.227 | 0.195 | 0.218 | 0.227 | 0.199 | 0.221 | 0.218 | 0.183
0.083 | +15 FT | C | RF | 0.212 | 0.215 | 0.218 | 0.211 | 0.187 | 0.22 | 0.22 | 0.229 | 0.228 | 0.215 | 0.227 | 0.228 | 0.22 | 0.228 | 0.261 | 0.323 | 0.337 | 0.272 | 0.225 | 0.222 | 0.223 | 0.22 | 0.227 | 0.225 | 0.221 | 0.224 | 0.228 | 0.218 | 0.23 | 0.224 | 0.231 | 0.223 | 0.219 | 0.221 | 0.225 | 0.219 | 0.219 | 0.221 | 0.227 | 0.227 | 0.228 | 0.225 | 0.227 | 0.266 | 0.329 | 0.296 | 0.259 | 0.19 | 0.219 | 0.213 | 0.217 | 0.213 | 0.225 | 0.226 | 0.226 | 0.229 | 0.217 | 0.228 | 0.219 | 0.227 | 0.225 | RF
|  | R | RF | 0.206 | 0.188 | 0.223 | 0.22 | 0.176 | 0.214 | 0.228 | 0.197 | 0.221 | 0.214 | 0.226 | 0.226 | 0.218 | 0.226 | 0.269 | 0.327 | 0.337 | 0.272 | 0.223 | 0.226 | 0.225 | 0.225 | 0.22 | 0.228 | 0.206 | 0.225 | 0.229 | 0.219 | 0.229 | 0.224 | 0.233 | 0.224 | 0.225 | 0.217 | 0.224 | 0.221 | 0.228 | 0.22 | 0.226 | 0.226 | 0.22 | 0.228 | 0.224 | 0.267 | 0.33 | 0.295 | 0.262 | 0.183 | 0.209 | 0.212 | 0.224 | 0.186 | 0.228 | 0.218 | 0.225 | 0.219 | 0.219 | 0.224 | 0.228 | 0.231 | 0.229 | RF
A |  | L | 0.232 | 0.205 | 0.215 | 0.211 | 0.196 | 0.209 | 0.219 | 0.217 | 0.212 | 0.23 | 0.228 | 0.215 | 0.23 | 0.226 | 0.229 | 0.244 | 0.333 | 0.304 | 0.253 | 0.205 | 0.213 | 0.218 | 0.199 | 0.208 | 0.221 | 0.228 | 0.234 | 0.215 | 0.229 | 0.231 | 0.235 | 0.231 | 0.229 | 0.227 | 0.233 | 0.22 | 0.232 | 0.227 | 0.219 | 0.225 | 0.225 | 0.221 | 0.231 | 0.222 | 0.261 | 0.311 | 0.315 | 0.265 | 0.228 | 0.226 | 0.215 | 0.191 | 0.218 | 0.221 | 0.212 | 0.215 | 0.22 | 0.227 | 0.229 | 0.23 | 0.219 | 0.227 | RF
0.083 | +13 FT 6 IN | C | 0.278 | 0.145 | 0.207 | 0.229 | 0.204 | 0.219 | 0.218 | 0.213 | 0.19 | 0.226 | 0.216 | 0.229 | 0.227 | 0.221 | 0.234 | 0.262 | 0.34 | 0.33 | 0.272 | 0.191 | 0.123 | 0.227 | 0.221 | 0.22 | 0.23 | 0.216 | 0.225 | 0.226 | 0.228 | 0.226 | 0.232 | 0.23 | 0.225 | 0.221 | 0.23 | 0.217 | 0.213 | 0.205 | 0.225 | 0.22 | 0.224 | 0.216 | 0.23 | 0.205 | 0.259 | 0.313 | 0.313 | 0.268 | 0.223 | 0.222 | 0.228 | 0.19 | 0.223 | 0.225 | 0.218 | 0.205 | 0.222 | 0.228 | 0.23 | 0.209 | 0.22 | 0.226 | RF
|  | R | 0.27 | 0.192 | 0.217 | 0.208 | 0.21 | 0.22 | 0.224 | 0.215 | 0.209 | 0.224 | 0.202 | 0.227 | 0.214 | 0.221 | 0.231 | 0.26 | 0.327 | 0.319 | 0.268 | 0.216 | 0.222 | 0.213 | 0.202 | 0.211 | 0.221 | 0.223 | 0.224 | 0.22 | 0.231 | 0.225 | 0.234 | 0.221 | 0.224 | 0.228 | 0.212 | 0.217 | 0.229 | 0.214 | 0.227 | 0.217 | 0.233 | 0.227 | 0.23 | 0.224 | 0.259 | 0.331 | 0.321 | 0.263 | 0.232 | 0.23 | 0.213 | 0.192 | 0.22 | 0.205 | 0.21 | 0.216 | 0.217 | 0.229 | 0.225 | 0.223 | 0.218 | 0.227 | RF
A |  | L | 0.254 | 0.214 | 0.207 | 0.214 | 0.224 | 0.219 | 0.2 | 0.221 | 0.213 | 0.21 | 0.22 | 0.208 | 0.221 | 0.212 | 0.211 | 0.244 | 0.315 | 0.293 | 0.261 | 0.216 | 0.199 | 0.204 | 0.22 | 0.21 | 0.216 | 0.207 | 0.214 | 0.216 | 0.205 | 0.213 | 0.215 | 0.229 | 0.221 | 0.226 | 0.219 | 0.224 | 0.203 | 0.215 | 0.226 | 0.21 | 0.196 | 0.21 | 0.216 | 0.085 | 0.255 | 0.308 | 0.296 | 0.235 | 0.197 | 0.21 | 0.214 | 0.217 | 0.202 | 0.219 | 0.217 | 0.218 | 0.22 | 0.211 | 0.228 | 0.231 | 0.225 | 0.205 | RF
0.083 | +12 FT | C | 0.276 | 0.21 | 0.207 | 0.226 | 0.221 | 0.213 | 0.199 | 0.22 | 0.219 | 0.205 | 0.209 | 0.217 | 0.219 | 0.197 | 0.204 | 0.243 | 0.319 | 0.309 | 0.256 | 0.209 | 0.211 | 0.216 | 0.212 | 0.227 | 0.211 | 0.203 | 0.223 | 0.227 | 0.226 | 0.213 | 0.217 | 0.229 | 0.228 | 0.233 | 0.225 | 0.226 | 0.196 | 0.217 | 0.213 | 0.207 | 0.201 | 0.217 | 0.216 | 0.099 | 0.258 | 0.312 | 0.312 | 0.244 | 0.204 | 0.202 | 0.21 | 0.212 | 0.208 | 0.224 | 0.228 | 0.224 | 0.222 | 0.231 | 0.228 | 0.229 | 0.224 | 0.207 | RF
|  | R | 0.285 | 0.195 | 0.197 | 0.229 | 0.204 | 0.223 | 0.187 | 0.219 | 0.206 | 0.2 | 0.207 | 0.216 | 0.221 | 0.208 | 0.204 | 0.25 | 0.309 | 0.289 | 0.251 | 0.212 | 0.201 | 0.222 | 0.21 | 0.227 | 0.215 | 0.209 | 0.217 | 0.212 | 0.211 | 0.215 | 0.212 | 0.233 | 0.219 | 0.228 | 0.227 | 0.217 | 0.206 | 0.215 | 0.209 | 0.207 | 0.211 | 0.216 | 0.204 | 0.08 | 0.258 | 0.313 | 0.326 | 0.235 | 0.191 | 0.199 | 0.214 | 0.216 | 0.196 | 0.225 | 0.225 | 0.226 | 0.229 | 0.213 | 0.225 | 0.228 | 0.22 | 0.209 | RF
A | POSITION A | L | 3: 0.211; 4: 0.194; 5: 0.201; 6: 0.212; 58: 0.215; 59: 0.221; 60: 0.215; 61: 0.22
0.083 | OF THE | C | 3: 0.195; 4: 0.237; 5: 0.207; 6: 0.211; 58: 0.218; 59: 0.211; 60: 0.209; 61: 0.222
| OB PORTS | R | 3: 0.204; 4: 0.222; 5: 0.197; 6: 0.21; 58: 0.216; 59: 0.211; 60: 0.197; 61: 0.216
A | POSITION B | L | 3: 0.202; 4: 0.189; 5: 0.199; 6: 0.212; 58: 0.221; 59: 0.212; 60: 0.213; 61: 0.198
0.083 | OF THE | C | 3: 0.229; 4: 0.199; 5: 0.188; 6: 0.216; 58: 0.216; 59: 0.215; 60: 0.217; 61: 0.202
| OB PORTS | R | 3: 0.203; 4: 0.209; 5: 0.198; 6: 0.222; 58: 0.218; 59: 0.204; 60: 0.22; 61: 0.211
A | POSITION C | L | 3: 0.221; 4: 0.205; 5: 0.212; 6: 0.224; 58: 0.209; 59: 0.209; 60: 0.214; 61: 0.218
0.083 | OF THE | C | 3: 0.209; 4: 0.227; 5: 0.198; 6: 0.228; 58: 0.216; 59: 0.204; 60: 0.224; 61: 0.218
| OB PORTS | R | 3: 0.22; 4: 0.207; 5: 0.21; 6: 0.213; 58: 0.205; 59: 0.212; 60: 0.241; 61: 0.228
A |  | L | 0.325 | 0.2 | 0.196 | 0.205 | 0.209 | 0.21 | 0.207 | 0.186 | 0.203 | 0.198 | 0.199 | 0.207 | 0.198 | 0.201 | 0.193 | 0.227 | 0.3 | 0.318 | 0.259 | 0.203 | 0.209 | 0.204 | 0.184 | 0.203 | 0.197 | 0.221 | 0.21 | 0.218 | 0.223 | 0.226 | 0.213 | 0.216 | 0.221 | 0.213 | 0.212 | 0.204 | 0.208 | 0.197 | 0.212 | 0.202 | 0.209 | 0.207 | 0.216 | 0.221 | 0.259 | 0.304 | 0.315 | 0.265 | 0.22 | 0.227 | 0.212 | 0.213 | 0.219 | 0.214 | 0.217 | 0.202 | 0.224 | 0.229 | 0.202 | 0.216 | 0.228 | 0.228 | RF
0.083 | +10 FT 6 IN | C | 0.331 | 0.202 | 0.206 | 0.199 | 0.201 | 0.21 | 0.204 | 0.192 | 0.209 | 0.21 | 0.213 | 0.205 | 0.19 | 0.218 | 0.19 | 0.242 | 0.301 | 0.307 | 0.257 | 0.203 | 0.207 | 0.207 | 0.191 | 0.201 | 0.222 | 0.209 | 0.207 | 0.212 | 0.216 | 0.215 | 0.223 | 0.213 | 0.219 | 0.218 | 0.216 | 0.221 | 0.209 | 0.194 | 0.213 | 0.201 | 0.207 | 0.214 | 0.197 | 0.208 | 0.249 | 0.326 | 0.319 | 0.265 | 0.214 | 0.216 | 0.207 | 0.214 | 0.218 | 0.219 | 0.211 | 0.226 | 0.227 | 0.223 | 0.207 | 0.214 | 0.235 | 0.227 | RF
|  | R | 0.328 | 0.2 | 0.212 | 0.212 | 0.201 | 0.206 | 0.209 | 0.204 | 0.218 | 0.211 | 0.209 | 0.202 | 0.206 | 0.201 | 0.201 | 0.223 | 0.302 | 0.297 | 0.252 | 0.194 | 0.199 | 0.205 | 0.198 | 0.211 | 0.198 | 0.211 | 0.21 | 0.217 | 0.213 | 0.218 | 0.227 | 0.214 | 0.216 | 0.209 | 0.217 | 0.225 | 0.198 | 0.19 | 0.203 | 0.211 | 0.193 | 0.207 | 0.202 | 0.209 | 0.244 | 0.325 | 0.313 | 0.266 | 0.22 | 0.221 | 0.196 | 0.221 | 0.206 | 0.216 | 0.221 | 0.224 | 0.227 | 0.211 | 0.211 | 0.212 | 0.235 | 0.221 | RF
A |  | L | 0.241 | 0.2 | 0.213 | 0.219 | 0.21 | 0.209 | 0.223 | 0.209 | 0.213 | 0.205 | 0.194 | 0.215 | 0.202 | 0.214 | 0.183 | 0.22 | 0.308 | 0.298 | 0.239 | 0.183 | 0.186 | 0.192 | 0.192 | 0.186 | 0.184 | 0.209 | 0.192 | 0.186 | 0.204 | 0.205 | 0.222 | 0.225 | 0.216 | 0.2 | 0.203 | 0.205 | 0.212 | 0.189 | 0.22 | 0.209 | 0.219 | 0.207 | 0.196 | 0.215 | 0.247 | 0.294 | 0.316 | 0.238 | 0.227 | 0.194 | 0.208 | 0.203 | 0.219 | 0.202 | 0.218 | 0.224 | 0.22 | 0.218 | 0.216 | 0.21 | 0.198 | 0.199 | RF
0.083 | +9 FT | C | 0.276 | 0.181 | 0.21 | 0.216 | 0.219 | 0.225 | 0.229 | 0.221 | 0.219 | 0.211 | 0.205 | 0.214 | 0.198 | 0.21 | 0.207 | 0.23 | 0.314 | 0.302 | 0.232 | 0.189 | 0.205 | 0.197 | 0.185 | 0.194 | 0.199 | 0.207 | 0.188 | 0.202 | 0.208 | 0.211 | 0.208 | 0.217 | 0.219 | 0.205 | 0.212 | 0.211 | 0.218 | 0.201 | 0.215 | 0.212 | 0.199 | 0.217 | 0.209 | 0.214 | 0.248 | 0.307 | 0.322 | 0.241 | 0.218 | 0.203 | 0.216 | 0.203 | 0.22 | 0.209 | 0.222 | 0.224 | 0.213 | 0.227 | 0.212 | 0.206 | 0.198 | 0.17 | 0.255
|  | R | 0.294 | 0.189 | 0.215 | 0.198 | 0.212 | 0.22 | 0.223 | 0.204 | 0.208 | 0.211 | 0.204 | 0.213 | 0.201 | 0.213 | 0.197 | 0.231 | 0.303 | 0.301 | 0.227 | 0.184 | 0.188 | 0.208 | 0.182 | 0.179 | 0.194 | 0.197 | 0.18 | 0.195 | 0.207 | 0.207 | 0.207 | 0.209 | 0.197 | 0.211 | 0.201 | 0.196 | 0.214 | 0.199 | 0.204 | 0.214 | 0.212 | 0.2 | 0.195 | 0.197 | 0.232 | 0.312 | 0.319 | 0.223 | 0.219 | 0.223 | 0.212 | 0.208 | 0.221 | 0.225 | 0.223 | 0.219 | 0.231 | 0.227 | 0.207 | 0.225 | 0.202 | 0.172 | RF
A | POSITION A | L | 29: 0.219; 30: 0.207; 31: 0.224; 32: 0.198; 33: 0.219; 34: 0.224
0.083 | OF THE | C | 29: 0.215; 30: 0.211; 31: 0.21; 32: 0.225; 33: 0.21; 34: 0.215
| OSCILLATOR | R | 29: 0.219; 30: 0.19; 31: 0.203; 32: 0.23; 33: 0.223; 34: 0.211
A | POSTION B | L | 29: 0.229; 30: 0.22; 31: 0.224; 32: 0.218; 33: 0.219; 34: 0.217
0.083 | OF THE | C | 29: 0.221; 30: 0.208; 31: 0.217; 32: 0.202; 33: 0.214; 34: 0.216
| OSCILLATOR | R | 29: 0.219; 30: 0.2; 31: 0.226; 32: 0.222; 33: 0.214; 34: 0.219
A | POSITION C | L | 29: 0.203; 30: 0.23; 31: 0.213; 32: 0.217; 33: 0.22; 34: 0.224
0.083 | OF THE | C | 29: 0.207; 30: 0.219; 31: 0.22; 32: 0.225; 33: 0.21; 34: 0.207
| OSCILLATOR | R | 29: 0.214; 30: 0.215; 31: 0.218; 32: 0.214; 33: 0.208; 34: 0.221
A | POSITION D | L | 29: 0.226; 30: 0.21; 31: 0.217; 32: 0.226; 33: 0.214; 34: 0.22
0.083 | OF THE | C | 29: 0.213; 30: 0.21; 31: 0.213; 32: 0.218; 33: 0.214; 34: 0.201
| OSCILLATOR | R | 29: 0.212; 30: 0.216; 31: 0.218; 32: 0.218; 33: 0.222; 34: 0.201
A | POSITION E | L | 29: 0.216; 30: 0.216; 31: 0.233; 32: 0.201; 33: 0.211; 34: 0.21
0.083 | OF THE | C | 29: 0.21; 30: 0.216; 31: 0.224; 32: 0.209; 33: 0.218; 34: 0.222
| OSCILLATOR | R | 29: 0.208; 30: 0.22; 31: 0.214; 32: 0.224; 33: 0.221; 34: 0.215
A |  | L | 0.252 | 0.187 | 0.202 | 0.224 | 0.223 | 0.21 | 0.211 | 0.221 | 0.214 | 0.204 | 0.217 | 0.203 | 0.205 | 0.184 | 0.203 | 0.251 | 0.305 | 0.305 | 0.252 | 0.212 | 0.202 | 0.203 | 0.216 | 0.169 | 0.19 | 0.186 | 0.182 | 0.191 | 0.206 | 0.19 | 0.206 | 0.224 | 0.224 | 0.197 | 0.214 | 0.201 | 0.212 | 0.193 | 0.185 | 0.195 | 0.211 | 0.204 | 0.221 | 0.21 | 0.259 | 0.296 | 0.315 | 0.264 | 0.203 | 0.224 | 0.211 | 0.217 | 0.212 | 0.215 | 0.219 | 0.213 | 0.21 | 0.209 | 0.22 | 0.227 | 0.216 | 0.203 | 0.117
0.083 | +7 FT 6 IN | C | 0.292 | 0.196 | 0.201 | 0.216 | 0.225 | 0.206 | 0.21 | 0.222 | 0.205 | 0.21 | 0.212 | 0.2 | 0.203 | 0.194 | 0.214 | 0.254 | 0.302 | 0.31 | 0.246 | 0.216 | 0.209 | 0.207 | 0.204 | 0.183 | 0.195 | 0.188 | 0.195 | 0.195 | 0.201 | 0.19 | 0.214 | 0.226 | 0.22 | 0.203 | 0.219 | 0.196 | 0.216 | 0.195 | 0.194 | 0.194 | 0.207 | 0.203 | 0.219 | 0.201 | 0.257 | 0.289 | 0.32 | 0.263 | 0.196 | 0.227 | 0.214 | 0.205 | 0.201 | 0.212 | 0.218 | 0.224 | 0.209 | 0.204 | 0.225 | 0.223 | 0.212 | 0.225 | 0.001
|  | R | 0.248 | 0.196 | 0.202 | 0.216 | 0.221 | 0.195 | 0.2 | 0.22 | 0.202 | 0.207 | 0.208 | 0.198 | 0.197 | 0.194 | 0.214 | 0.246 | 0.308 | 0.315 | 0.243 | 0.2 | 0.206 | 0.206 | 0.207 | 0.176 | 0.186 | 0.181 | 0.178 | 0.187 | 0.197 | 0.186 | 0.223 | 0.225 | 0.214 | 0.198 | 0.215 | 0.18 | 0.216 | 0.2 | 0.199 | 0.213 | 0.212 | 0.215 | 0.21 | 0.199 | 0.255 | 0.303 | 0.32 | 0.265 | 0.212 | 0.217 | 0.221 | 0.2 | 0.215 | 0.202 | 0.214 | 0.213 | 0.198 | 0.2 | 0.229 | 0.223 | 0.197 | 0.226 | RF
A |  | L | 0.273 | 0.183 | 0.205 | 0.207 | 0.22 | 0.217 | 0.221 | 0.225 | 0.225 | 0.221 | 0.221 | 0.212 | 0.193 | 0.211 | 0.192 | 0.235 | 0.307 | 0.256 | 0.24 | 0.201 | 0.217 | 0.199 | 0.178 | 0.216 | 0.19 | 0.212 | 0.191 | 0.193 | 0.169 | 0.218 | 0.182 | 0.18 | 0.208 | 0.193 | 0.199 | 0.21 | 0.2 | 0.194 | 0.189 | 0.204 | 0.202 | 0.211 | 0.217 | 0.203 | 0.247 | 0.294 | 0.299 | 0.243 | 0.212 | 0.217 | 0.203 | 0.219 | 0.213 | 0.222 | 0.215 | 0.227 | 0.222 | 0.218 | 0.224 | 0.227 | 0.227 | 0.225 | 0.299
0.083 | +6 FT | C | 0.307 | 0.182 | 0.201 | 0.209 | 0.22 | 0.227 | 0.214 | 0.204 | 0.219 | 0.211 | 0.216 | 0.214 | 0.212 | 0.215 | 0.2 | 0.236 | 0.24 | 0.274 | 0.241 | 0.193 | 0.21 | 0.202 | 0.215 | 0.208 | 0.205 | 0.213 | 0.191 | 0.202 | 0.196 | 0.198 | 0.184 | 0.187 | 0.179 | 0.183 | 0.196 | 0.197 | 0.201 | 0.169 | 0.183 | 0.204 | 0.209 | 0.214 | 0.198 | 0.204 | 0.248 | 0.259 | 0.301 | 0.229 | 0.204 | 0.215 | 0.206 | 0.218 | 0.213 | 0.216 | 0.218 | 0.224 | 0.213 | 0.215 | 0.227 | 0.233 | 0.224 | 0.217 | 0.278
|  | R | 0.294 | 0.198 | 0.211 | 0.207 | 0.219 | 0.221 | 0.211 | 0.202 | 0.208 | 0.215 | 0.215 | 0.212 | 0.205 | 0.212 | 0.196 | 0.234 | 0.29 | 0.267 | 0.231 | 0.19 | 0.221 | 0.196 | 0.197 | 0.214 | 0.19 | 0.212 | 0.214 | 0.21 | 0.206 | 0.207 | 0.2 | 0.186 | 0.185 | 0.189 | 0.192 | 0.179 | 0.21 | 0.187 | 0.189 | 0.209 | 0.206 | 0.202 | 0.199 | 0.213 | 0.263 | 0.277 | 0.323 | 0.252 | 0.203 | 0.219 | 0.197 | 0.217 | 0.22 | 0.221 | 0.224 | 0.229 | 0.226 | 0.213 | 0.221 | 0.225 | 0.222 | 0.222 | 0.237
A |  | L | 0.209 | 0.195 | 0.219 | 0.227 | 0.221 | 0.205 | 0.233 | 0.222 | 0.229 | 0.193 | 0.206 | 0.212 | 0.215 | 0.221 | 0.203 | 0.249 | 0.234 | 0.229 | 0.245 | 0.215 | 0.219 | 0.218 | 0.216 | 0.211 | 0.17 | 0.204 | 0.198 | 0.218 | 0.193 | 0.214 | 0.21 | 0.202 | 0.184 | 0.191 | 0.196 | 0.205 | 0.205 | 0.194 | 0.202 | 0.201 | 0.214 | 0.19 | 0.186 | 0.21 | 0.215 | 0.271 | 0.291 | 0.247 | 0.199 | 0.193 | 0.209 | 0.214 | 0.192 | 0.223 | 0.217 | 0.209 | 0.209 | 0.216 | 0.205 | 0.211 | 0.218 | 0.225 | 0.319
0.083 | +4 FT 6 IN | C | 0.26 | 0.189 | 0.217 | 0.228 | 0.22 | 0.205 | 0.23 | 0.224 | 0.23 | 0.195 | 0.206 | 0.211 | 0.223 | 0.216 | 0.201 | 0.245 | 0.254 | 0.282 | 0.23 | 0.203 | 0.211 | 0.219 | 0.214 | 0.203 | 0.201 | 0.188 | 0.199 | 0.196 | 0.213 | 0.187 | 0.205 | 0.192 | 0.182 | 0.182 | 0.173 | 0.177 | 0.182 | 0.198 | 0.186 | 0.194 | 0.19 | 0.195 | 0.184 | 0.209 | 0.221 | 0.283 | 0.273 | 0.245 | 0.201 | 0.198 | 0.222 | 0.213 | 0.206 | 0.213 | 0.216 | 0.214 | 0.22 | 0.215 | 0.213 | 0.22 | 0.219 | 0.229 | 0.299
|  | R | 0.261 | 0.178 | 0.218 | 0.202 | 0.214 | 0.224 | 0.223 | 0.22 | 0.229 | 0.196 | 0.215 | 0.216 | 0.204 | 0.218 | 0.188 | 0.239 | 0.252 | 0.274 | 0.222 | 0.193 | 0.202 | 0.207 | 0.2 | 0.204 | 0.201 | 0.193 | 0.192 | 0.195 | 0.206 | 0.181 | 0.196 | 0.188 | 0.193 | 0.18 | 0.176 | 0.193 | 0.175 | 0.194 | 0.186 | 0.195 | 0.185 | 0.196 | 0.189 | 0.2 | 0.231 | 0.283 | 0.264 | 0.239 | 0.209 | 0.199 | 0.212 | 0.22 | 0.218 | 0.219 | 0.217 | 0.218 | 0.225 | 0.218 | 0.214 | 0.219 | 0.233 | 0.237 | 0.252
A |  | L | 0.216 | 0.183 | 0.218 | 0.218 | 0.214 | 0.216 | 0.208 | 0.21 | 0.222 | 0.22 | 0.212 | 0.201 | 0.216 | 0.197 | 0.217 | 0.255 | 0.293 | 0.325 | 0.251 | 0.218 | 0.22 | 0.208 | 0.212 | 0.189 | 0.221 | 0.222 | 0.224 | 0.217 | 0.217 | 0.226 | 0.214 | 0.208 | 0.197 | 0.214 | 0.218 | 0.209 | 0.22 | 0.215 | 0.185 | 0.183 | 0.19 | 0.183 | 0.19 | 0.177 | 0.197 | 0.24 | 0.161 | 0.205 | 0.204 | 0.212 | 0.206 | 0.209 | 0.19 | 0.206 | 0.212 | 0.216 | 0.201 | 0.199 | 0.22 | 0.216 | 0.221 | 0.214 | 0.3
0.083 | +3 FT | C | 0.226 | 0.225 | 0.202 | 0.2 | 0.224 | 0.204 | 0.203 | 0.218 | 0.222 | 0.217 | 0.215 | 0.214 | 0.217 | 0.198 | 0.21 | 0.248 | 0.303 | 0.303 | 0.256 | 0.224 | 0.217 | 0.232 | 0.187 | 0.208 | 0.214 | 0.2 | 0.204 | 0.189 | 0.209 | 0.206 | 0.215 | 0.21 | 0.195 | 0.2 | 0.218 | 0.207 | 0.193 | 0.176 | 0.163 | 0.185 | 0.173 | 0.148 | 0.172 | 0.155 | 0.189 | 0.203 | 0.197 | 0.166 | 0.187 | 0.199 | 0.205 | 0.192 | 0.185 | 0.198 | 0.217 | 0.199 | 0.201 | 0.203 | 0.223 | 0.208 | 0.222 | 0.223 | 0.294
|  | R | 0.231 | 0.214 | 0.207 | 0.206 | 0.198 | 0.209 | 0.209 | 0.223 | 0.213 | 0.198 | 0.216 | 0.2 | 0.23 | 0.19 | 0.216 | 0.227 | 0.298 | 0.283 | 0.249 | 0.213 | 0.219 | 0.196 | 0.198 | 0.202 | 0.19 | 0.218 | 0.193 | 0.195 | 0.201 | 0.184 | 0.198 | 0.2 | 0.188 | 0.17 | 0.184 | 0.199 | 0.181 | 0.167 | 0.166 | 0.155 | 0.155 | 0.142 | 0.16 | 0.156 | 0.154 | 0.213 | 0.169 | 0.185 | 0.2 | 0.197 | 0.208 | 0.193 | 0.195 | 0.201 | 0.218 | 0.215 | 0.21 | 0.194 | 0.223 | 0.198 | 0.217 | 0.224 | 0.276
A |  | L | 0.296 | 0.203 | 0.198 | 0.205 | 0.225 | 0.21 | 0.201 | 0.191 | 0.187 | 0.198 | 0.204 | 0.196 | 0.221 | 0.191 | 0.211 | 0.22 | 0.285 | 0.256 | 0.235 | 0.23 | 0.21 | 0.216 | 0.214 | 0.211 | 0.214 | 0.232 | 0.226 | 0.21 | 0.203 | 0.208 | 0.223 | 0.228 | 0.23 | 0.208 | 0.225 | 0.222 | 0.224 | 0.219 | 0.211 | 0.218 | 0.227 | 0.212 | 0.221 | 0.165 | 0.258 | 0.316 | 0.32 | 0.195 | 0.211 | 0.185 | 0.19 | 0.154 | 0.183 | 0.159 | 0.137 | 0.171 | 0.182 | 0.2 | 0.206 | 0.211 | 0.198 | 0.208 | 0.265
0.083 | +1 FT 6 IN | C | 0.286 | 0.201 | 0.218 | 0.218 | 0.216 | 0.228 | 0.218 | 0.214 | 0.219 | 0.208 | 0.206 | 0.213 | 0.215 | 0.218 | 0.218 | 0.213 | 0.313 | 0.3 | 0.25 | 0.214 | 0.245 | 0.21 | 0.224 | 0.215 | 0.22 | 0.215 | 0.216 | 0.233 | 0.217 | 0.218 | 0.22 | 0.223 | 0.212 | 0.23 | 0.22 | 0.222 | 0.229 | 0.221 | 0.221 | 0.217 | 0.22 | 0.219 | 0.225 | 0.184 | 0.264 | 0.307 | 0.304 | 0.173 | 0.214 | 0.191 | 0.19 | 0.159 | 0.195 | 0.172 | 0.159 | 0.192 | 0.198 | 0.195 | 0.223 | 0.214 | 0.196 | 0.217 | 0.289
|  | R | 0.294 | 0.208 | 0.217 | 0.232 | 0.218 | 0.224 | 0.217 | 0.214 | 0.22 | 0.207 | 0.206 | 0.221 | 0.214 | 0.204 | 0.208 | 0.224 | 0.301 | 0.297 | 0.24 | 0.217 | 0.224 | 0.216 | 0.201 | 0.201 | 0.211 | 0.204 | 0.212 | 0.21 | 0.207 | 0.216 | 0.217 | 0.211 | 0.211 | 0.202 | 0.204 | 0.192 | 0.196 | 0.204 | 0.197 | 0.188 | 0.192 | 0.186 | 0.206 | 0.09 | 0.202 | 0.227 | 0.199 | 0.115 | 0.164 | 0.105 | 0.145 | 0.102 | 0.175 | 0.142 | 0.177 | 0.141 | 0.187 | 0.194 | 0.232 | 0.219 | 0.177 | 0.209 | 0.281
A |  | L | 0.3 | 0.219 | 0.208 | 0.215 | 0.182 | 0.227 | 0.216 | 0.238 | 0.233 | 0.247 | 0.203 | 0.216 | 0.221 | 0.217 | 0.2 | 0.256 | 0.324 | 0.328 | 0.258 | 0.228 | 0.223 | 0.228 | 0.218 | 0.195 | 0.218 | 0.22 | 0.232 | 0.208 | 0.211 | 0.213 | 0.227 | 0.218 | 0.211 | 0.212 | 0.209 | 0.212 | 0.21 | 0.221 | 0.229 | 0.219 | 0.221 | 0.223 | 0.229 | 0.221 | 0.243 | 0.304 | 0.311 | 0.246 | 0.219 | 0.213 | 0.223 | 0.223 | 0.217 | 0.21 | 0.207 | 0.197 | 0.2 | 0.198 | 0.198 | 0.204 | 0.221 | 0.16 | 0.305
0.083 | 0 REFERENCE | C | 0.289 | 0.227 | 0.215 | 0.224 | 0.204 | 0.221 | 0.221 | 0.232 | 0.226 | 0.2 | 0.213 | 0.218 | 0.224 | 0.221 | 0.221 | 0.272 | 0.316 | 0.323 | 0.257 | 0.215 | 0.203 | 0.219 | 0.23 | 0.22 | 0.22 | 0.221 | 0.23 | 0.221 | 0.21 | 0.218 | 0.217 | 0.223 | 0.228 | 0.215 | 0.223 | 0.214 | 0.216 | 0.218 | 0.216 | 0.211 | 0.213 | 0.231 | 0.214 | 0.225 | 0.259 | 0.327 | 0.321 | 0.246 | 0.219 | 0.214 | 0.228 | 0.217 | 0.218 | 0.217 | 0.232 | 0.196 | 0.215 | 0.209 | 0.198 | 0.209 | 0.209 | 0.223 | 0.251
|  | R | 0.275 | 0.226 | 0.222 | 0.217 | 0.226 | 0.22 | 0.212 | 0.227 | 0.225 | 0.215 | 0.226 | 0.24 | 0.219 | 0.226 | 0.227 | 0.262 | 0.315 | 0.315 | 0.268 | 0.226 | 0.22 | 0.218 | 0.212 | 0.226 | 0.231 | 0.211 | 0.218 | 0.185 | 0.199 | 0.202 | 0.212 | 0.214 | 0.205 | 0.198 | 0.206 | 0.206 | 0.194 | 0.212 | 0.213 | 0.211 | 0.2 | 0.2 | 0.199 | 0.202 | 0.225 | 0.27 | 0.269 | 0.218 | 0.208 | 0.209 | 0.209 | 0.202 | 0.196 | 0.196 | 0.191 | 0.183 | 0.198 | 0.177 | 0.201 | 0.197 | 0.229 | 0.215 | 0.23
A |  | L | 0.306 | 0.217 | 0.223 | 0.224 | 0.224 | 0.21 | 0.205 | 0.221 | 0.237 | 0.226 | 0.224 | 0.238 | 0.21 | 0.221 | 0.216 | 0.23 | 0.306 | 0.294 | 0.253 | 0.215 | 0.217 | 0.219 | 0.203 | 0.212 | 0.231 | 0.222 | 0.198 | 0.22 | 0.227 | 0.229 | 0.222 | 0.23 | 0.219 | 0.203 | 0.221 | 0.211 | 0.205 | 0.217 | 0.22 | 0.206 | 0.212 | 0.214 | 0.216 | 0.197 | 0.239 | 0.276 | 0.291 | 0.244 | 0.197 | 0.223 | 0.202 | 0.198 | 0.185 | 0.203 | 0.206 | 0.207 | 0.222 | 0.217 | 0.215 | 0.222 | 0.226 | 0.219 | 0.314
0.083 | -9 IN | C | 0.315 | 0.208 | 0.213 | 0.223 | 0.231 | 0.22 | 0.23 | 0.237 | 0.226 | 0.221 | 0.224 | 0.223 | 0.217 | 0.219 | 0.217 | 0.248 | 0.34 | 0.315 | 0.248 | 0.204 | 0.221 | 0.187 | 0.23 | 0.225 | 0.24 | 0.213 | 0.195 | 0.21 | 0.214 | 0.217 | 0.213 | 0.223 | 0.212 | 0.232 | 0.22 | 0.203 | 0.222 | 0.224 | 0.208 | 0.183 | 0.22 | 0.213 | 0.216 | 0.229 | 0.24 | 0.292 | 0.295 | 0.247 | 0.205 | 0.221 | 0.213 | 0.204 | 0.204 | 0.22 | 0.195 | 0.209 | 0.196 | 0.232 | 0.226 | 0.218 | 0.207 | 0.208 | 0.301
|  | R | 0.322 | 0.222 | 0.22 | 0.228 | 0.223 | 0.207 | 0.216 | 0.219 | 0.214 | 0.217 | 0.203 | 0.203 | 0.195 | 0.207 | 0.199 | 0.236 | 0.313 | 0.304 | 0.247 | 0.208 | 0.209 | 0.2 | 0.223 | 0.204 | 0.213 | 0.206 | 0.201 | 0.18 | 0.209 | 0.207 | 0.23 | 0.213 | 0.204 | 0.207 | 0.213 | 0.207 | 0.195 | 0.211 | 0.211 | 0.196 | 0.206 | 0.219 | 0.201 | 0.191 | 0.242 | 0.274 | 0.265 | 0.223 | 0.203 | 0.204 | 0.213 | 0.188 | 0.205 | 0.211 | 0.211 | 0.209 | 0.211 | 0.227 | 0.223 | 0.22 | 0.202 | 0.232 | 0.31
A |  | L | 0.24 | 0.23 | 0.202 | 0.176 | 0.215 | 0.209 | 0.219 | 0.193 | 0.228 | 0.202 | 0.231 | 0.229 | 0.21 | 0.207 | 0.219 | 0.26 | 0.306 | 0.295 | 0.179 | 0.168 | 0.22 | 0.205 | 0.215 | 0.217 | 0.218 | 0.217 | 0.219 | 0.209 | 0.205 | 0.223 | 0.22 | 0.214 | 0.22 | 0.214 | 0.216 | 0.213 | 0.221 | 0.207 | 0.221 | 0.207 | 0.213 | 0.204 | 0.194 | 0.225 | 0.224 | 0.289 | 0.279 | 0.231 | 0.205 | 0.214 | 0.205 | 0.205 | 0.184 | 0.208 | 0.213 | 0.208 | 0.202 | 0.205 | 0.221 | 0.205 | 0.22 | 0.248 | 0.312
0.083 | -18 IN | C | 0.304 | 0.207 | 0.213 | 0.229 | 0.222 | 0.236 | 0.215 | 0.229 | 0.214 | 0.228 | 0.227 | 0.233 | 0.216 | 0.211 | 0.221 | 0.23 | 0.3 | 0.319 | 0.187 | 0.187 | 0.217 | 0.223 | 0.219 | 0.205 | 0.22 | 0.214 | 0.214 | 0.207 | 0.224 | 0.219 | 0.223 | 0.21 | 0.212 | 0.214 | 0.199 | 0.204 | 0.216 | 0.207 | 0.217 | 0.214 | 0.229 | 0.22 | 0.211 | 0.209 | 0.203 | 0.299 | 0.279 | 0.213 | 0.216 | 0.211 | 0.182 | 0.206 | 0.2 | 0.229 | 0.212 | 0.207 | 0.22 | 0.206 | 0.222 | 0.2 | 0.214 | 0.245 | 0.203
|  | R | 0.224 | 0.22 | 0.217 | 0.219 | 0.239 | 0.223 | 0.216 | 0.222 | 0.203 | 0.194 | 0.235 | 0.222 | 0.206 | 0.216 | 0.196 | 0.246 | 0.299 | 0.327 | 0.244 | 0.215 | 0.209 | 0.209 | 0.193 | 0.202 | 0.203 | 0.189 | 0.183 | 0.22 | 0.212 | 0.197 | 0.207 | 0.159 | 0.219 | 0.217 | 0.202 | 0.207 | 0.183 | 0.183 | 0.183 | 0.187 | 0.199 | 0.199 | 0.194 | 0.185 | 0.24 | 0.291 | 0.267 | 0.228 | 0.202 | 0.206 | 0.209 | 0.189 | 0.219 | 0.213 | 0.203 | 0.218 | 0.226 | 0.218 | 0.212 | 0.199 | 0.229 | 0.259 | 0.309
A |  | L | RF | 0.225 | 0.247 | 0.236 | 0.22 | 0.207 | 0.207 | 0.231 | 0.21 | 0.205 | 0.238 | 0.224 | 0.204 | 0.217 | 0.221 | 0.247 | 0.313 | 0.306 | 0.265 | 0.204 | 0.227 | 0.211 | 0.223 | 0.222 | 0.224 | 0.23 | 0.194 | 0.217 | 0.208 | 0.227 | 0.218 | 0.214 | 0.189 | 0.201 | 0.206 | 0.209 | 0.206 | 0.195 | 0.195 | 0.228 | 0.209 | 0.204 | 0.191 | 0.206 | 0.237 | 0.281 | 0.277 | 0.215 | 0.185 | 0.2 | 0.213 | 0.204 | 0.188 | 0.216 | 0.22 | 0.213 | 0.221 | 0.201 | 0.219 | 0.223 | 0.201 | 0.228 | RF
0.083 | -27 IN | C | 0.259 | 0.233 | 0.218 | 0.212 | 0.21 | 0.21 | 0.217 | 0.224 | 0.222 | 0.21 | 0.217 | 0.214 | 0.23 | 0.226 | 0.222 | 0.249 | 0.335 | 0.313 | 0.256 | 0.208 | 0.205 | 0.219 | 0.211 | 0.212 | 0.207 | 0.203 | 0.221 | 0.189 | 0.203 | 0.192 | 0.208 | 0.219 | 0.208 | 0.202 | 0.217 | 0.214 | 0.201 | 0.201 | 0.205 | 0.202 | 0.216 | 0.203 | 0.22 | 0.21 | 0.233 | 0.284 | 0.276 | 0.214 | 0.201 | 0.219 | 0.195 | 0.2 | 0.212 | 0.209 | 0.206 | 0.202 | 0.218 | 0.205 | 0.212 | 0.201 | 0.216 | 0.207 | RF
|  | R | RF | 0.22 | 0.189 | 0.196 | 0.228 | 0.226 | 0.199 | 0.221 | 0.226 | 0.221 | 0.214 | 0.212 | 0.218 | 0.23 | 0.205 | 0.247 | 0.287 | 0.308 | 0.253 | 0.229 | 0.208 | 0.201 | 0.221 | 0.219 | 0.203 | 0.201 | 0.217 | 0.2 | 0.196 | 0.196 | 0.226 | 0.215 | 0.191 | 0.209 | 0.2 | 0.199 | 0.221 | 0.212 | 0.195 | 0.218 | 0.199 | 0.212 | 0.207 | 0.213 | 0.234 | 0.303 | 0.278 | 0.238 | 0.198 | 0.203 | 0.22 | 0.209 | 0.202 | 0.21 | 0.202 | 0.206 | 0.208 | 0.213 | 0.218 | 0.213 | 0.181 | 0.22 | RF
A |  | L | 0.244 | 0.239 | 0.206 | 0.211 | 0.204 | 0.188 | 0.24 | 0.244 | 0.216 | 0.232 | 0.22 | 0.238 | 0.225 | 0.234 | 0.236 | 0.27 | 0.301 | 0.28 | 0.255 | 0.214 | 0.209 | 0.209 | 0.211 | 0.21 | 0.225 | 0.202 | 0.212 | 0.219 | 0.219 | 0.196 | 0.237 | 0.216 | 0.2 | 0.194 | 0.201 | 0.206 | 0.2 | 0.198 | 0.185 | 0.186 | 0.198 | 0.194 | 0.199 | 0.197 | 0.244 | 0.305 | 0.282 | 0.234 | 0.206 | 0.22 | 0.188 | 0.204 | 0.195 | 0.205 | 0.207 | 0.199 | 0.204 | 0.209 | 0.202 | 0.214 | 0.201 | 0.209 | RF
0.083 | -36 IN | C | 0.273 | 0.236 | 0.221 | 0.197 | 0.214 | 0.203 | 0.236 | 0.243 | 0.246 | 0.234 | 0.227 | 0.227 | 0.236 | 0.229 | 0.21 | 0.265 | 0.304 | 0.286 | 0.254 | 0.209 | 0.201 | 0.223 | 0.228 | 0.232 | 0.212 | 0.203 | 0.215 | 0.22 | 0.228 | 0.219 | 0.239 | 0.228 | 0.191 | 0.202 | 0.199 | 0.195 | 0.212 | 0.203 | 0.212 | 0.154 | 0.196 | 0.225 | 0.205 | 0.204 | 0.239 | 0.3 | 0.313 | 0.229 | 0.214 | 0.21 | 0.218 | 0.203 | 0.209 | 0.205 | 0.219 | 0.205 | 0.202 | 0.212 | 0.229 | 0.195 | 0.219 | 0.23 | RF
|  | R | 0.315 | 0.218 | 0.212 | 0.211 | 0.214 | 0.204 | 0.205 | 0.229 | 0.215 | 0.237 | 0.231 | 0.225 | 0.202 | 0.214 | 0.206 | 0.269 | 0.312 | 0.29 | 0.27 | 0.207 | 0.206 | 0.212 | 0.223 | 0.208 | 0.212 | 0.226 | 0.216 | 0.203 | 0.201 | 0.208 | 0.23 | 0.211 | 0.196 | 0.204 | 0.228 | 0.206 | 0.2 | 0.22 | 0.206 | 0.218 | 0.177 | 0.223 | 0.202 | 0.197 | 0.241 | 0.329 | 0.29 | 0.233 | 0.199 | 0.197 | 0.205 | 0.206 | 0.224 | 0.21 | 0.225 | 0.205 | 0.196 | 0.21 | 0.214 | 0.21 | 0.219 | 0.216 | RF
A |  | L | 0.322 | 0.201 | 0.224 | 0.208 | 0.23 | 0.216 | 0.198 | 0.232 | 0.233 | 0.236 | 0.209 | 0.227 | 0.201 | 0.233 | 0.201 | 0.271 | 0.323 | 0.314 | 0.253 | 0.214 | 0.205 | 0.229 | 0.203 | 0.226 | 0.226 | 0.182 | 0.225 | 0.189 | 0.219 | 0.211 | 0.21 | 0.207 | 0.204 | 0.204 | 0.203 | 0.198 | 0.202 | 0.172 | 0.205 | 0.2 | 0.203 | 0.221 | 0.231 | 0.202 | 0.208 | 0.328 | 0.268 | 0.241 | 0.205 | 0.203 | 0.223 | 0.201 | 0.211 | 0.223 | 0.222 | 0.22 | 0.208 | 0.212 | 0.212 | 0.201 | 0.211 | 0.255 | 0.291
0.083 | -45 IN | C | 0.319 | 0.219 | 0.204 | 0.217 | 0.223 | 0.227 | 0.231 | 0.21 | 0.225 | 0.234 | 0.217 | 0.21 | 0.209 | 0.213 | 0.218 | 0.249 | 0.315 | 0.314 | 0.265 | 0.225 | 0.2 | 0.204 | 0.222 | 0.225 | 0.213 | 0.235 | 0.205 | 0.205 | 0.224 | 0.222 | 0.217 | 0.226 | 0.213 | 0.187 | 0.178 | 0.224 | 0.15 | 0.187 | 0.205 | 0.206 | 0.188 | 0.209 | 0.21 | 0.189 | 0.246 | 0.295 | 0.279 | 0.243 | 0.204 | 0.206 | 0.213 | 0.214 | 0.209 | 0.23 | 0.229 | 0.225 | 0.21 | 0.219 | 0.204 | 0.17 | 0.209 | 0.219 | 0.289
|  | R | 0.318 | 0.2 | 0.219 | 0.198 | 0.182 | 0.211 | 0.229 | 0.221 | 0.225 | 0.221 | 0.218 | 0.2 | 0.211 | 0.229 | 0.218 | 0.253 | 0.314 | 0.315 | 0.255 | 0.193 | 0.212 | 0.231 | 0.195 | 0.249 | 0.229 | 0.21 | 0.211 | 0.192 | 0.23 | 0.197 | 0.205 | 0.207 | 0.204 | 0.189 | 0.22 | 0.199 | 0.188 | 0.188 | 0.208 | 0.196 | 0.231 | 0.213 | 0.209 | 0.192 | 0.239 | 0.301 | 0.286 | 0.236 | 0.209 | 0.206 | 0.222 | 0.237 | 0.189 | 0.21 | 0.217 | 0.202 | 0.2 | 0.209 | 0.192 | 0.178 | 0.226 | 0.188 | 0.291
A |  | L | 0.234 | 0.198 | 0.201 | 0.219 | 0.211 | 0.205 | 0.215 | 0.194 | 0.209 | 0.217 | 0.216 | 0.222 | 0.199 | 0.204 | 0.195 | 0.266 | 0.335 | 0.306 | 0.266 | 0.209 | 0.211 | 0.215 | 0.213 | 0.211 | 0.212 | 0.182 | 0.204 | 0.175 | 0.211 | 0.222 | 0.226 | 0.218 | 0.221 | 0.183 | 0.22 | 0.216 | 0.209 | 0.187 | 0.202 | 0.191 | 0.196 | 0.201 | 0.207 | 0.172 | 0.232 | 0.293 | 0.292 | 0.237 | 0.207 | 0.222 | 0.206 | 0.205 | 0.226 | 0.22 | 0.224 | 0.219 | 0.226 | 0.211 | 0.212 | 0.219 | 0.224 | 0.215 | 0.294
0.083 | -54 IN | C | 0.327 | 0.205 | 0.198 | 0.195 | 0.218 | 0.209 | 0.219 | 0.219 | 0.213 | 0.219 | 0.214 | 0.203 | 0.2 | 0.209 | 0.21 | 0.242 | 0.295 | 0.294 | 0.261 | 0.164 | 0.217 | 0.208 | 0.226 | 0.217 | 0.212 | 0.212 | 0.2 | 0.166 | 0.208 | 0.226 | 0.211 | 0.208 | 0.21 | 0.201 | 0.211 | 0.219 | 0.172 | 0.217 | 0.203 | 0.207 | 0.21 | 0.202 | 0.225 | 0.206 | 0.247 | 0.294 | 0.29 | 0.244 | 0.208 | 0.208 | 0.213 | 0.209 | 0.209 | 0.205 | 0.212 | 0.204 | 0.208 | 0.213 | 0.203 | 0.218 | 0.228 | 0.228 | 0.295
|  | R | 0.297 | 0.188 | 0.213 | 0.205 | 0.204 | 0.217 | 0.219 | 0.203 | 0.228 | 0.22 | 0.21 | 0.222 | 0.2 | 0.216 | 0.212 | 0.252 | 0.309 | 0.3 | 0.261 | 0.204 | 0.211 | 0.201 | 0.193 | 0.205 | 0.209 | 0.188 | 0.226 | 0.207 | 0.212 | 0.229 | 0.204 | 0.204 | 0.217 | 0.21 | 0.201 | 0.203 | 0.186 | 0.22 | 0.19 | 0.221 | 0.216 | 0.199 | 0.217 | 0.207 | 0.255 | 0.291 | 0.286 | 0.258 | 0.216 | 0.203 | 0.225 | 0.221 | 0.211 | 0.206 | 0.212 | 0.212 | 0.217 | 0.196 | 0.208 | 0.214 | 0.224 | 0.229 | 0.293
A |  | L | 0.278 | 0.219 | 0.185 | 0.191 | 0.215 | 0.183 | 0.149 | 0.215 | 0.214 | 0.201 | 0.205 | 0.198 | 0.208 | 0.208 | 0.201 | 0.219 | 0.319 | 0.288 | 0.195 | 0.135 | 0.204 | 0.213 | 0.201 | 0.201 | 0.189 | 0.187 | 0.207 | 0.174 | 0.194 | 0.232 | 0.189 | 0.188 | 0.222 | 0.212 | 0.222 | 0.216 | 0.175 | 0.188 | 0.193 | 0.217 | 0.198 | 0.213 | 0.208 | 0.21 | 0.219 | 0.31 | 0.285 | 0.154 | 0.218 | 0.195 | 0.175 | 0.197 | 0.181 | 0.176 | 0.208 | 0.18 | 0.172 | 0.226 | 0.211 | 0.202 | 0.182 | 0.207 | 0.332
0.083 | -63 IN | C | 0.303 | 0.202 | 0.193 | 0.199 | 0.225 | 0.201 | 0.195 | 0.215 | 0.202 | 0.199 | 0.211 | 0.202 | 0.197 | 0.214 | 0.205 | 0.226 | 0.313 | 0.285 | 0.175 | 0.131 | 0.194 | 0.215 | 0.206 | 0.203 | 0.187 | 0.195 | 0.198 | 0.193 | 0.191 | 0.211 | 0.198 | 0.205 | 0.231 | 0.199 | 0.203 | 0.213 | 0.195 | 0.184 | 0.204 | 0.213 | 0.191 | 0.199 | 0.221 | 0.212 | 0.224 | 0.303 | 0.267 | 0.179 | 0.181 | 0.196 | 0.215 | 0.229 | 0.228 | 0.182 | 0.221 | 0.201 | 0.202 | 0.193 | 0.21 | 0.186 | 0.192 | 0.072 | 0.306
|  | R | 0.295 | 0.188 | 0.204 | 0.209 | 0.222 | 0.188 | 0.205 | 0.214 | 0.206 | 0.208 | 0.21 | 0.211 | 0.182 | 0.209 | 0.196 | 0.243 | 0.278 | 0.307 | 0.277 | 0.196 | 0.161 | 0.205 | 0.186 | 0.189 | 0.204 | 0.205 | 0.19 | 0.212 | 0.204 | 0.197 | 0.178 | 0.23 | 0.187 | 0.179 | 0.199 | 0.214 | 0.216 | 0.188 | 0.179 | 0.213 | 0.207 | 0.224 | 0.208 | 0.207 | 0.264 | 0.289 | 0.28 | 0.175 | 0.201 | 0.191 | 0.226 | 0.225 | 0.197 | 0.189 | 0.198 | 0.198 | 0.147 | 0.207 | 0.19 | 0.2 | 0.205 | 0.064 | 0.28
A |  | L | 0.106 | 0.193 | 0.213 | 0.188 | 0.195 | 0.197 | 0.199 | 0.22 | 0.191 | 0.148 | 0.191 | 0.188 | 0.205 | 0.211 | 0.208 | 0.23 | 0.289 | 0.276 | 0.246 | 0.19 | 0.19 | 0.212 | 0.185 | 0.175 | 0.149 | 0.216 | 0.175 | 0.149 | 0.192 | 0.199 | 0.172 | 0.191 | 0.216 | 0.2 | 0.209 | 0.223 | 0.164 | 0.16 | 0.184 | 0.18 | 0.203 | 0.195 | 0.202 | 0.191 | 0.169 | 0.235 | 0.268 | 0.249 | 0.17 | 0.195 | 0.137 | 0.201 | 0.157 | 0.192 | 0.135 | 0.198 | 0.192 | 0.198 | 0.22 | 0.198 | 0.169 | 0.201 | 0.203
0.083 | -72 IN | C | 0.107 | 0.232 | 0.207 | 0.213 | 0.184 | 0.188 | 0.209 | 0.195 | 0.181 | 0.179 | 0.203 | 0.207 | 0.214 | 0.213 | 0.199 | 0.244 | 0.275 | 0.287 | 0.243 | 0.187 | 0.184 | 0.208 | 0.187 | 0.193 | 0.204 | 0.216 | 0.187 | 0.191 | 0.227 | 0.202 | 0.205 | 0.214 | 0.189 | 0.2 | 0.219 | 0.19 | 0.19 | 0.191 | 0.199 | 0.18 | 0.202 | 0.208 | 0.198 | 0.196 | 0.23 | 0.244 | 0.26 | 0.236 | 0.194 | 0.191 | 0.188 | 0.18 | 0.198 | 0.203 | 0.168 | 0.191 | 0.2 | 0.21 | 0.165 | 0.188 | 0.189 | 0.205 | 0.179
|  | R | 0.074 | 0.224 | 0.207 | 0.187 | 0.184 | 0.192 | 0.171 | 0.193 | 0.175 | 0.144 | 0.207 | 0.204 | 0.191 | 0.209 | 0.197 | 0.235 | 0.291 | 0.272 | 0.252 | 0.173 | 0.184 | 0.182 | 0.212 | 0.186 | 0.215 | 0.188 | 0.177 | 0.216 | 0.203 | 0.207 | 0.199 | 0.194 | 0.206 | 0.203 | 0.188 | 0.105 | 0.141 | 0.196 | 0.189 | 0.192 | 0.19 | 0.195 | 0.2 | 0.191 | 0.204 | 0.258 | 0.298 | 0.206 | 0.2 | 0.163 | 0.19 | 0.2 | 0.196 | 0.18 | 0.185 | 0.191 | 0.193 | 0.193 | 0.189 | 0.193 | 0.186 | 0.194 | 0.21
A |  | L | 0.25 | 0.127 | 0.213 | 0.185 | 0.192 | 0.14 | 0.165 | 0.187 | 0.179 | 0.146 | 0.189 | 0.19 | 0.207 | 0.208 | 0.23 | 0.251 | 0.29 | 0.312 | 0.2 | 0.186 | 0.199 | 0.161 | 0.227 | 0.186 | 0.176 | 0.207 | 0.192 | 0.18 | 0.232 | 0.197 | 0.209 | 0.21 | 0.209 | 0.213 | 0.193 | 0.202 | 0.145 | 0.165 | 0.194 | 0.19 | 0.206 | 0.212 | 0.204 | 0.21 | 0.211 | 0.281 | 0.266 | 0.302 | 0.258 | 0.203 | 0.196 | 0.181 | 0.203 | 0.196 | 0.221 | 0.224 | 0.183 | 0.18 | 0.181 | 0.199 | 0.224 | 0.223 | 0.057
0.083 | -81 IN | C | 0.133 | 0.221 | 0.219 | 0.195 | 0.2 | 0.197 | 0.183 | 0.178 | 0.214 | 0.206 | 0.199 | 0.198 | 0.192 | 0.22 | 0.205 | 0.239 | 0.306 | 0.259 | 0.144 | 0.167 | 0.188 | 0.176 | 0.226 | 0.201 | 0.214 | 0.203 | 0.228 | 0.214 | 0.229 | 0.24 | 0.23 | 0.222 | 0.208 | 0.228 | 0.199 | 0.183 | 0.147 | 0.189 | 0.219 | 0.204 | 0.2 | 0.197 | 0.188 | 0.218 | 0.297 | 0.283 | 0.193 | 0.29 | 0.243 | 0.199 | 0.196 | 0.197 | 0.204 | 0.192 | 0.197 | 0.196 | 0.199 | 0.181 | 0.196 | 0.237 | 0.225 | 0.19 | 0.078
|  | R | 0.274 | 0.247 | 0.2 | 0.184 | 0.174 | 0.208 | 0.161 | 0.175 | 0.214 | 0.188 | 0.197 | 0.206 | 0.178 | 0.201 | 0.199 | 0.251 | 0.326 | 0.259 | 0.333 | 0.205 | 0.199 | 0.196 | 0.223 | 0.193 | 0.215 | 0.195 | 0.17 | 0.199 | 0.188 | 0.237 | 0.217 | 0.224 | 0.201 | 0.229 | 0.208 | 0.18 | 0.183 | 0.194 | 0.205 | 0.171 | 0.201 | 0.188 | 0.188 | 0.211 | 0.297 | 0.285 | 0.251 | 0.305 | 0.245 | 0.19 | 0.178 | 0.163 | 0.188 | 0.187 | 0.192 | 0.2 | 0.19 | 0.177 | 0.153 | 0.225 | 0.238 | 0.219 | 0.239
A | POSITION A | L |  |  |  | 0.222 | 0.205 |  | 0.236 | 0.224 |  | 0.23 | 0.206 |  | 0.224 | 0.199 |  | 0.232 | 0.312 |  | 0.262 | 0.207 |  | 0.214 | 0.205 |  | 0.207 | 0.211 |  |  | 0.218 | 0.211 |  | 0.221 | 0.222 |  | 0.227 | 0.232 |  |  | 0.211 | 0.196 |  | 0.215 | 0.216 |  | 0.261 | 0.276 |  | 0.237 | 0.204 |  | 0.216 | 0.209 |  | 0.226 | 0.214 |  | 0.223 | 0.21 |  | 0.225 | 0.223
0.083 | OF THE | C |  |  |  | 0.214 | 0.206 |  | 0.223 | 0.208 |  | 0.225 | 0.221 |  | 0.226 | 0.196 |  | 0.256 | 0.308 |  | 0.241 | 0.198 |  | 0.198 | 0.208 |  | 0.209 | 0.225 |  |  | 0.207 | 0.234 |  | 0.214 | 0.212 |  | 0.213 | 0.205 |  |  | 0.206 | 0.208 |  | 0.211 | 0.208 |  | 0.234 | 0.275 |  | 0.247 | 0.208 |  | 0.192 | 0.225 |  | 0.222 | 0.21 |  | 0.235 | 0.206 |  | 0.232 | 0.215
| PRIMARIES | R |  |  |  | 0.194 | 0.206 |  | 0.214 | 0.194 |  | 0.205 | 0.211 |  | 0.212 | 0.201 |  | 0.236 | 0.297 |  | 0.253 | 0.202 |  | 0.188 | 0.197 |  | 0.198 | 0.211 |  |  | 0.189 | 0.224 |  | 0.201 | 0.207 |  | 0.213 | 0.198 |  |  | 0.198 | 0.218 |  | 0.214 | 0.221 |  | 0.231 | 0.278 |  | 0.222 | 0.213 |  | 0.214 | 0.223 |  | 0.218 | 0.215 |  | 0.226 | 0.212 |  | 0.206 | 0.231
A | POSITION B | L |  |  |  | 0.201 | 0.197 |  | 0.208 | 0.191 |  | 0.205 | 0.216 |  | 0.194 | 0.19 |  | 0.23 | 0.302 |  | 0.243 | 0.194 |  | 0.192 | 0.204 |  | 0.209 | 0.194 |  |  | 0.198 | 0.221 |  | 0.211 | 0.208 |  | 0.219 | 0.216 |  |  | 0.199 | 0.192 |  | 0.216 | 0.219 |  | 0.216 | 0.287 |  | 0.214 | 0.197 |  | 0.189 | 0.202 |  | 0.206 | 0.206 |  | 0.193 | 0.194 |  | 0.211 | 0.204
0.083 | OF THE | C |  |  |  | 0.187 | 0.204 |  | 0.204 | 0.203 |  | 0.218 | 0.211 |  | 0.19 | 0.198 |  | 0.232 | 0.298 |  | 0.245 | 0.2 |  | 0.201 | 0.199 |  | 0.216 | 0.198 |  |  | 0.208 | 0.207 |  | 0.205 | 0.218 |  | 0.221 | 0.203 |  |  | 0.211 | 0.192 |  | 0.209 | 0.209 |  | 0.233 | 0.285 |  | 0.237 | 0.207 |  | 0.216 | 0.218 |  | 0.218 | 0.206 |  | 0.191 | 0.203 |  | 0.201 | 0.207
| PRIMARIES | R |  |  |  | 0.191 | 0.217 |  | 0.199 | 0.195 |  | 0.212 | 0.195 |  | 0.172 | 0.206 |  | 0.247 | 0.298 |  | 0.24 | 0.195 |  | 0.204 | 0.199 |  | 0.218 | 0.21 |  |  | 0.21 | 0.223 |  | 0.198 | 0.213 |  | 0.202 | 0.21 |  |  | 0.193 | 0.201 |  | 0.195 | 0.209 |  | 0.212 | 0.302 |  | 0.236 | 0.201 |  | 0.198 | 0.21 |  | 0.196 | 0.205 |  | 0.204 | 0.211 |  | 0.204 | 0.205
A | POSITION C | L |  |  |  | 0.19 | 0.191 |  | 0.185 | 0.211 |  | 0.213 | 0.208 |  | 0.215 | 0.215 |  | 0.242 | 0.294 |  | 0.253 | 0.198 |  | 0.19 | 0.195 |  | 0.214 | 0.211 |  |  | 0.198 | 0.201 |  | 0.218 | 0.217 |  | 0.206 | 0.196 |  |  | 0.207 | 0.197 |  | 0.215 | 0.194 |  | 0.219 | 0.226 |  | 0.231 | 0.179 |  | 0.198 | 0.219 |  | 0.209 | 0.206 |  | 0.195 | 0.198 |  | 0.209 | 0.209
0.083 | OF THE | C |  |  |  | 0.183 | 0.187 |  | 0.22 | 0.198 |  | 0.201 | 0.21 |  | 0.181 | 0.195 |  | 0.254 | 0.269 |  | 0.238 | 0.212 |  | 0.19 | 0.191 |  | 0.204 | 0.212 |  |  | 0.193 | 0.205 |  | 0.199 | 0.216 |  | 0.194 | 0.208 |  |  | 0.185 | 0.208 |  | 0.191 | 0.196 |  | 0.212 | 0.257 |  | 0.214 | 0.198 |  | 0.229 | 0.206 |  | 0.198 | 0.195 |  | 0.202 | 0.196 |  | 0.176 | 0.205
| PRIMARIES | R |  |  |  | 0.195 | 0.173 |  | 0.24 | 0.193 |  | 0.197 | 0.201 |  | 0.189 | 0.196 |  | 0.232 | 0.298 |  | 0.223 | 0.201 |  | 0.202 | 0.171 |  | 0.199 | 0.203 |  |  | 0.225 | 0.207 |  | 0.218 | 0.226 |  | 0.204 | 0.195 |  |  | 0.201 | 0.2 |  | 0.208 | 0.188 |  | 0.187 | 0.284 |  | 0.185 | 0.183 |  | 0.205 | 0.209 |  | 0.226 | 0.203 |  | 0.216 | 0.208 |  | 0.191 | 0.214
A |  | L | 0.32 | 0.306 | 0.217 | 0.201 | 0.211 | 0.176 | 0.242 | 0.215 | 0.157 | 0.179 | 0.227 | 0.19 | 0.175 | 0.201 | 0.236 | 0.303 | 0.328 | 0.287 | 0.242 | 0.179 | 0.238 | 0.203 | 0.244 | 0.16 | 0.21 | 0.192 | 0.242 | 0.243 | 0.198 | 0.236 | 0.168 | 0.235 | 0.135 | 0.236 | 0.207 | 0.209 | 0.22 | 0.2 | 0.202 | 0.245 | 0.239 | 0.189 | 0.189 | 0.236 | 0.263 | 0.186 | 0.286 | 0.301 | 0.215 | 0.213 | 0.213 | 0.193 | 0.201 | 0.173 | 0.2 | 0.217 | 0.189 | 0.197 | 0.229 | 0.172 | 0.127 | 0.22 | 0.302
0.083 | -90 IN | C | 0.161 | 0.248 | 0.221 | 0.214 | 0.223 | 0.224 | 0.221 | 0.2 | 0.207 | 0.194 | 0.223 | 0.181 | 0.189 | 0.236 | 0.219 | 0.267 | 0.285 | 0.309 | 0.235 | 0.159 | 0.24 | 0.239 | 0.218 | 0.199 | 0.241 | 0.212 | 0.193 | 0.153 | 0.196 | 0.224 | 0.197 | 0.225 | 0.217 | 0.209 | 0.207 | 0.246 | 0.239 | 0.199 | 0.207 | 0.239 | 0.229 | 0.188 | 0.203 | 0.247 | 0.254 | 0.215 | 0.296 | 0.317 | 0.233 | 0.205 | 0.236 | 0.193 | 0.199 | 0.191 | 0.235 | 0.245 | 0.194 | 0.174 | 0.239 | 0.217 | 0.161 | 0.164 | 0.314
|  | R | 0.231 | 0.229 | 0.247 | 0.239 | 0.19 | 0.179 | 0.232 | 0.216 | 0.202 | 0.199 | 0.231 | 0.212 | 0.2 | 0.236 | 0.231 | 0.271 | 0.305 | 0.362 | 0.24 | 0.218 | 0.241 | 0.225 | 0.197 | 0.204 | 0.227 | 0.18 | 0.242 | 0.195 | 0.207 | 0.214 | 0.184 | 0.228 | 0.193 | 0.211 | 0.239 | 0.225 | 0.235 | 0.234 | 0.19 | 0.213 | 0.237 | 0.221 | 0.237 | 0.247 | 0.265 | 0.244 | 0.262 | 0.342 | 0.238 | 0.186 | 0.156 | 0.174 | 0.204 | 0.205 | 0.203 | 0.2 | 0.174 | 0.185 | 0.116 | 0.236 | 0.186 | 0.212 | 0.272
A | POSITION A | L | 16: 0.261; 17: 0.308; 18: 0.282; 19: 0.253; 45: 0.221; 46: 0.282; 47: 0.215; 48: 0.198
0.083 | OF THE | C | 16: 0.246; 17: 0.266; 18: 0.301; 19: 0.26; 45: 0.205; 46: 0.269; 47: 0.286; 48: 0.204
| SMELTS | R | 16: 0.274; 17: 0.193; 18: 0.347; 19: 0.259; 45: 0.219; 46: 0.26; 47: 0.28; 48: 0.205
A | POSITION B | L | 16: RF; 17: 0.337; 18: 0.296; 19: RF; 45: RF; 46: 0.249; 47: 0.3; 48: RF
0.083 | OF THE | C | 16: 0.263; 17: 0.292; 18: 0.311; 19: 0.279; 45: 0.294; 46: 0.301; 47: 0.323; 48: 0.277
| SMELTS | R | 16: RF; 17: 0.304; 18: 0.306; 19: RF; 45: RF; 46: 0.325; 47: 0.286; 48: RF
A | POSITION C | L | 16: 0.208; 17: 0.292; 18: 0.326; 19: 0.234; 45: 0.177; 46: RF; 47: 0.279; 48: 0.19
0.083 | OF THE | C | 16: 0.225; 17: RF; 18: 0.326; 19: 0.233; 45: 0.191; 46: 0.288; 47: 0.286; 48: 0.202
| SMELTS | R | 16: 0.215; 17: 0.308; 18: 0.311; 19: 0.247; 45: 0.207; 46: 0.281; 47: 0.244; 48: 0.2
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | AVG | MIN
B | 0.001-0.099 | 0.141-0.150 | 10: OUTSIDE DIAMETER:; 0.247 23: 2.969; 0.247 30: FUTURE PROJECTION
LEGEND | 0.100-0.110 | 0.151-0.160 | 10: TUBE MATERIAL:; 0.247 23: SA-178A; 0.247 35: MAX. THICKNESS
| 0.111-0.120 | 0.161-0.170 | 10: NOMINAL WALL:; 0.247 23: 0.18; 0.247 35: AVG. THICKNESS
| 0.121-0.130 | 0.171-0.180 | 10: ASME MIN:; 0.247 23: 0.099; 0.247 35: MIN. THICKNESS
| 0.131-0.140 | 0.181-0.999 | 10: MILL FLAG:; 0.247 23: 0.11; 0.247 35: STD DEV.
A | 0.001-0.083 | 0.131-0.140 | 10: OUTSIDE DIAMETER:; 0.247 23: 3; 0.247 30: FUTURE PROJECTION |  |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | 0.084-0.100 | 0.141-0.150 | 10: TUBE MATERIAL:; 0.247 23: SA210A1; 0.247 35: MAX. THICKNESS
| 0.101-0.110 | 0.151-0.160 | 10: NOMINAL WALL:; 0.247 23: 0.203; 0.247 35: AVG. THICKNESS |  |  |  | PROJECTED TUBE WALL THICKNESS - 5 YEARS
| 0.111-0.120 | 0.161-0.170 | 10: ASME MIN:; 0.247 23: 0.083; 0.247 35: MIN. THICKNESS
| 0.121-0.130 | 0.171-0.999 | 10: MILL FLAG:; 0.247 23: 0.1; 0.247 35: STD DEV.
PROJECTION
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Retirement
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. | [65 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63
B | POSITION A | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2052 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
MANWAY
B | POSITION B | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Mar 2053 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
MANWAY
B | POSITION C | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | Oct 2052 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
MANWAY
B | POSITION D | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
MANWAY
B | POSITION E | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Feb 2035 | May 2055 | May 2055 | Jul 2053 | Sep 2048 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
MANWAY
B | POSITION A | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | Dec 2029 | May 2055 | May 2055 | Dec 2028 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | Jan 2041 | Sep 2042 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
TERTIARIES
B | POSITION B | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | ND | ND | May 2055 | ND | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
TERTIARIES
B | POSITION C | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Dec 2052 | May 2029 | Feb 2053 | May 2055 | Aug 2034 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | Feb 2031 | May 2055 | Jan 2052 | Jun 2034 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
TERTIARIES
A |  | Year | ND | Jul 2039 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2055 | ND | ND | May 2055 | ND | ND | ND | ND | ND | May 2055 | ND | May 2055 | ND | ND | ND | ND | ND | ND | Oct 2034 | ND | May 2055 | May 2055 | ND | May 2055 | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | Apr 2046 | May 2055 | ND | Dec 2045 | May 2055 | Nov 2048 | Oct 2042 | May 2055 | May 2055 | ND | Sep 2030 | ND
+16 FT 6 IN
A |  | Year | Jun 2046 | May 2055 | Feb 2048 | May 2055 | May 2055 | Dec 2044 | May 2055 | May 2055 | May 2055 | ND | Oct 2045 | Nov 2048 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | ND | Jan 2046 | ND | May 2055 | May 2055 | Jul 2043 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | ND | ND | ND | May 2055 | ND | ND | May 2055 | ND | May 2055 | ND | Nov 2050 | May 2055 | May 2055 | ND | Feb 2055 | ND | May 2055 | ND | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2054
+15 FT
A |  | Year | Jul 2051 | Nov 2035 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | Aug 2051 | Dec 2032 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | ND
+13 FT 6 IN
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Mar 2030 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | ND | ND | May 2055 | ND
+12 FT
A | POSITION A | Year | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND
OF THE
OB PORTS
A | POSITION B | Year | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND
OF THE
OB PORTS
A | POSITION C | Year | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND
OF THE
OB PORTS
A |  | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Sep 2053 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | ND | ND
+10 FT 6 IN
A |  | Year | May 2055 | Feb 2054 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2054 | Jul 2053 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Nov 2046 | Jan 2048
+9 FT
A | POSITION A | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
A | POSTION B | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
A | POSITION C | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
A | POSITION D | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
A | POSITION E | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2047 | May 2055 | May 2055 | Dec 2052 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2025
+7 FT 6 IN
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | Apr 2055 | Sep 2053 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2053 | May 2055 | May 2055 | ND | May 2055 | May 2055 | Nov 2045 | May 2055 | Sep 2052 | Apr 2049 | Aug 2050 | May 2055 | May 2055 | Jan 2053 | May 2055 | Jul 2045 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | ND | May 2055 | ND | ND | May 2055 | ND | ND | ND | ND | May 2055
+6 FT
A |  | Year | Feb 2044 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | Mar 2049 | Sep 2050 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | Mar 2045 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Dec 2051 | May 2055 | Aug 2052 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055
+4 FT 6 IN
A |  | Year | Apr 2050 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2053 | Oct 2046 | Mar 2044 | Nov 2042 | Sep 2039 | May 2042 | Feb 2043 | May 2036 | Jul 2041 | Jun 2035 | Oct 2037 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055
+3 FT
A |  | Year | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2053 | May 2055 | Aug 2049 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | ND | ND | ND | May 2055 | ND | ND | ND | ND | May 2055 | May 2055 | ND | May 2055 | ND | Nov 2030 | ND | May 2055 | Dec 2042 | May 2032 | Nov 2047 | Mar 2032 | Sep 2043 | Nov 2031 | May 2055 | Mar 2039 | Sep 2036 | Jul 2038 | May 2055 | May 2055 | ND | ND | May 2051 | May 2055 | Nov 2052
+1 FT 6 IN
A |  | Year | May 2055 | ND | May 2055 | ND | Dec 2049 | ND | ND | ND | ND | May 2055 | ND | ND | ND | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | ND | ND | ND | Apr 2052 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2039 | May 2055
0 REFERENCE
A |  | Year | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | Apr 2052 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2052 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | ND | ND | ND | May 2055 | May 2055 | May 2055
-9 IN
A |  | Year | Oct 2044 | May 2055 | May 2055 | Apr 2045 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2038 | Jan 2041 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Sep 2052 | May 2055 | May 2055 | May 2055 | May 2055 | Dec 2039 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2051 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | Aug 2040
-18 IN
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2043 | May 2055 | ND
-27 IN
A |  | Year | Sep 2046 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2038 | May 2049 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND
-36 IN
A |  | Year | ND | May 2055 | May 2055 | May 2055 | May 2046 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Mar 2046 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2047 | May 2055 | Jul 2038 | Dec 2049 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2049 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | Jan 2043 | May 2055 | Dec 2047 | ND
-45 IN
A |  | Year | Mar 2039 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Dec 2039 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Dec 2047 | May 2055 | Nov 2042 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Feb 2054 | May 2055 | May 2055 | Dec 2046 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2045 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055
-54 IN
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2053 | Nov 2036 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2037 | Mar 2034 | Aug 2040 | May 2055 | Aug 2052 | May 2055 | Nov 2053 | May 2055 | May 2055 | Apr 2047 | May 2055 | May 2055 | Feb 2047 | May 2055 | Nov 2051 | Aug 2049 | May 2055 | May 2055 | Jul 2047 | May 2055 | Oct 2049 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2035 | Dec 2045 | May 2055 | Mar 2049 | May 2055 | Aug 2051 | Oct 2047 | May 2055 | Feb 2052 | Aug 2036 | May 2055 | May 2055 | Sep 2054 | Jun 2052 | Aug 2029 | May 2055
-63 IN
A |  | Year | Jan 2030 | May 2055 | May 2055 | May 2055 | Jun 2053 | May 2055 | Jan 2042 | May 2055 | Feb 2051 | Jan 2036 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2046 | May 2055 | Feb 2055 | Nov 2052 | Feb 2049 | Oct 2036 | May 2055 | May 2051 | Feb 2038 | May 2055 | May 2055 | Feb 2046 | May 2055 | May 2055 | May 2055 | May 2055 | Aug 2031 | Jan 2036 | Mar 2039 | May 2055 | Nov 2052 | May 2055 | May 2055 | May 2055 | May 2055 | Dec 2037 | Jan 2047 | May 2055 | Aug 2049 | May 2045 | Apr 2042 | Jan 2035 | Jul 2051 | Dec 2041 | Oct 2054 | Oct 2034 | May 2055 | May 2055 | May 2055 | Mar 2045 | May 2055 | Jul 2043 | May 2055 | Mar 2037
-72 IN
A |  | Year | Jul 2032 | Jan 2033 | May 2055 | May 2055 | Mar 2048 | Mar 2037 | Sep 2041 | Aug 2048 | May 2055 | Oct 2036 | May 2055 | May 2055 | Sep 2050 | May 2055 | May 2055 | May 2055 | May 2055 | Jan 2049 | Jul 2035 | Feb 2043 | May 2055 | Sep 2040 | ND | May 2055 | Aug 2046 | May 2055 | Apr 2044 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Aug 2050 | Sep 2036 | Oct 2042 | May 2055 | Sep 2044 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2038 | ND | ND | May 2055 | Dec 2051 | Jul 2041 | Nov 2054 | May 2055 | May 2055 | May 2055 | Nov 2051 | Dec 2054 | Oct 2037 | May 2055 | ND | May 2055 | Jul 2029
-81 IN
A | POSITION A | Year | ND | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND
OF THE
PRIMARIES
A | POSITION B | Year | ND | ND | ND | Sep 2054 | May 2055 | ND | May 2055 | Dec 2053 | ND | May 2055 | May 2055 | ND | Jan 2049 | Apr 2053 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND
OF THE
PRIMARIES
A | POSITION C | Year | ND | ND | ND | Jan 2055 | Oct 2046 | ND | Sep 2053 | May 2055 | ND | May 2055 | May 2055 | ND | Jan 2049 | May 2055 | ND | May 2055 | May 2055 | ND | Dec 2053 | May 2055 | ND | Mar 2054 | Feb 2046 | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | Aug 2041 | Apr 2046 | ND | Aug 2041 | Jun 2047 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | Oct 2048 | May 2055 | ND | ND
OF THE
PRIMARIES
A |  | Year | Oct 2039 | ND | May 2055 | May 2055 | May 2055 | Feb 2044 | ND | May 2055 | Apr 2040 | Oct 2054 | ND | Jun 2054 | Nov 2052 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2038 | ND | May 2055 | May 2055 | Jun 2039 | May 2055 | Jan 2049 | May 2055 | Jan 2040 | May 2055 | May 2055 | Apr 2043 | ND | Sep 2034 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | Feb 2050 | May 2055 | ND | ND | May 2037 | May 2055 | ND | May 2055 | May 2055 | Sep 2037 | Mar 2046 | May 2055 | Jun 2049 | May 2055 | May 2055 | Jun 2049 | Jun 2047 | Sep 2032 | Mar 2046 | Jun 2033 | Nov 2040 | ND
-90 IN
A | POSITION A | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | Sep 2037 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Jul 2049 | May 2055 | Nov 2041 | Jun 2046 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
SMELTS
A | POSITION B | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Jun 2048 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
SMELTS
A | POSITION C | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Jul 2047 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Sep 2037 | May 2055 | Feb 2044 | Dec 2041 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
SMELTS
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63
| PROJECTED TO REACH TMIN: |  | 10: NOTE: CORROSION RATE IS BASED ON COMPARISON OF; 30: EARLIEST DATE OF PROJECTED RETIREMENT: | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | + 5 YEARS (or no data)
| WITHIN 5 YEARS |  | 10: 2020, 2022, 2023, 2024, 2025 |  | PROJECTED TUBE RETIREMENT DATE
| WITHIN 3 YEARS |  | 10: INSPECTION DATA; 30: May 2025
| WITHIN 1 YEAR |  | 10: ND; 15: NO COMPARISON DATA
RETIREMENT
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Low (hidden)
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. LOW THICKNESS MEASUREMENTS ARE IN INCHES. | [67 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | AVG | MIN
B | POSITION A | LOWEST
0.099 | OF THE
MANWAY
B | POSITION B | LOWEST
0.099 | OF THE
MANWAY
B | POSITION C | LOWEST
0.099 | OF THE
MANWAY
B | POSITION D | LOWEST
0.099 | OF THE
MANWAY
B | POSITION E | LOWEST
0.099 | OF THE
MANWAY
B | POSITION A | LOWEST
0.099 | OF THE
TERTIARIES
B | POSITION B | LOWEST | bar: 19; 22; 41; 44
0.099 | OF THE
TERTIARIES
B | POSITION C | LOWEST
0.099 | OF THE
TERTIARIES
A |  | LOWEST | bar: 62 to 63
0.083 | +16 FT 6 IN
A |  | LOWEST | bar: 1; 63
0.083 | +15 FT
A |  | LOWEST | bar: 63
0.083 | +13 FT 6 IN
A |  | LOWEST | bar: 63
0.083 | +12 FT
A | POSITION A | LOWEST
0.083 | OF THE
OB PORTS
A | POSITION B | LOWEST
0.083 | OF THE
OB PORTS
A | POSITION C | LOWEST
0.083 | OF THE
OB PORTS
A |  | LOWEST | bar: 63
0.083 | +10 FT 6 IN
A |  | LOWEST | bar: 63
0.083 | +9 FT
A | POSITION A | LOWEST
0.083 | OF THE
OSCILLATOR
A | POSTION B | LOWEST
0.083 | OF THE
OSCILLATOR
A | POSITION C | LOWEST
0.083 | OF THE
OSCILLATOR
A | POSITION D | LOWEST
0.083 | OF THE
OSCILLATOR
A | POSITION E | LOWEST
0.083 | OF THE
OSCILLATOR
A |  | LOWEST
0.083 | +7 FT 6 IN
A |  | LOWEST
0.083 | +6 FT
A |  | LOWEST
0.083 | +4 FT 6 IN
A |  | LOWEST
0.083 | +3 FT
A |  | LOWEST
0.083 | +1 FT 6 IN
A |  | LOWEST
0.083 | 0 REFERENCE
A |  | LOWEST
0.083 | -9 IN
A |  | LOWEST
0.083 | -18 IN
A |  | LOWEST | bar: 1; 63
0.083 | -27 IN
A |  | LOWEST | bar: 63
0.083 | -36 IN
A |  | LOWEST
0.083 | -45 IN
A |  | LOWEST
0.083 | -54 IN
A |  | LOWEST
0.083 | -63 IN
A |  | LOWEST
0.083 | -72 IN
A |  | LOWEST
0.083 | -81 IN
A | POSITION A | LOWEST
0.083 | OF THE
PRIMARIES
A | POSITION B | LOWEST
0.083 | OF THE
PRIMARIES
A | POSITION C | LOWEST
0.083 | OF THE
PRIMARIES
A |  | LOWEST
0.083 | -90 IN
A | POSITION A | LOWEST
0.083 | OF THE
SMELTS
A | POSITION B | LOWEST
0.083 | OF THE
SMELTS
A | POSITION C | LOWEST | bar: 16 to 19; 45 to 48
0.083 | OF THE
SMELTS
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | AVG | MIN
B | 0.001-0.099 | 0.141-0.150 | 10: OUTSIDE DIAMETER:; 23: 2.969; 30: INSPECTION RESULTS
LEGEND | 0.100-0.110 | 0.151-0.160 | 10: TUBE MATERIAL:; 23: SA-178A; 35: MAX. THICKNESS
| 0.111-0.120 | 0.161-0.170 | 10: NOMINAL WALL:; 23: 0.18; 35: AVG. THICKNESS
| 0.121-0.130 | 0.171-0.180 | 10: ASME MIN:; 23: 0.099; 35: MIN. THICKNESS
| 0.131-0.140 | 0.181-0.999 | 10: MILL FLAG:; 23: 0.11; 35: STD DEV.
A | 0.001-0.083 | 0.131-0.140 | 10: OUTSIDE DIAMETER:; 23: 3; 30: INSPECTION RESULTS |  |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | 0.084-0.100 | 0.141-0.150 | 10: TUBE MATERIAL:; 23: SA210A1; 35: MAX. THICKNESS
| 0.101-0.110 | 0.151-0.160 | 10: NOMINAL WALL:; 23: 0.203; 35: AVG. THICKNESS |  |  |  | TUBE WALL THICKNESS SURVEY (LOW VALUE)
| 0.111-0.120 | 0.161-0.170 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS
| 0.121-0.130 | 0.171-0.999 | 10: MILL FLAG:; 23: 0.1; 35: STD DEV.
LOW THICKNESS
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com