## Thickness
2025 |  | RF - REFRACTORY; ST - STRUCTURAL INTERFERENCE; RT - RECESSED TUBE; | [72 empty] | OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. THICKNESS MEASUREMENTS ARE IN INCHES. | [72 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MIN
A |  | L | RF | 0.225 | 0.223 | 0.217 | 0.241 | 0.268 | 0.276 | 0.267 | 0.277 | 0.259 | 0.266 | 0.219 | 0.223 | 0.211 | 0.217 | 0.222 | 0.217 | 0.222 | 0.21 | 0.217 | 0.22 | 0.217 | 0.217 | 0.216 | 0.221 | 0.222 | 0.214 | 0.22 | 0.216 | 0.219 | 0.212 | 0.224 | 0.232 | 0.232 | 0.223 | 0.213 | 0.213 | 0.224 | 0.207 | 0.209 | 0.221 | 0.229 | 0.219 | 0.197 | 0.221 | 0.22 | 0.222 | 0.219 | 0.221 | 0.214 | 0.234 | 0.22 | 0.219 | 0.214 | 0.217 | 0.214 | 0.218 | 0.232 | 0.217 | 0.226 | 0.227 | 0.223 | 0.22 | 0.22 | 0.228 | 0.227 | 0.232 | 0.239 | 0.212
0.083 | +16 FT 6 IN | C | RF | 0.238 | 0.226 | 0.224 | 0.225 | 0.262 | 0.266 | 0.274 | 0.276 | 0.263 | 0.263 | 0.218 | 0.224 | 0.235 | 0.212 | 0.225 | 0.218 | 0.219 | 0.21 | 0.217 | 0.226 | 0.21 | 0.216 | 0.213 | 0.215 | 0.206 | 0.217 | 0.23 | 0.211 | 0.225 | 0.215 | 0.222 | 0.223 | 0.23 | 0.222 | 0.223 | 0.207 | 0.216 | 0.213 | 0.228 | 0.232 | 0.233 | 0.222 | 0.214 | 0.228 | 0.217 | 0.227 | 0.213 | 0.218 | 0.216 | 0.221 | 0.213 | 0.219 | 0.214 | 0.213 | 0.212 | 0.219 | 0.227 | 0.217 | 0.219 | 0.222 | 0.224 | 0.226 | 0.219 | 0.225 | 0.225 | 0.229 | 0.226 | 0.215
|  | R | RF | 0.23 | 0.223 | 0.223 | 0.23 | 0.269 | 0.241 | 0.26 | 0.273 | 0.262 | 0.27 | 0.219 | 0.221 | 0.236 | 0.209 | 0.229 | 0.217 | 0.219 | 0.207 | 0.219 | 0.222 | 0.211 | 0.21 | 0.214 | 0.219 | 0.202 | 0.217 | 0.226 | 0.219 | 0.224 | 0.212 | 0.214 | 0.221 | 0.229 | 0.226 | 0.236 | 0.22 | 0.223 | 0.215 | 0.214 | 0.227 | 0.224 | 0.211 | 0.226 | 0.222 | 0.222 | 0.23 | 0.216 | 0.215 | 0.211 | 0.216 | 0.211 | 0.217 | 0.215 | 0.219 | 0.212 | 0.223 | 0.222 | 0.214 | 0.221 | 0.224 | 0.22 | 0.222 | 0.226 | 0.229 | 0.228 | 0.237 | 0.227 | 0.221
A |  | L | RF | 0.217 | 0.233 | 0.23 | 0.229 | 0.27 | 0.263 | 0.267 | 0.255 | 0.263 | 0.267 | 0.226 | 0.229 | 0.223 | 0.208 | 0.216 | 0.217 | 0.212 | 0.219 | 0.211 | 0.212 | 0.208 | 0.221 | 0.21 | 0.207 | 0.22 | 0.213 | 0.212 | 0.213 | 0.205 | 0.208 | 0.215 | 0.204 | 0.228 | 0.226 | 0.215 | 0.21 | 0.211 | 0.2 | 0.204 | 0.207 | 0.209 | 0.217 | 0.21 | 0.212 | 0.202 | 0.216 | 0.208 | 0.228 | 0.21 | 0.226 | 0.209 | 0.209 | 0.209 | 0.208 | 0.224 | 0.215 | 0.215 | 0.218 | 0.218 | 0.223 | 0.226 | 0.226 | 0.22 | 0.24 | 0.227 | 0.219 | 0.229 | RF
0.083 | +15 FT | C | RF | 0.216 | 0.23 | 0.225 | 0.229 | 0.274 | 0.263 | 0.267 | 0.265 | 0.26 | 0.272 | 0.23 | 0.224 | 0.217 | 0.221 | 0.212 | 0.212 | 0.211 | 0.212 | 0.205 | 0.23 | 0.21 | 0.214 | 0.217 | 0.21 | 0.207 | 0.208 | 0.208 | 0.207 | 0.202 | 0.223 | 0.216 | 0.22 | 0.228 | 0.209 | 0.213 | 0.216 | 0.208 | 0.202 | 0.208 | 0.212 | 0.206 | 0.215 | 0.223 | 0.216 | 0.198 | 0.207 | 0.21 | 0.214 | 0.218 | 0.227 | 0.217 | 0.214 | 0.208 | 0.206 | 0.208 | 0.208 | 0.22 | 0.223 | 0.22 | 0.217 | 0.221 | 0.226 | 0.217 | 0.228 | 0.233 | 0.221 | 0.231 | RF
|  | R | RF | 0.218 | 0.229 | 0.225 | 0.224 | 0.268 | 0.271 | 0.268 | 0.272 | 0.257 | 0.271 | 0.21 | 0.219 | 0.213 | 0.201 | 0.215 | 0.218 | 0.203 | 0.211 | 0.199 | 0.227 | 0.204 | 0.213 | 0.213 | 0.215 | 0.211 | 0.217 | 0.215 | 0.207 | 0.217 | 0.217 | 0.212 | 0.219 | 0.226 | 0.223 | 0.215 | 0.221 | 0.221 | 0.209 | 0.196 | 0.214 | 0.215 | 0.212 | 0.215 | 0.205 | 0.204 | 0.21 | 0.214 | 0.209 | 0.219 | 0.216 | 0.217 | 0.209 | 0.22 | 0.21 | 0.216 | 0.218 | 0.219 | 0.22 | 0.221 | 0.216 | 0.224 | 0.232 | 0.225 | 0.222 | 0.243 | 0.225 | 0.227 | RF
A |  | L | RF | 0.223 | 0.231 | 0.235 | 0.223 | 0.278 | 0.278 | 0.268 | 0.277 | 0.271 | 0.268 | 0.223 | 0.218 | 0.22 | 0.203 | 0.214 | 0.215 | 0.209 | 0.205 | 0.223 | 0.221 | 0.2 | 0.2 | 0.207 | 0.209 | 0.207 | 0.212 | 0.21 | 0.214 | 0.19 | 0.206 | 0.225 | 0.209 | 0.224 | 0.205 | 0.208 | 0.208 | 0.209 | 0.194 | 0.195 | 0.21 | 0.221 | 0.194 | 0.213 | 0.208 | 0.193 | 0.222 | 0.217 | 0.216 | 0.202 | 0.191 | 0.199 | 0.193 | 0.229 | 0.208 | 0.204 | 0.209 | 0.204 | 0.206 | 0.23 | 0.228 | 0.217 | 0.235 | 0.223 | 0.23 | 0.231 | 0.24 | 0.237 | RF
0.083 | +13 FT 6 IN | C | RF | 0.224 | 0.221 | 0.226 | 0.216 | 0.275 | 0.276 | 0.275 | 0.268 | 0.268 | 0.263 | 0.225 | 0.218 | 0.229 | 0.209 | 0.214 | 0.213 | 0.213 | 0.206 | 0.202 | 0.208 | 0.217 | 0.227 | 0.227 | 0.207 | 0.203 | 0.21 | 0.21 | 0.226 | 0.193 | 0.2 | 0.208 | 0.202 | 0.228 | 0.205 | 0.212 | 0.198 | 0.206 | 0.194 | 0.185 | 0.185 | 0.205 | 0.212 | 0.205 | 0.206 | 0.214 | 0.2 | 0.218 | 0.218 | 0.213 | 0.219 | 0.205 | 0.197 | 0.235 | 0.215 | 0.206 | 0.235 | 0.218 | 0.212 | 0.223 | 0.21 | 0.222 | 0.217 | 0.224 | 0.23 | 0.234 | 0.228 | 0.237 | RF
|  | R | RF | 0.218 | 0.221 | 0.22 | 0.222 | 0.272 | 0.288 | 0.274 | 0.267 | 0.27 | 0.273 | 0.221 | 0.216 | 0.217 | 0.201 | 0.205 | 0.204 | 0.201 | 0.2 | 0.202 | 0.212 | 0.21 | 0.212 | 0.215 | 0.204 | 0.216 | 0.219 | 0.217 | 0.208 | 0.201 | 0.203 | 0.213 | 0.211 | 0.212 | 0.206 | 0.209 | 0.205 | 0.206 | 0.192 | 0.182 | 0.205 | 0.21 | 0.196 | 0.21 | 0.208 | 0.205 | 0.207 | 0.202 | 0.209 | 0.213 | 0.196 | 0.21 | 0.201 | 0.205 | 0.208 | 0.22 | 0.231 | 0.207 | 0.212 | 0.219 | 0.226 | 0.227 | 0.216 | 0.225 | 0.227 | 0.226 | 0.224 | 0.226 | RF
A |  | L | RF | 0.23 | 0.227 | 0.225 | 0.223 | 0.252 | 0.276 | 0.255 | 0.247 | 0.246 | 0.248 | 0.206 | 0.212 | 0.213 | 0.208 | 0.213 | 0.199 | 0.208 | 0.215 | 0.2 | 0.199 | 0.217 | 0.209 | 0.21 | 0.202 | 0.21 | 0.208 | 0.206 | 0.2 | 0.202 | 0.246 | 0.207 | 0.22 | 0.222 | 0.219 | 0.219 | 0.196 | 0.182 | 0.192 | 0.185 | 0.195 | 0.189 | 0.182 | 0.2 | 0.188 | 0.194 | 0.193 | 0.195 | 0.189 | 0.201 | 0.191 | 0.199 | 0.195 | 0.214 | 0.195 | 0.186 | 0.202 | 0.214 | 0.198 | 0.215 | 0.21 | 0.206 | 0.221 | 0.221 | 0.229 | 0.234 | 0.229 | 0.226 | 0.233
0.083 | +12 FT | C | RF | 0.229 | 0.221 | 0.22 | 0.216 | 0.252 | 0.25 | 0.255 | 0.243 | 0.25 | 0.249 | 0.217 | 0.214 | 0.222 | 0.208 | 0.215 | 0.216 | 0.214 | 0.219 | 0.21 | 0.206 | 0.218 | 0.196 | 0.207 | 0.207 | 0.206 | 0.196 | 0.197 | 0.199 | 0.205 | 0.198 | 0.201 | 0.22 | 0.223 | 0.216 | 0.204 | 0.207 | 0.189 | 0.181 | 0.172 | 0.196 | 0.225 | 0.18 | 0.187 | 0.188 | 0.198 | 0.192 | 0.197 | 0.193 | 0.197 | 0.191 | 0.19 | 0.201 | 0.207 | 0.203 | 0.195 | 0.207 | 0.204 | 0.213 | 0.209 | 0.214 | 0.21 | 0.218 | 0.225 | 0.229 | 0.235 | 0.221 | 0.236 | 0.216
|  | R | RF | 0.225 | 0.23 | 0.219 | 0.219 | 0.25 | 0.256 | 0.261 | 0.243 | 0.25 | 0.245 | 0.218 | 0.214 | 0.211 | 0.204 | 0.215 | 0.21 | 0.213 | 0.215 | 0.205 | 0.214 | 0.203 | 0.197 | 0.227 | 0.206 | 0.208 | 0.199 | 0.204 | 0.23 | 0.194 | 0.205 | 0.218 | 0.223 | 0.223 | 0.216 | 0.197 | 0.196 | 0.185 | 0.183 | 0.192 | 0.222 | 0.184 | 0.182 | 0.21 | 0.2 | 0.198 | 0.198 | 0.194 | 0.194 | 0.197 | 0.186 | 0.189 | 0.199 | 0.201 | 0.203 | 0.208 | 0.211 | 0.196 | 0.195 | 0.204 | 0.208 | 0.23 | 0.218 | 0.233 | 0.237 | 0.226 | 0.227 | 0.226 | 0.224
A | POSITION 'A' | L | 2: 0.216; 3: 0.218; 4: 0.212; 5: 0.211; 65: 0.218; 66: 0.233; 67: 0.227; 68: 0.226
0.083 | OF THE | C | 2: 0.207; 3: 0.214; 4: 0.214; 5: 0.212; 65: 0.214; 66: 0.222; 67: 0.217; 68: 0.24
| OB PORTS | R | 2: 0.226; 3: 0.219; 4: 0.215; 5: 0.212; 65: 0.218; 66: 0.219; 67: 0.216; 68: 0.222
A | POSITION 'B' | L | 2: 0.214; 3: 0.219; 4: 0.221; 5: 0.235; 65: 0.218; 66: 0.222; 67: 0.218; 68: 0.232
0.083 | OF THE | C | 2: 0.21; 3: 0.213; 4: 0.224; 5: 0.214; 65: 0.22; 66: 0.22; 67: 0.224; 68: 0.22
| OB PORTS | R | 2: 0.214; 3: 0.216; 4: 0.221; 5: 0.21; 65: 0.223; 66: 0.216; 67: 0.219; 68: 0.223
A | POSITION 'C' | L | 2: 0.217; 3: 0.228; 4: 0.22; 5: 0.214; 65: 0.22; 66: 0.222; 67: 0.221; 68: 0.218
0.083 | OF THE | C | 2: 0.218; 3: 0.221; 4: 0.224; 5: 0.216; 65: 0.216; 66: 0.22; 67: 0.225; 68: 0.216
| OB PORTS | R | 2: 0.221; 3: 0.227; 4: 0.215; 5: 0.223; 65: 0.213; 66: 0.222; 67: 0.222; 68: 0.224
A |  | L | 0.196 | 0.234 | 0.224 | 0.223 | 0.218 | RF | 0.27 | 0.279 | 0.286 | 0.257 | 0.251 | 0.23 | 0.229 | 0.218 | 0.206 | 0.203 | 0.206 | 0.184 | 0.213 | 0.192 | 0.191 | 0.191 | 0.185 | 0.2 | 0.201 | 0.192 | 0.198 | 0.196 | 0.198 | 0.188 | 0.206 | 0.222 | 0.21 | 0.212 | 0.226 | 0.219 | 0.183 | 0.19 | 0.177 | 0.19 | 0.181 | 0.197 | 0.237 | 0.233 | 0.193 | 0.178 | 0.216 | 0.22 | 0.216 | 0.191 | 0.202 | 0.192 | 0.217 | 0.196 | 0.191 | 0.216 | 0.203 | 0.204 | 0.215 | 0.224 | 0.209 | 0.216 | 0.22 | 0.224 | 0.227 | 0.228 | 0.225 | 0.223 | RF
0.083 | +10 FT 6 IN | C | 0.202 | 0.232 | 0.224 | 0.221 | 0.22 | RF | 0.264 | 0.273 | 0.278 | 0.271 | 0.253 | 0.233 | 0.204 | 0.231 | 0.207 | 0.206 | 0.198 | 0.194 | 0.182 | 0.198 | 0.193 | 0.19 | 0.217 | 0.199 | 0.225 | 0.213 | 0.206 | 0.204 | 0.199 | 0.204 | 0.2 | 0.218 | 0.223 | 0.226 | 0.226 | 0.2 | 0.207 | 0.191 | 0.182 | 0.184 | 0.207 | 0.176 | 0.194 | 0.19 | 0.202 | 0.187 | 0.212 | 0.196 | 0.196 | 0.211 | 0.188 | 0.21 | 0.21 | 0.209 | 0.201 | 0.223 | 0.209 | 0.201 | 0.2 | 0.209 | 0.216 | 0.217 | 0.217 | 0.224 | 0.225 | 0.222 | 0.228 | 0.235 | RF
|  | R | 0.214 | 0.227 | 0.233 | 0.221 | 0.225 | RF | 0.28 | 0.275 | 0.264 | 0.264 | 0.25 | 0.217 | 0.218 | 0.232 | 0.209 | 0.206 | 0.196 | 0.199 | 0.207 | 0.202 | 0.209 | 0.213 | 0.197 | 0.195 | 0.224 | 0.196 | 0.199 | 0.222 | 0.185 | 0.204 | 0.203 | 0.215 | 0.222 | 0.225 | 0.225 | 0.206 | 0.195 | 0.183 | 0.203 | 0.221 | 0.197 | 0.18 | 0.189 | 0.19 | 0.189 | 0.194 | 0.197 | 0.203 | 0.193 | 0.203 | 0.197 | 0.196 | 0.21 | 0.206 | 0.212 | 0.211 | 0.216 | 0.21 | 0.208 | 0.228 | 0.22 | 0.217 | 0.22 | 0.22 | 0.227 | 0.223 | 0.227 | 0.243 | RF
A | POSITION 'A' | L | 4: 0.215; 5: 0.218; 6: 0.263; 7: 0.259; 8: 0.275; 9: 0.272; 10: 0.271; 11: 0.265; 12: 0.213; 13: 0.207; 32: 0.194; 33: 0.215; 34: 0.218; 35: 0.213; 36: 0.214; 37: 0.21
0.083 | OF THE MANWAY | C | 4: 0.215; 5: 0.206; 6: 0.265; 7: 0.279; 8: 0.261; 9: 0.26; 10: 0.272; 11: 0.279; 12: 0.205; 13: 0.207; 32: 0.203; 33: 0.216; 34: 0.223; 35: 0.22; 36: 0.236; 37: 0.185
| & OSCILLATOR | R | 4: 0.223; 5: 0.216; 6: 0.268; 7: 0.263; 8: 0.267; 9: 0.276; 10: 0.26; 11: 0.279; 12: 0.203; 13: 0.211; 32: 0.222; 33: 0.21; 34: 0.219; 35: 0.216; 36: 0.229; 37: 0.179
A | POSITION 'B' | L | 4: 0.22; 5: 0.209; 6: RT; 7: 0.283; 8: 0.268; 9: 0.293; 10: 0.266; 11: RT; 12: 0.225; 13: 0.224; 32: 0.23; 33: 0.22; 34: 0.229; 35: 0.219; 36: 0.217; 37: 0.203
0.083 | OF THE MANWAY | C | 4: 0.219; 5: 0.207; 6: RT; 7: 0.256; 8: 0.25; 9: 0.261; 10: 0.252; 11: RT; 12: 0.213; 13: 0.228; 32: 0.217; 33: 0.22; 34: 0.226; 35: 0.222; 36: 0.214; 37: 0.197
| & OSCILLATOR | R | 4: 0.219; 5: 0.209; 6: RT; 7: 0.239; 8: 0.245; 9: 0.275; 10: 0.277; 11: RT; 12: 0.216; 13: 0.221; 32: 0.209; 33: 0.211; 34: 0.214; 35: 0.217; 36: 0.196; 37: 0.209
A | POSITION 'C' | L | 4: 0.213; 5: 0.213; 6: RT; 7: RT; 8: 0.278; 9: 0.27; 10: RT; 11: RT; 12: 0.223; 13: 0.22; 32: 0.206; 33: 0.213; 34: 0.233; 35: 0.23; 36: 0.198; 37: 0.192
0.083 | OF THE MANWAY | C | 4: 0.213; 5: 0.221; 6: RT; 7: RT; 8: 0.278; 9: 0.275; 10: RT; 11: RT; 12: 0.209; 13: 0.226; 32: 0.22; 33: 0.218; 34: 0.231; 35: 0.22; 36: 0.237; 37: 0.192
| & OSCILLATOR | R | 4: 0.214; 5: 0.213; 6: RT; 7: RT; 8: 0.284; 9: 0.282; 10: RT; 11: RT; 12: 0.213; 13: 0.216; 32: 0.207; 33: 0.223; 34: 0.219; 35: 0.222; 36: 0.188; 37: 0.237
A | POSITION 'D' | L | 4: 0.225; 5: 0.21; 6: RT; 7: 0.255; 8: 0.235; 9: 0.268; 10: RT; 11: RT; 12: 0.218; 13: 0.21; 32: 0.217; 33: 0.21; 34: 0.216; 35: 0.224; 36: 0.196; 37: 0.169
0.083 | OF THE MANWAY | C | 4: 0.219; 5: 0.207; 6: RT; 7: 0.273; 8: 0.233; 9: 0.266; 10: RT; 11: RT; 12: 0.218; 13: 0.198; 32: 0.211; 33: 0.204; 34: 0.227; 35: 0.227; 36: 0.215; 37: 0.17
| & OSCILLATOR | R | 4: 0.222; 5: 0.205; 6: RT; 7: 0.247; 8: 0.235; 9: 0.269; 10: RT; 11: RT; 12: 0.219; 13: 0.204; 32: 0.211; 33: 0.205; 34: 0.23; 35: 0.206; 36: 0.208; 37: 0.213
A | POSITION 'E' | L | 4: 0.229; 5: 0.21; 6: 0.222; 7: 0.249; 8: 0.269; 9: 0.267; 10: 0.26; 11: 0.27; 12: 0.222; 13: 0.213; 32: 0.209; 33: 0.202; 34: 0.229; 35: 0.23; 36: 0.186; 37: 0.189
0.083 | OF THE MANWAY | C | 4: 0.213; 5: 0.23; 6: 0.214; 7: 0.246; 8: 0.253; 9: 0.245; 10: 0.257; 11: 0.251; 12: 0.23; 13: 0.23; 32: 0.22; 33: 0.197; 34: 0.217; 35: 0.222; 36: 0.198; 37: 0.183
| & OSCILLATOR | R | 4: 0.214; 5: 0.216; 6: 0.238; 7: 0.249; 8: 0.28; 9: 0.27; 10: 0.25; 11: 0.265; 12: 0.235; 13: 0.223; 32: 0.221; 33: 0.193; 34: 0.215; 35: 0.237; 36: 0.211; 37: 0.197
A |  | L | 0.21 | 0.228 | 0.225 | 0.226 | 0.213 | RT | RT | 0.264 | 0.247 | RT | RT | 0.227 | 0.212 | 0.216 | 0.214 | 0.198 | 0.222 | 0.192 | 0.194 | 0.181 | 0.182 | 0.191 | 0.184 | 0.194 | 0.205 | 0.202 | 0.185 | 0.183 | 0.193 | 0.182 | 0.215 | 0.196 | 0.209 | 0.229 | 0.232 | 0.196 | 0.177 | 0.175 | 0.186 | 0.185 | 0.188 | 0.191 | 0.19 | 0.19 | 0.198 | 0.2 | 0.2 | 0.195 | 0.199 | 0.204 | 0.19 | 0.204 | 0.194 | 0.203 | 0.205 | 0.198 | 0.202 | 0.2 | 0.206 | 0.203 | 0.203 | 0.208 | 0.212 | 0.215 | 0.22 | 0.22 | 0.222 | 0.214 | RF
0.083 | +9 FT | C | 0.225 | 0.219 | 0.219 | 0.234 | 0.211 | RT | RT | 0.254 | 0.257 | RT | RT | 0.225 | 0.212 | 0.211 | 0.226 | 0.192 | 0.209 | 0.2 | 0.189 | 0.188 | 0.209 | 0.189 | 0.193 | 0.187 | 0.195 | 0.188 | 0.186 | 0.185 | 0.178 | 0.182 | 0.195 | 0.215 | 0.21 | 0.226 | 0.227 | 0.201 | 0.178 | 0.194 | 0.202 | 0.193 | 0.189 | 0.191 | 0.196 | 0.187 | 0.185 | 0.203 | 0.196 | 0.216 | 0.197 | 0.199 | 0.188 | 0.194 | 0.195 | 0.2 | 0.214 | 0.2 | 0.201 | 0.203 | 0.206 | 0.211 | 0.214 | 0.213 | 0.217 | 0.216 | 0.223 | 0.22 | 0.221 | 0.217 | RF
|  | R | 0.223 | 0.22 | 0.226 | 0.223 | 0.213 | RT | RT | 0.256 | 0.266 | RT | RT | 0.221 | 0.22 | 0.215 | 0.224 | 0.192 | 0.214 | 0.214 | 0.201 | 0.204 | 0.196 | 0.195 | 0.218 | 0.207 | 0.203 | 0.184 | 0.183 | 0.191 | 0.198 | 0.185 | 0.19 | 0.218 | 0.216 | 0.234 | 0.227 | 0.193 | 0.197 | 0.195 | 0.212 | 0.204 | 0.19 | 0.203 | 0.192 | 0.194 | 0.189 | 0.188 | 0.192 | 0.2 | 0.211 | 0.214 | 0.193 | 0.201 | 0.197 | 0.195 | 0.206 | 0.212 | 0.213 | 0.202 | 0.208 | 0.214 | 0.206 | 0.206 | 0.22 | 0.212 | 0.219 | 0.218 | 0.217 | 0.214 | RF
A |  | L | 0.213 | 0.225 | 0.23 | 0.226 | 0.209 | 0.258 | 0.242 | 0.253 | 0.253 | 0.253 | 0.251 | 0.214 | 0.226 | 0.195 | 0.212 | 0.198 | 0.194 | 0.199 | 0.183 | 0.203 | 0.173 | 0.18 | 0.203 | 0.187 | 0.205 | 0.178 | 0.186 | 0.208 | 0.179 | 0.186 | 0.166 | 0.18 | 0.17 | 0.199 | 0.188 | 0.22 | 0.212 | 0.193 | 0.186 | 0.196 | 0.211 | 0.211 | 0.193 | 0.202 | 0.198 | 0.192 | 0.189 | 0.201 | 0.199 | 0.186 | 0.19 | 0.181 | 0.204 | 0.199 | 0.207 | 0.203 | 0.203 | 0.204 | 0.211 | 0.214 | 0.207 | 0.215 | 0.202 | 0.215 | 0.226 | 0.212 | 0.224 | 0.222 | RF
0.083 | +7 FT 6 IN | C | 0.215 | 0.221 | 0.221 | 0.214 | 0.216 | 0.249 | 0.257 | 0.246 | 0.242 | 0.259 | 0.257 | 0.21 | 0.211 | 0.194 | 0.207 | 0.192 | 0.185 | 0.199 | 0.205 | 0.192 | 0.178 | 0.181 | 0.2 | 0.199 | 0.185 | 0.174 | 0.183 | 0.192 | 0.176 | 0.195 | 0.187 | 0.178 | 0.188 | 0.192 | 0.204 | 0.211 | 0.211 | 0.197 | 0.2 | 0.202 | 0.197 | 0.192 | 0.196 | 0.205 | 0.195 | 0.201 | 0.215 | 0.198 | 0.195 | 0.192 | 0.195 | 0.195 | 0.2 | 0.199 | 0.207 | 0.206 | 0.208 | 0.204 | 0.21 | 0.212 | 0.208 | 0.203 | 0.205 | 0.215 | 0.228 | 0.21 | 0.22 | 0.207 | RF
|  | R | 0.217 | 0.218 | 0.231 | 0.218 | 0.234 | 0.242 | 0.257 | 0.249 | 0.239 | 0.243 | 0.239 | 0.202 | 0.191 | 0.209 | 0.205 | 0.177 | 0.222 | 0.205 | 0.193 | 0.196 | 0.196 | 0.194 | 0.179 | 0.189 | 0.201 | 0.177 | 0.198 | 0.193 | 0.2 | 0.188 | 0.199 | 0.186 | 0.207 | 0.195 | 0.206 | 0.216 | 0.2 | 0.202 | 0.19 | 0.187 | 0.205 | 0.19 | 0.203 | 0.202 | 0.186 | 0.203 | 0.19 | 0.208 | 0.202 | 0.198 | 0.198 | 0.199 | 0.196 | 0.205 | 0.206 | 0.212 | 0.204 | 0.212 | 0.21 | 0.198 | 0.215 | 0.216 | 0.211 | 0.222 | 0.225 | 0.215 | 0.216 | 0.217 | RF
A |  | L | 0.214 | 0.221 | 0.227 | 0.218 | 0.224 | 0.261 | 0.275 | 0.265 | 0.261 | 0.251 | 0.251 | 0.216 | 0.195 | 0.178 | 0.213 | 0.194 | 0.19 | 0.183 | 0.195 | 0.171 | 0.169 | 0.167 | 0.183 | 0.205 | 0.181 | 0.177 | 0.178 | 0.194 | 0.186 | 0.172 | 0.197 | 0.179 | 0.188 | 0.2 | 0.216 | 0.178 | 0.228 | 0.196 | 0.218 | 0.2 | 0.206 | 0.193 | 0.226 | 0.205 | 0.22 | 0.215 | 0.222 | 0.225 | 0.209 | 0.207 | 0.204 | 0.209 | 0.213 | 0.214 | 0.213 | 0.209 | 0.207 | 0.211 | 0.208 | 0.206 | 0.223 | 0.211 | 0.215 | 0.208 | 0.21 | 0.204 | 0.204 | 0.214 | 0.214
0.083 | +6 FT | C | 0.204 | 0.219 | 0.232 | 0.221 | 0.225 | 0.262 | 0.265 | 0.263 | 0.263 | 0.26 | 0.253 | 0.211 | 0.198 | 0.217 | 0.201 | 0.18 | 0.203 | 0.186 | 0.184 | 0.183 | 0.195 | 0.174 | 0.19 | 0.205 | 0.194 | 0.182 | 0.18 | 0.188 | 0.196 | 0.191 | 0.187 | 0.182 | 0.192 | 0.212 | 0.176 | 0.181 | 0.225 | 0.205 | 0.214 | 0.205 | 0.182 | 0.2 | 0.213 | 0.207 | 0.22 | 0.217 | 0.226 | 0.219 | 0.209 | 0.217 | 0.214 | 0.2 | 0.204 | 0.219 | 0.205 | 0.209 | 0.215 | 0.217 | 0.218 | 0.207 | 0.214 | 0.228 | 0.219 | 0.214 | 0.212 | 0.208 | 0.202 | 0.219 | 0.214
|  | R | 0.23 | 0.224 | 0.227 | 0.226 | 0.216 | 0.26 | 0.265 | 0.264 | 0.262 | 0.258 | 0.249 | 0.212 | 0.2 | 0.187 | 0.2 | 0.185 | 0.193 | 0.175 | 0.178 | 0.194 | 0.187 | 0.188 | 0.217 | 0.203 | 0.221 | 0.194 | 0.208 | 0.179 | 0.192 | 0.191 | 0.188 | 0.187 | 0.228 | 0.199 | 0.189 | 0.216 | 0.207 | 0.218 | 0.212 | 0.214 | 0.202 | 0.2 | 0.207 | 0.205 | 0.226 | 0.225 | 0.226 | 0.219 | 0.215 | 0.211 | 0.214 | 0.203 | 0.221 | 0.2 | 0.206 | 0.211 | 0.207 | 0.214 | 0.208 | 0.21 | 0.217 | 0.213 | 0.215 | 0.214 | 0.215 | 0.208 | 0.207 | 0.218 | 0.211
A |  | L | 0.203 | 0.219 | 0.245 | 0.221 | 0.223 | 0.262 | 0.271 | 0.256 | 0.26 | 0.265 | 0.258 | 0.208 | 0.211 | 0.205 | 0.213 | 0.21 | 0.192 | 0.208 | 0.195 | 0.184 | 0.224 | 0.171 | 0.171 | 0.18 | 0.183 | 0.192 | 0.189 | 0.214 | 0.314 | 0.181 | 0.192 | 0.192 | 0.208 | 0.198 | 0.2 | 0.209 | 0.2 | 0.198 | 0.21 | 0.218 | 0.218 | 0.225 | 0.217 | 0.211 | 0.199 | 0.196 | 0.204 | 0.212 | 0.211 | 0.22 | 0.208 | 0.201 | 0.213 | 0.207 | 0.213 | 0.214 | 0.211 | 0.211 | 0.219 | 0.207 | 0.209 | 0.203 | 0.214 | 0.201 | 0.206 | 0.205 | 0.214 | 0.214 | 0.222
0.083 | +4 FT 6 IN | C | 0.2 | 0.218 | 0.221 | 0.219 | 0.217 | 0.26 | 0.264 | 0.257 | 0.248 | 0.258 | 0.253 | 0.207 | 0.205 | 0.214 | 0.217 | 0.209 | 0.191 | 0.2 | 0.187 | 0.185 | 0.198 | 0.173 | 0.187 | 0.181 | 0.221 | 0.185 | 0.189 | 0.198 | 0.324 | 0.188 | 0.2 | 0.226 | 0.2 | 0.212 | 0.201 | 0.196 | 0.212 | 0.214 | 0.21 | 0.213 | 0.217 | 0.208 | 0.218 | 0.208 | 0.213 | 0.212 | 0.209 | 0.213 | 0.212 | 0.218 | 0.207 | 0.213 | 0.207 | 0.218 | 0.208 | 0.218 | 0.211 | 0.212 | 0.216 | 0.209 | 0.212 | 0.204 | 0.204 | 0.2 | 0.213 | 0.209 | 0.208 | 0.201 | 0.216
|  | R | 0.194 | 0.227 | 0.215 | 0.218 | 0.223 | 0.26 | 0.273 | 0.263 | 0.264 | 0.262 | 0.259 | 0.205 | 0.196 | 0.208 | 0.195 | 0.195 | 0.192 | 0.18 | 0.196 | 0.183 | 0.195 | 0.193 | 0.183 | 0.18 | 0.199 | 0.206 | 0.195 | 0.223 | 0.323 | 0.208 | 0.2 | 0.185 | 0.194 | 0.204 | 0.213 | 0.202 | 0.207 | 0.21 | 0.215 | 0.21 | 0.214 | 0.219 | 0.22 | 0.214 | 0.215 | 0.213 | 0.211 | 0.21 | 0.217 | 0.21 | 0.211 | 0.212 | 0.217 | 0.223 | 0.207 | 0.207 | 0.217 | 0.217 | 0.212 | 0.21 | 0.218 | 0.209 | 0.222 | 0.196 | 0.202 | 0.212 | 0.209 | 0.194 | 0.23
A |  | L | 0.204 | 0.222 | 0.226 | 0.223 | 0.227 | 0.237 | 0.267 | 0.269 | 0.269 | 0.267 | 0.248 | 0.205 | 0.225 | 0.221 | 0.198 | 0.207 | 0.201 | 0.18 | 0.207 | 0.213 | 0.221 | 0.2 | 0.195 | 0.197 | 0.216 | 0.222 | 0.204 | 0.197 | 0.314 | 0.202 | RF | 0.201 | 0.214 | 0.205 | 0.199 | 0.206 | 0.213 | 0.217 | 0.216 | 0.211 | 0.226 | 0.226 | 0.208 | 0.209 | 0.22 | 0.211 | 0.216 | 0.213 | 0.239 | 0.21 | 0.23 | 0.233 | 0.213 | 0.212 | 0.22 | 0.22 | 0.222 | 0.212 | 0.235 | 0.207 | 0.208 | 0.22 | 0.205 | 0.226 | 0.21 | 0.206 | 0.235 | 0.236 | 0.229
0.083 | +3 FT | C | 0.23 | 0.214 | 0.22 | 0.221 | 0.229 | 0.259 | 0.264 | 0.266 | 0.261 | 0.267 | 0.261 | 0.215 | 0.236 | 0.242 | 0.208 | 0.208 | 0.201 | 0.213 | 0.218 | 0.23 | 0.214 | 0.2 | 0.201 | 0.195 | 0.2 | 0.205 | 0.208 | 0.217 | 0.328 | RF | 0.202 | 0.203 | 0.212 | 0.214 | 0.208 | 0.209 | 0.212 | 0.209 | 0.22 | 0.224 | 0.216 | 0.209 | 0.208 | 0.21 | 0.213 | 0.211 | 0.226 | 0.214 | 0.213 | 0.22 | 0.204 | 0.203 | 0.214 | 0.208 | 0.218 | 0.212 | 0.207 | 0.211 | 0.232 | 0.21 | 0.23 | 0.22 | 0.211 | 0.217 | 0.208 | 0.229 | 0.216 | 0.207 | 0.207
|  | R | RF | 0.215 | 0.222 | 0.218 | 0.22 | 0.26 | 0.273 | 0.269 | 0.263 | 0.267 | 0.255 | 0.215 | 0.213 | 0.211 | 0.211 | 0.217 | 0.313 | 0.198 | 0.206 | 0.219 | 0.233 | 0.205 | 0.195 | 0.203 | 0.205 | 0.204 | 0.197 | 0.217 | 0.34 | 0.195 | 0.199 | 0.227 | 0.203 | 0.214 | 0.209 | 0.215 | 0.219 | 0.217 | 0.215 | 0.22 | 0.226 | 0.217 | 0.206 | 0.216 | 0.219 | 0.213 | 0.218 | 0.221 | 0.213 | 0.221 | 0.216 | 0.218 | 0.218 | 0.215 | 0.212 | 0.213 | 0.224 | 0.213 | 0.216 | 0.211 | 0.212 | 0.223 | 0.22 | 0.221 | 0.195 | 0.229 | 0.216 | 0.207 | 0.213
A |  | L | 0.214 | 0.215 | 0.226 | 0.216 | 0.21 | 0.251 | 0.257 | 0.266 | 0.248 | 0.278 | 0.255 | 0.219 | 0.218 | 0.227 | 0.226 | 0.209 | 0.207 | 0.213 | 0.214 | 0.21 | 0.221 | 0.206 | 0.211 | 0.208 | 0.204 | 0.215 | 0.213 | 0.211 | 0.213 | 0.206 | 0.208 | 0.215 | 0.215 | 0.216 | 0.211 | 0.236 | 0.199 | 0.208 | 0.203 | 0.214 | 0.215 | 0.209 | 0.221 | 0.209 | 0.203 | 0.205 | 0.215 | 0.205 | 0.209 | 0.209 | 0.222 | 0.207 | 0.206 | 0.214 | 0.222 | 0.222 | 0.212 | 0.209 | 0.216 | 0.216 | 0.206 | 0.236 | 0.237 | 0.252 | 0.213 | 0.209 | 0.234 | 0.235 | 0.21
0.083 | +1 FT 6 IN | C | 0.227 | 0.219 | 0.22 | 0.219 | 0.223 | 0.281 | 0.257 | 0.261 | 0.278 | 0.258 | 0.292 | 0.222 | 0.232 | 0.229 | 0.209 | 0.208 | 0.207 | 0.209 | 0.215 | 0.222 | 0.221 | 0.221 | 0.211 | 0.226 | 0.23 | 0.209 | 0.211 | 0.21 | 0.204 | 0.207 | 0.21 | 0.205 | 0.204 | 0.199 | 0.21 | 0.204 | 0.211 | 0.211 | 0.211 | 0.213 | 0.217 | 0.218 | 0.214 | 0.204 | 0.199 | 0.206 | 0.208 | 0.226 | 0.21 | 0.226 | 0.209 | 0.209 | 0.205 | 0.215 | 0.216 | 0.218 | 0.221 | 0.216 | 0.216 | 0.214 | 0.208 | 0.215 | 0.235 | 0.215 | 0.21 | 0.216 | 0.236 | 0.211 | 0.239
|  | R | 0.234 | 0.225 | 0.217 | 0.217 | 0.205 | 0.257 | 0.256 | 0.273 | 0.263 | 0.259 | 0.256 | 0.217 | 0.207 | 0.218 | 0.213 | 0.209 | 0.208 | 0.207 | 0.215 | 0.22 | 0.218 | 0.227 | 0.219 | 0.216 | 0.207 | 0.211 | 0.211 | 0.232 | 0.215 | 0.24 | 0.206 | 0.209 | 0.208 | 0.199 | 0.21 | 0.209 | 0.207 | 0.243 | 0.209 | 0.228 | 0.224 | 0.219 | 0.212 | 0.199 | 0.213 | 0.201 | 0.209 | 0.213 | 0.214 | 0.216 | 0.213 | 0.208 | 0.209 | 0.211 | 0.214 | 0.221 | 0.215 | 0.22 | 0.226 | 0.22 | 0.218 | 0.234 | 0.252 | 0.235 | 0.211 | 0.21 | 0.21 | 0.239 | 0.211
A |  | L | 0.219 | 0.241 | 0.211 | 0.219 | 0.23 | 0.25 | 0.278 | 0.278 | 0.26 | 0.28 | 0.264 | 0.22 | 0.23 | 0.229 | 0.215 | 0.205 | 0.204 | 0.208 | 0.218 | 0.206 | 0.239 | 0.251 | 0.234 | 0.199 | 0.215 | 0.205 | 0.21 | 0.213 | 0.21 | 0.223 | 0.205 | 0.202 | 0.212 | 0.219 | 0.223 | 0.217 | 0.197 | 0.2 | RF | 0.257 | 0.227 | 0.221 | 0.201 | 0.203 | 0.199 | 0.227 | 0.191 | 0.219 | 0.216 | 0.215 | 0.207 | 0.192 | 0.202 | 0.202 | 0.2 | RF | 0.248 | 0.219 | 0.223 | 0.21 | 0.223 | 0.211 | 0.201 | RF | 0.22 | 0.232 | 0.217 | RF | RF
0.083 | 0 REFERENCE | C | 0.216 | 0.219 | 0.206 | 0.231 | 0.211 | 0.278 | 0.278 | 0.257 | 0.283 | 0.296 | 0.263 | 0.225 | 0.208 | 0.227 | 0.216 | 0.21 | 0.204 | 0.228 | 0.201 | 0.219 | 0.23 | 0.246 | 0.201 | 0.211 | 0.213 | 0.205 | 0.216 | 0.201 | 0.214 | 0.207 | 0.2 | 0.216 | 0.21 | 0.21 | 0.187 | 0.217 | 0.201 | 0.208 | 0.238 | 0.244 | 0.192 | 0.199 | 0.195 | 0.213 | 0.199 | 0.227 | 0.192 | 0.239 | 0.201 | 0.205 | 0.201 | 0.194 | 0.201 | 0.202 | 0.2 | 0.221 | 0.228 | 0.261 | 0.217 | 0.219 | 0.221 | 0.229 | 0.238 | RF | RF | 0.232 | 0.213 | 0.251 | 0.221
|  | R | RF | 0.21 | 0.205 | 0.221 | 0.232 | 0.266 | 0.278 | 0.267 | 0.27 | 0.281 | 0.263 | 0.225 | 0.212 | 0.227 | 0.206 | 0.208 | 0.202 | 0.213 | 0.208 | 0.217 | 0.234 | RF | 0.199 | 0.216 | 0.218 | 0.213 | 0.207 | 0.237 | 0.208 | 0.218 | 0.204 | 0.206 | 0.21 | 0.202 | 0.205 | 0.233 | 0.207 | 0.202 | 0.257 | RF | 0.22 | 0.215 | 0.198 | 0.208 | 0.191 | 0.196 | 0.219 | 0.208 | 0.205 | 0.203 | 0.194 | 0.194 | 0.202 | 0.202 | 0.2 | 0.229 | RF | 0.222 | 0.217 | 0.219 | 0.237 | 0.229 | 0.228 | 0.246 | RF | 0.22 | 0.212 | 0.232 | 0.221
A | POSITION 'A' | L |  | 0.208 | 0.225 | 0.205 | 0.205 | 0.262 | 0.246 |  |  |  | 0.26 | 0.211 | 0.223 | 0.207 | 0.214 | 0.197 |  |  | 0.212 | 0.208 | 0.22 | 0.207 | 0.204 | 0.206 | [7 empty] | 0.225 | 0.216 | 0.208 | 0.208 |  | 0.209 | 0.205 | 0.205 | 0.206 | 0.199 | 0.2 |  |  | 0.217 | 0.204 | 0.208 | 0.202 | 0.196 | 0.202 |  |  |  | 0.212 | 0.216 | 0.204 | 0.214 | 0.204 | 0.204 |  |  | 0.206 | 0.216 | 0.228 | 0.222 | 0.229 | 0.222
0.083 | OF THE | C |  | 0.208 | 0.219 | 0.207 | 0.204 | 0.255 | 0.249 |  |  |  | 0.25 | 0.207 | 0.215 | 0.226 | 0.204 | 0.204 |  |  | 0.213 | 0.207 | 0.206 | 0.214 | 0.215 | 0.205 | [7 empty] | 0.215 | 0.217 | 0.229 | 0.201 |  | 0.199 | 0.201 | 0.218 | 0.21 | 0.201 | 0.204 |  |  | 0.191 | 0.191 | 0.201 | 0.206 | 0.192 | 0.2 |  |  |  | 0.226 | 0.205 | 0.205 | 0.197 | 0.205 | 0.207 |  |  | 0.215 | 0.227 | 0.212 | 0.228 | 0.236 | 0.203
| SECONDARIES | R |  | 0.208 | 0.23 | 0.202 | 0.218 | 0.245 | 0.253 |  |  |  | 0.247 | 0.217 | 0.2 | 0.22 | 0.198 | 0.214 |  |  | 0.212 | 0.208 | 0.21 | 0.206 | 0.216 | 0.202 | [7 empty] | 0.219 | 0.194 | 0.219 | 0.209 |  | 0.198 | 0.199 | 0.216 | 0.206 | 0.198 | 0.205 |  |  | 0.189 | 0.186 | 0.194 | 0.205 | 0.204 | 0.203 |  |  |  | 0.213 | 0.216 | 0.19 | 0.206 | 0.206 | 0.216 |  |  | 0.217 | 0.225 | 0.217 | 0.225 | 0.232 | 0.225
A | POSITION 'B' | L |  | 0.227 | 0.201 | 0.208 | 0.219 | 0.232 | 0.257 |  |  |  | 0.259 | 0.215 | 0.228 | 0.221 | 0.209 | 0.202 |  |  | 0.204 | 0.204 | 0.228 | 0.227 | 0.214 | 0.212 | [7 empty] | 0.2 | 0.211 | 0.217 | 0.189 |  | 0.199 | 0.2 | 0.212 | 0.224 | 0.237 | 0.221 |  |  | 0.214 | 0.205 | 0.194 | 0.218 | 0.198 | 0.204 |  |  |  | 0.193 | 0.199 | 0.228 | 0.226 | 0.225 | 0.204 |  |  | 0.204 | 0.228 | 0.228 | 0.227 | 0.221 | 0.21
0.083 | OF THE | C |  | 0.205 | 0.192 | 0.212 | 0.216 | 0.234 | 0.247 |  |  |  | 0.258 | 0.225 | 0.208 | 0.223 | 0.209 | 0.207 |  |  | 0.203 | 0.209 | 0.234 | 0.228 | 0.208 | 0.202 | [7 empty] | 0.211 | 0.211 | 0.208 | 0.191 |  | 0.203 | 0.216 | 0.21 | 0.233 | 0.235 | 0.218 |  |  | 0.196 | 0.194 | 0.199 | 0.198 | 0.206 | 0.203 |  |  |  | 0.193 | 0.19 | 0.228 | 0.22 | 0.212 | 0.202 |  |  | 0.201 | 0.217 | 0.234 | 0.226 | 0.228 | 0.211
| SECONDARIES | R |  | 0.208 | 0.194 | 0.223 | 0.219 | 0.239 | 0.257 |  |  |  | 0.252 | 0.228 | 0.206 | 0.207 | 0.207 | 0.213 |  |  | 0.2 | 0.206 | 0.233 | 0.229 | 0.202 | 0.204 | [7 empty] | 0.205 | 0.215 | 0.207 | 0.198 |  | 0.198 | 0.199 | 0.218 | 0.237 | 0.209 | 0.219 |  |  | 0.201 | 0.198 | 0.202 | 0.203 | 0.209 | 0.199 |  |  |  | 0.196 | 0.212 | 0.228 | 0.22 | 0.21 | 0.209 |  |  | 0.211 | 0.22 | 0.23 | 0.227 | 0.222 | 0.205
A |  | L | 0.212 | 0.227 | RF | 0.223 | 0.208 | 0.26 | 0.269 | 0.266 | 0.284 | 0.279 | 0.263 | 0.226 | 0.218 | 0.238 | 0.218 | 0.212 | 0.21 | 0.224 | 0.217 | 0.215 | 0.227 | 0.205 | 0.213 | 0.212 | 0.224 | 0.207 | 0.209 | 0.208 | 0.21 | 0.236 | 0.207 | 0.215 | 0.225 | 0.219 | 0.211 | 0.204 | 0.199 | 0.204 | 0.2 | 0.202 | 0.2 | 0.204 | 0.214 | 0.201 | 0.208 | 0.196 | 0.2 | 0.228 | 0.219 | 0.209 | 0.205 | 0.219 | 0.203 | 0.206 | 0.204 | 0.175 | 0.21 | 0.214 | 0.21 | 0.213 | 0.205 | 0.216 | 0.218 | 0.215 | 0.208 | 0.222 | 0.223 | 0.19 | RF
0.083 | -9 IN | C | RF | 0.221 | 0.227 | 0.213 | 0.218 | 0.261 | 0.269 | 0.276 | 0.271 | 0.266 | 0.261 | 0.254 | 0.215 | 0.221 | 0.232 | 0.228 | 0.208 | 0.215 | 0.198 | 0.203 | 0.221 | 0.205 | 0.208 | 0.212 | 0.223 | 0.207 | 0.206 | 0.21 | 0.23 | 0.21 | 0.201 | 0.19 | 0.197 | 0.205 | 0.217 | 0.21 | 0.214 | 0.189 | 0.248 | 0.194 | 0.206 | 0.197 | 0.222 | 0.196 | 0.202 | 0.196 | 0.21 | 0.202 | 0.214 | 0.194 | 0.207 | 0.202 | 0.207 | 0.192 | 0.192 | 0.205 | 0.196 | 0.215 | 0.2 | 0.222 | 0.215 | 0.221 | 0.218 | 0.208 | 0.213 | 0.222 | 0.223 | 0.186 | 0.222
|  | R | RF | 0.222 | 0.227 | 0.207 | 0.212 | 0.262 | 0.263 | 0.275 | 0.259 | 0.267 | 0.251 | 0.218 | 0.221 | 0.221 | 0.219 | 0.217 | 0.219 | 0.221 | 0.204 | 0.194 | 0.214 | 0.239 | 0.211 | 0.213 | 0.221 | 0.215 | 0.214 | 0.211 | 0.211 | 0.227 | 0.208 | 0.197 | 0.232 | 0.236 | 0.217 | 0.216 | 0.196 | 0.207 | 0.217 | 0.227 | 0.204 | 0.224 | 0.217 | 0.198 | 0.194 | 0.194 | 0.216 | 0.204 | 0.215 | 0.202 | 0.199 | 0.203 | 0.196 | 0.185 | 0.181 | 0.211 | 0.193 | 0.211 | 0.211 | 0.223 | 0.218 | 0.221 | 0.233 | RF | RF | 0.227 | 0.219 | RF | 0.223
A | POSITION 'C' | L |  | 0.228 | 0.228 | 0.229 | 0.216 | 0.224 | 0.254 |  |  |  | 0.255 | 0.236 | 0.214 | 0.242 | 0.22 | 0.221 |  |  | 0.23 | 0.206 | 0.206 | 0.216 | 0.213 | 0.207 | [7 empty] | 0.205 | 0.209 | 0.206 | 0.214 |  | 0.199 | 0.201 | 0.198 | 0.217 | 0.202 | 0.206 |  |  | 0.205 | 0.198 | 0.203 | 0.207 | 0.213 | 0.207 |  |  |  | 0.18 | 0.2 | 0.204 | 0.218 | 0.221 | 0.213 |  |  | 0.209 | 0.235 | 0.217 | 0.206 | 0.218 | 0.222
0.083 | OF THE | C |  | 0.211 | 0.217 | 0.216 | 0.205 | 0.23 | 0.249 |  |  |  | 0.253 | 0.224 | 0.214 | 0.215 | 0.215 | 0.22 |  |  | 0.213 | 0.195 | 0.211 | 0.222 | 0.21 | 0.205 | [7 empty] | 0.217 | 0.197 | 0.198 | 0.207 |  | 0.203 | 0.193 | 0.218 | 0.187 | 0.205 | 0.199 |  |  | 0.201 | 0.188 | 0.188 | 0.197 | 0.202 | 0.2 |  |  |  | 0.194 | 0.199 | 0.214 | 0.201 | 0.207 | 0.208 |  |  | 0.21 | 0.229 | 0.201 | 0.198 | 0.216 | 0.212
| SECONDARIES | R |  | 0.209 | 0.212 | 0.221 | 0.211 | 0.202 | 0.254 |  |  |  | 0.265 | 0.218 | 0.203 | 0.201 | 0.216 | 0.222 |  |  | 0.211 | 0.195 | 0.195 | 0.211 | 0.206 | 0.202 | [7 empty] | 0.208 | 0.206 | 0.209 | 0.202 |  | 0.205 | 0.19 | 0.219 | 0.206 | 0.203 | 0.214 |  |  | 0.199 | 0.198 | 0.212 | 0.205 | 0.193 | 0.204 |  |  |  | 0.176 | 0.16 | 0.199 | 0.195 | 0.211 | 0.21 |  |  | 0.213 | 0.226 | 0.209 | 0.209 | 0.219 | 0.218
A |  | L | 0.214 | 0.227 | 0.232 | 0.228 | 0.24 | 0.303 | 0.274 | 0.276 | 0.264 | 0.265 | 0.255 | 0.221 | 0.234 | 0.23 | 0.231 | 0.212 | 0.225 | 0.208 | 0.211 | 0.209 | 0.214 | 0.218 | 0.206 | 0.214 | 0.214 | 0.21 | 0.206 | 0.212 | 0.212 | 0.214 | 0.207 | 0.229 | 0.208 | 0.204 | 0.206 | 0.198 | 0.205 | 0.209 | 0.203 | 0.205 | 0.211 | 0.209 | 0.199 | 0.206 | 0.199 | 0.209 | 0.206 | 0.207 | 0.208 | 0.213 | 0.207 | 0.212 | 0.216 | 0.212 | 0.212 | 0.222 | 0.219 | 0.212 | 0.193 | 0.219 | 0.223 | 0.213 | 0.226 | 0.215 | 0.21 | 0.219 | 0.234 | 0.215 | 0.218
0.083 | -18 IN | C | 0.23 | 0.221 | 0.224 | 0.244 | 0.207 | 0.294 | 0.291 | 0.298 | 0.278 | 0.256 | 0.258 | 0.223 | 0.234 | 0.219 | 0.231 | 0.213 | 0.245 | 0.204 | 0.216 | 0.211 | 0.212 | 0.217 | 0.207 | 0.218 | 0.217 | 0.216 | 0.21 | 0.235 | 0.212 | 0.209 | 0.208 | 0.205 | 0.199 | 0.204 | 0.206 | 0.208 | 0.197 | 0.193 | 0.205 | 0.201 | 0.199 | 0.194 | 0.208 | 0.214 | 0.19 | 0.203 | 0.196 | 0.21 | 0.204 | 0.215 | 0.197 | 0.202 | 0.203 | 0.203 | 0.211 | 0.219 | 0.208 | 0.212 | 0.208 | 0.218 | 0.208 | 0.21 | 0.226 | 0.218 | 0.211 | 0.233 | 0.221 | 0.216 | 0.219
|  | R | RF | 0.226 | 0.218 | 0.241 | 0.233 | 0.271 | 0.292 | 0.302 | 0.261 | 0.252 | 0.256 | 0.209 | 0.215 | 0.219 | 0.213 | 0.218 | 0.221 | 0.239 | 0.217 | 0.217 | 0.208 | 0.236 | 0.214 | 0.22 | 0.214 | 0.216 | 0.215 | 0.234 | 0.213 | 0.211 | 0.213 | 0.217 | 0.22 | 0.226 | 0.211 | 0.214 | 0.203 | 0.196 | 0.201 | 0.198 | 0.193 | 0.229 | 0.2 | 0.196 | 0.193 | 0.202 | 0.196 | 0.207 | 0.204 | 0.217 | 0.202 | 0.204 | 0.2 | 0.209 | 0.21 | 0.225 | 0.221 | 0.223 | 0.215 | 0.221 | 0.21 | 0.222 | 0.233 | 0.228 | 0.247 | 0.222 | 0.222 | 0.226 | 0.21
A |  | L | 0.206 | RF | 0.228 | 0.237 | 0.226 | 0.262 | 0.297 | 0.266 | 0.261 | 0.25 | 0.264 | 0.225 | 0.236 | 0.23 | 0.226 | 0.22 | 0.215 | 0.206 | 0.217 | 0.211 | 0.215 | 0.212 | 0.216 | 0.216 | 0.202 | 0.213 | 0.214 | 0.215 | 0.215 | 0.217 | 0.207 | 0.208 | 0.217 | 0.211 | 0.215 | 0.204 | 0.201 | 0.204 | 0.21 | 0.205 | 0.211 | 0.21 | 0.221 | 0.216 | 0.211 | 0.213 | 0.21 | 0.217 | 0.224 | 0.215 | 0.214 | 0.21 | 0.21 | 0.215 | 0.208 | 0.227 | 0.22 | 0.221 | 0.211 | 0.216 | 0.216 | 0.208 | 0.207 | 0.227 | 0.219 | 0.224 | 0.222 | 0.214 | RF
0.083 | -27 IN | C | RF | 0.229 | 0.249 | 0.231 | 0.226 | 0.267 | 0.273 | 0.294 | 0.3 | 0.262 | 0.264 | 0.226 | 0.22 | 0.23 | 0.219 | 0.218 | 0.213 | 0.214 | 0.225 | 0.215 | 0.214 | 0.209 | 0.219 | 0.214 | 0.213 | 0.212 | 0.207 | 0.209 | 0.213 | 0.208 | 0.211 | 0.207 | 0.206 | 0.204 | 0.198 | 0.208 | 0.201 | 0.212 | 0.212 | 0.209 | 0.205 | 0.205 | 0.228 | 0.235 | 0.228 | 0.216 | 0.205 | 0.221 | 0.215 | 0.212 | 0.221 | 0.206 | 0.213 | 0.207 | 0.211 | 0.206 | 0.21 | 0.211 | 0.219 | 0.21 | 0.216 | 0.203 | 0.202 | 0.216 | 0.221 | 0.228 | 0.216 | 0.21 | RF
|  | R | RF | 0.226 | 0.301 | 0.223 | 0.232 | 0.259 | 0.264 | 0.262 | 0.269 | 0.26 | 0.265 | 0.231 | 0.222 | 0.231 | 0.212 | 0.223 | 0.212 | 0.216 | 0.215 | 0.226 | 0.215 | 0.216 | 0.216 | 0.217 | 0.216 | 0.215 | 0.215 | 0.216 | 0.208 | 0.225 | 0.215 | 0.227 | 0.217 | 0.225 | 0.213 | 0.235 | 0.201 | 0.223 | 0.217 | 0.199 | 0.206 | 0.209 | 0.223 | 0.215 | 0.204 | 0.203 | 0.206 | 0.217 | 0.211 | 0.211 | 0.214 | 0.204 | 0.212 | 0.213 | 0.213 | 0.217 | 0.234 | 0.211 | 0.216 | 0.223 | 0.216 | 0.212 | 0.21 | 0.226 | 0.226 | 0.218 | 0.22 | 0.232 | 0.234
A |  | L | 0.229 | RF | 0.227 | 0.228 | 0.218 | 0.256 | 0.275 | 0.263 | 0.263 | 0.259 | 0.262 | 0.225 | 0.227 | 0.245 | 0.218 | 0.224 | 0.208 | 0.217 | 0.217 | 0.205 | 0.245 | 0.21 | 0.217 | 0.222 | 0.216 | 0.214 | 0.213 | 0.216 | 0.22 | 0.206 | 0.206 | 0.209 | 0.216 | 0.215 | 0.234 | 0.215 | 0.211 | 0.213 | 0.211 | 0.216 | 0.217 | 0.226 | 0.226 | 0.215 | 0.216 | 0.225 | 0.216 | 0.226 | 0.222 | 0.204 | 0.204 | 0.22 | 0.22 | 0.215 | 0.214 | 0.213 | 0.225 | 0.225 | 0.214 | 0.224 | 0.221 | 0.215 | 0.223 | 0.222 | 0.254 | 0.225 | 0.222 | 0.243 | 0.23
0.083 | -36 IN | C | RF | 0.22 | 0.226 | 0.228 | 0.218 | 0.269 | 0.29 | 0.266 | 0.256 | 0.251 | 0.261 | 0.227 | 0.218 | 0.217 | 0.219 | 0.233 | 0.216 | 0.222 | 0.222 | 0.2 | 0.243 | 0.214 | 0.213 | 0.219 | 0.216 | 0.21 | 0.219 | 0.245 | 0.217 | 0.208 | 0.203 | 0.207 | 0.225 | 0.224 | 0.208 | 0.215 | 0.225 | 0.217 | 0.212 | 0.214 | 0.209 | 0.226 | 0.218 | 0.207 | 0.229 | 0.226 | 0.219 | 0.224 | 0.226 | 0.214 | 0.208 | 0.222 | 0.22 | 0.229 | 0.215 | 0.212 | 0.229 | 0.214 | 0.214 | 0.224 | 0.213 | 0.213 | 0.217 | 0.227 | 0.222 | 0.221 | 0.228 | 0.219 | 0.227
|  | R | RF | 0.219 | 0.225 | 0.226 | 0.22 | 0.268 | 0.267 | 0.267 | 0.258 | 0.251 | 0.266 | 0.225 | 0.22 | 0.218 | 0.223 | 0.217 | 0.206 | 0.218 | 0.222 | 0.212 | 0.225 | 0.212 | 0.205 | 0.217 | 0.217 | 0.205 | 0.217 | 0.218 | 0.22 | 0.21 | 0.208 | 0.213 | 0.222 | 0.221 | 0.214 | 0.209 | 0.214 | 0.221 | 0.218 | 0.214 | 0.21 | 0.212 | 0.216 | 0.214 | 0.21 | 0.221 | 0.225 | 0.225 | 0.211 | 0.217 | 0.213 | 0.218 | 0.215 | 0.22 | 0.228 | 0.225 | 0.213 | 0.214 | 0.219 | 0.224 | 0.215 | 0.218 | 0.213 | 0.232 | 0.223 | 0.214 | 0.227 | 0.219 | 0.226
A |  | L | 0.227 | 0.226 | 0.249 | 0.235 | RF | 0.244 | 0.27 | 0.266 | 0.284 | 0.267 | 0.258 | 0.234 | 0.218 | 0.226 | 0.223 | 0.214 | 0.217 | 0.22 | 0.215 | 0.199 | 0.213 | 0.229 | 0.235 | 0.227 | 0.219 | 0.206 | 0.218 | 0.24 | 0.212 | 0.223 | 0.208 | 0.208 | 0.198 | 0.213 | 0.22 | 0.222 | 0.219 | 0.211 | 0.21 | 0.22 | 0.21 | 0.217 | 0.223 | 0.218 | 0.208 | 0.23 | 0.217 | 0.212 | 0.219 | 0.215 | 0.219 | 0.219 | 0.207 | 0.21 | 0.224 | 0.218 | 0.218 | 0.218 | 0.211 | 0.219 | 0.213 | 0.229 | 0.199 | 0.219 | 0.218 | 0.203 | 0.215 | 0.212 | 0.228
0.083 | -45 IN | C | RF | 0.228 | 0.225 | 0.225 | 0.228 | 0.272 | 0.265 | 0.285 | 0.252 | 0.27 | 0.263 | 0.223 | 0.22 | 0.222 | 0.236 | 0.22 | 0.219 | 0.219 | 0.235 | 0.214 | 0.213 | 0.228 | 0.211 | 0.217 | 0.233 | 0.203 | 0.227 | 0.216 | 0.214 | 0.216 | 0.211 | 0.209 | 0.226 | 0.221 | 0.22 | 0.218 | 0.218 | 0.209 | 0.222 | 0.232 | 0.211 | 0.239 | 0.229 | 0.218 | 0.208 | 0.23 | 0.222 | 0.223 | 0.211 | 0.214 | 0.211 | 0.22 | 0.218 | 0.218 | 0.217 | 0.211 | 0.223 | 0.211 | 0.213 | 0.229 | 0.244 | 0.221 | 0.211 | 0.214 | 0.205 | 0.214 | 0.244 | 0.217 | 0.215
|  | R | RF | 0.231 | 0.244 | 0.231 | 0.222 | 0.265 | 0.271 | 0.269 | 0.253 | 0.252 | 0.28 | 0.222 | 0.222 | 0.22 | 0.219 | 0.224 | 0.224 | 0.22 | 0.22 | 0.217 | 0.228 | 0.214 | 0.217 | 0.217 | 0.224 | 0.216 | 0.224 | 0.217 | 0.213 | 0.225 | 0.219 | 0.232 | 0.214 | 0.233 | 0.216 | 0.21 | 0.215 | 0.213 | 0.23 | 0.225 | 0.224 | 0.209 | 0.227 | 0.213 | 0.207 | 0.218 | 0.212 | 0.215 | 0.212 | 0.225 | 0.213 | 0.209 | 0.213 | 0.217 | 0.218 | 0.212 | 0.226 | 0.212 | 0.223 | 0.222 | 0.241 | 0.2 | 0.208 | 0.214 | 0.205 | 0.21 | 0.217 | 0.212 | 0.215
A |  | L | 0.225 | RF | RF | 0.227 | 0.235 | 0.25 | 0.276 | 0.278 | 0.253 | 0.267 | 0.271 | 0.216 | 0.218 | 0.219 | 0.219 | 0.218 | 0.225 | 0.228 | 0.224 | 0.211 | 0.213 | 0.215 | 0.214 | 0.216 | 0.216 | 0.211 | 0.211 | 0.221 | 0.215 | 0.216 | 0.216 | 0.204 | 0.227 | 0.217 | 0.212 | 0.205 | 0.226 | 0.225 | 0.213 | 0.232 | 0.219 | 0.222 | 0.23 | 0.225 | 0.224 | 0.234 | 0.222 | 0.227 | 0.227 | 0.214 | 0.22 | 0.216 | 0.215 | 0.217 | 0.21 | 0.213 | 0.223 | 0.212 | 0.202 | 0.21 | 0.203 | 0.209 | 0.206 | 0.201 | 0.205 | 0.199 | 0.209 | 0.215 | 0.245
0.083 | -54 IN | C | 0.225 | RF | 0.228 | 0.224 | 0.227 | RF | 0.271 | 0.271 | 0.242 | 0.261 | 0.284 | 0.216 | 0.219 | 0.223 | 0.241 | 0.217 | 0.225 | 0.222 | 0.237 | 0.212 | 0.237 | 0.219 | 0.219 | 0.214 | 0.226 | 0.228 | 0.214 | 0.228 | 0.211 | 0.209 | 0.221 | 0.212 | 0.234 | 0.221 | 0.22 | 0.221 | 0.211 | 0.214 | 0.22 | 0.222 | 0.211 | 0.218 | 0.223 | 0.221 | 0.219 | 0.222 | 0.214 | 0.222 | 0.221 | 0.209 | 0.214 | 0.227 | 0.219 | 0.209 | 0.21 | 0.206 | 0.211 | 0.213 | 0.213 | 0.204 | 0.201 | 0.212 | 0.217 | 0.21 | 0.203 | 0.189 | 0.21 | 0.203 | 0.227
|  | R | 0.225 | 0.226 | 0.229 | 0.224 | 0.223 | 0.273 | 0.274 | 0.263 | 0.27 | 0.253 | 0.265 | 0.228 | 0.22 | 0.217 | 0.226 | 0.216 | 0.216 | 0.231 | 0.24 | 0.219 | 0.221 | 0.22 | 0.225 | 0.213 | 0.243 | 0.221 | 0.215 | 0.22 | 0.215 | 0.204 | 0.221 | 0.223 | 0.231 | 0.235 | 0.212 | 0.221 | 0.207 | 0.219 | 0.224 | 0.219 | 0.208 | 0.227 | 0.216 | 0.214 | 0.214 | 0.215 | 0.212 | 0.222 | 0.206 | 0.204 | 0.211 | 0.216 | 0.219 | 0.214 | 0.214 | 0.218 | 0.218 | 0.214 | 0.197 | 0.203 | 0.201 | 0.205 | 0.2 | 0.206 | 0.202 | 0.205 | 0.208 | 0.212 | 0.218
A | POSITION 'A' | L |  |  | 0.219 | 0.228 |  | 0.255 | 0.266 |  | 0.25 | 0.252 |  | 0.229 | 0.219 |  | 0.226 | 0.222 |  | 0.227 | 0.216 |  | 0.213 | 0.212 |  | 0.221 | 0.216 |  | 0.218 | 0.213 |  | 0.222 | 0.212 |  | 0.211 | 0.21 |  | 0.214 | 0.215 |  | 0.209 | 0.213 |  | 0.216 | 0.217 |  | 0.217 | 0.228 |  | 0.213 | 0.209 |  | 0.219 | 0.218 |  | 0.232 | 0.214 |  | 0.223 | 0.219 |  | 0.216 | 0.218 |  | 0.213 | 0.22 |  | 0.217 | 0.218
0.083 | OF THE | C |  |  | 0.218 | 0.225 |  | 0.257 | 0.261 |  | 0.259 | 0.251 |  | 0.22 | 0.216 |  | 0.23 | 0.211 |  | 0.216 | 0.217 |  | 0.217 | 0.216 |  | 0.216 | 0.22 |  | 0.217 | 0.207 |  | 0.218 | 0.211 |  | 0.21 | 0.211 |  | 0.222 | 0.216 |  | 0.207 | 0.215 |  | 0.211 | 0.219 |  | 0.216 | 0.226 |  | 0.222 | 0.205 |  | 0.213 | 0.217 |  | 0.224 | 0.211 |  | 0.222 | 0.207 |  | 0.216 | 0.205 |  | 0.21 | 0.223 |  | 0.217 | 0.22
| PRIMARIES | R |  |  | 0.224 | 0.224 |  | 0.261 | 0.266 |  | 0.254 | 0.25 |  | 0.212 | 0.218 |  | 0.229 | 0.216 |  | 0.227 | 0.224 |  | 0.217 | 0.211 |  | 0.216 | 0.22 |  | 0.218 | 0.22 |  | 0.223 | 0.213 |  | 0.205 | 0.221 |  | 0.212 | 0.219 |  | 0.209 | 0.209 |  | 0.21 | 0.209 |  | 0.198 | 0.22 |  | 0.212 | 0.22 |  | 0.208 | 0.211 |  | 0.22 | 0.217 |  | 0.211 | 0.209 |  | 0.218 | 0.209 |  | 0.217 | 0.219 |  | 0.213 | 0.225
A | POSITION 'B' | L |  |  | 0.227 | 0.213 |  | 0.257 | 0.266 |  | 0.247 | 0.252 |  | 0.215 | 0.215 |  | 0.213 | 0.212 |  | 0.208 | 0.218 |  | 0.205 | 0.217 |  | 0.214 | 0.215 |  | 0.21 | 0.217 |  | 0.207 | 0.212 |  | 0.218 | 0.214 |  | 0.207 | 0.211 |  | 0.209 | 0.222 |  | 0.229 | 0.219 |  | 0.2 | 0.222 |  | 0.212 | 0.209 |  | 0.215 | 0.219 |  | 0.215 | 0.215 |  | 0.211 | 0.211 |  | 0.217 | 0.21 |  | 0.22 | 0.207 |  | 0.203 | 0.22
0.083 | OF THE | C |  |  | 0.219 | 0.209 |  | 0.249 | 0.263 |  | 0.242 | 0.224 |  | 0.216 | 0.209 |  | 0.213 | 0.213 |  | 0.215 | 0.232 |  | 0.212 | 0.226 |  | 0.225 | 0.225 |  | 0.213 | 0.219 |  | 0.205 | 0.221 |  | 0.219 | 0.216 |  | 0.209 | 0.211 |  | 0.209 | 0.217 |  | 0.206 | 0.219 |  | 0.215 | 0.22 |  | 0.22 | 0.203 |  | 0.216 | 0.229 |  | 0.206 | 0.206 |  | 0.214 | 0.205 |  | 0.224 | 0.205 |  | 0.221 | 0.218 |  | 0.2 | 0.204
| PRIMARIES | R |  |  | 0.225 | 0.213 |  | 0.252 | 0.264 |  | 0.249 | 0.244 |  | 0.21 | 0.219 |  | 0.219 | 0.214 |  | 0.214 | 0.224 |  | 0.216 | 0.215 |  | 0.214 | 0.216 |  | 0.214 | 0.212 |  | 0.205 | 0.215 |  | 0.22 | 0.22 |  | 0.21 | 0.205 |  | 0.201 | 0.224 |  | 0.204 | 0.205 |  | 0.214 | 0.213 |  | 0.211 | 0.216 |  | 0.217 | 0.213 |  | 0.205 | 0.205 |  | 0.222 | 0.206 |  | 0.216 | 0.211 |  | 0.199 | 0.22 |  | 0.204 | 0.211
A | POSITION 'C' | L |  |  | 0.197 | 0.212 |  | 0.253 | 0.259 |  | 0.251 | 0.253 |  | 0.214 | 0.206 |  | 0.212 | 0.216 |  | 0.207 | 0.208 |  | 0.211 | 0.21 |  | 0.209 | 0.218 |  | 0.212 | 0.216 |  | 0.208 | 0.216 |  | 0.22 | 0.203 |  | 0.21 | 0.202 |  | 0.214 | 0.219 |  | 0.22 | 0.217 |  | 0.209 | 0.226 |  | 0.226 | 0.205 |  | 0.22 | 0.209 |  | 0.208 | 0.206 |  | 0.222 | 0.215 |  | 0.218 | 0.206 |  | 0.208 | 0.211 |  | 0.208 | 0.212
0.083 | OF THE | C |  |  | 0.198 | 0.193 |  | 0.25 | 0.234 |  | 0.239 | 0.252 |  | 0.208 | 0.205 |  | 0.212 | 0.209 |  | 0.212 | 0.205 |  | 0.21 | 0.219 |  | 0.218 | 0.216 |  | 0.207 | 0.209 |  | 0.214 | 0.21 |  | 0.205 | 0.203 |  | 0.21 | 0.208 |  | 0.218 | 0.212 |  | 0.206 | 0.212 |  | 0.209 | 0.214 |  | 0.218 | 0.208 |  | 0.219 | 0.216 |  | 0.204 | 0.209 |  | 0.216 | 0.211 |  | 0.212 | 0.206 |  | 0.195 | 0.214 |  | 0.209 | 0.202
| PRIMARIES | R |  |  | 0.212 | 0.222 |  | 0.254 | 0.245 |  | 0.247 | 0.256 |  | 0.206 | 0.225 |  | 0.219 | 0.213 |  | 0.217 | 0.215 |  | 0.214 | 0.213 |  | 0.214 | 0.215 |  | 0.209 | 0.205 |  | 0.208 | 0.214 |  | 0.213 | 0.217 |  | 0.207 | 0.198 |  | 0.215 | 0.213 |  | 0.209 | 0.209 |  | 0.209 | 0.209 |  | 0.208 | 0.206 |  | 0.209 | 0.206 |  | 0.199 | 0.219 |  | 0.209 | 0.203 |  | 0.212 | 0.2 |  | 0.197 | 0.207 |  | 0.196 | 0.231
A |  | L | 0.228 | 0.241 | 0.248 | 0.224 | 0.212 | 0.259 | 0.261 | 0.251 | 0.264 | 0.264 | 0.261 | 0.204 | 0.216 | 0.223 | 0.204 | 0.219 | 0.208 | 0.215 | 0.227 | 0.199 | 0.212 | 0.221 | 0.213 | 0.226 | 0.22 | 0.198 | 0.218 | 0.216 | 0.214 | 0.219 | 0.199 | 0.209 | 0.214 | 0.215 | 0.218 | 0.201 | 0.202 | 0.219 | 0.218 | 0.224 | 0.229 | 0.218 | 0.222 | 0.217 | 0.214 | 0.217 | 0.223 | 0.223 | 0.207 | 0.205 | 0.207 | 0.219 | 0.229 | 0.217 | 0.226 | 0.224 | 0.211 | 0.214 | 0.212 | 0.216 | 0.223 | 0.227 | 0.21 | 0.213 | 0.228 | 0.202 | 0.22 | 0.215 | RF
0.083 | -63 IN | C | 0.278 | 0.222 | 0.222 | 0.209 | 0.204 | 0.257 | 0.286 | 0.261 | 0.249 | 0.264 | 0.254 | 0.203 | 0.211 | 0.208 | 0.215 | 0.224 | 0.198 | 0.22 | 0.23 | 0.198 | 0.23 | 0.229 | 0.218 | 0.222 | 0.219 | 0.213 | 0.217 | 0.212 | 0.214 | 0.212 | 0.208 | 0.212 | 0.206 | 0.205 | 0.214 | 0.205 | 0.204 | 0.201 | 0.219 | 0.217 | 0.208 | 0.222 | 0.216 | 0.216 | 0.21 | 0.216 | 0.234 | 0.222 | 0.209 | 0.22 | 0.203 | 0.211 | 0.219 | 0.21 | 0.217 | 0.218 | 0.206 | 0.2 | 0.213 | 0.224 | 0.203 | 0.228 | 0.189 | 0.211 | 0.209 | 0.191 | 0.226 | 0.215 | 0.226
|  | R | 0.207 | 0.204 | 0.222 | 0.223 | 0.217 | 0.259 | 0.263 | 0.248 | 0.253 | 0.264 | 0.255 | 0.206 | 0.217 | 0.21 | 0.219 | 0.221 | 0.202 | 0.234 | 0.234 | 0.195 | 0.221 | 0.225 | 0.232 | 0.224 | 0.218 | 0.217 | 0.22 | 0.212 | 0.214 | 0.213 | 0.22 | 0.214 | 0.209 | 0.227 | 0.209 | 0.204 | 0.202 | 0.217 | 0.215 | 0.209 | 0.206 | 0.222 | 0.214 | 0.214 | 0.221 | 0.216 | 0.217 | 0.218 | 0.206 | 0.221 | 0.207 | 0.211 | 0.207 | 0.214 | 0.217 | 0.223 | 0.212 | 0.208 | 0.215 | 0.221 | 0.205 | 0.201 | 0.186 | 0.219 | 0.204 | 0.199 | 0.217 | 0.218 | 0.216
A |  | L | 0.222 | 0.218 | 0.217 | 0.232 | 0.213 | 0.247 | 0.274 | 0.278 | 0.238 | 0.252 | 0.249 | 0.209 | 0.212 | 0.226 | 0.216 | 0.2 | 0.21 | 0.219 | 0.213 | 0.209 | 0.216 | 0.219 | 0.206 | 0.222 | 0.213 | 0.207 | 0.209 | 0.2 | 0.219 | 0.22 | 0.209 | 0.226 | 0.209 | 0.23 | 0.207 | 0.208 | 0.213 | 0.216 | 0.21 | 0.216 | 0.21 | 0.225 | 0.213 | 0.22 | 0.207 | 0.216 | 0.217 | 0.218 | 0.213 | 0.231 | 0.219 | 0.21 | 0.23 | 0.21 | 0.209 | 0.226 | 0.236 | 0.221 | 0.23 | 0.243 | 0.216 | 0.216 | 0.22 | 0.219 | 0.216 | 0.204 | 0.219 | 0.216 | 0.211
0.083 | -72 IN | C | 0.214 | 0.218 | 0.207 | 0.205 | 0.206 | 0.262 | 0.245 | 0.255 | 0.236 | 0.23 | 0.25 | 0.21 | 0.21 | 0.216 | 0.214 | 0.206 | 0.218 | 0.221 | 0.221 | 0.203 | 0.212 | 0.214 | 0.22 | 0.226 | 0.211 | 0.22 | 0.217 | 0.205 | 0.215 | 0.214 | 0.211 | 0.209 | 0.209 | 0.195 | 0.201 | 0.203 | 0.209 | 0.201 | 0.209 | 0.236 | 0.2 | 0.212 | 0.203 | 0.211 | 0.205 | 0.217 | 0.209 | 0.224 | 0.21 | 0.221 | 0.222 | 0.224 | 0.215 | 0.214 | 0.212 | 0.222 | 0.227 | 0.213 | 0.232 | 0.224 | 0.22 | 0.213 | 0.24 | 0.223 | 0.22 | 0.215 | 0.215 | 0.216 | 0.215
|  | R | 0.232 | 0.22 | 0.219 | 0.216 | 0.218 | 0.246 | 0.25 | 0.259 | 0.245 | 0.238 | 0.258 | 0.202 | 0.211 | 0.216 | 0.212 | 0.212 | 0.214 | 0.221 | 0.217 | 0.202 | 0.218 | 0.226 | 0.223 | 0.233 | 0.236 | 0.212 | 0.226 | 0.219 | 0.216 | 0.212 | 0.208 | 0.219 | 0.213 | 0.207 | 0.207 | 0.215 | 0.226 | 0.22 | 0.207 | 0.223 | 0.205 | 0.214 | 0.215 | 0.216 | 0.222 | 0.217 | 0.211 | 0.224 | 0.214 | 0.214 | 0.223 | 0.226 | 0.218 | 0.212 | 0.24 | 0.216 | 0.224 | 0.217 | 0.233 | 0.222 | 0.216 | 0.212 | 0.223 | 0.219 | 0.217 | 0.222 | 0.223 | 0.214 | 0.211
A |  | L | 0.206 | 0.219 | 0.218 | 0.224 | 0.22 | 0.263 | 0.263 | 0.255 | 0.255 | 0.245 | 0.26 | 0.202 | 0.228 | 0.217 | 0.225 | 0.211 | 0.208 | 0.207 | 0.214 | 0.215 | 0.219 | 0.214 | 0.214 | 0.218 | 0.214 | 0.229 | 0.212 | 0.218 | 0.212 | 0.212 | 0.21 | 0.218 | 0.224 | 0.212 | 0.212 | 0.22 | 0.217 | 0.211 | 0.218 | 0.214 | 0.227 | 0.214 | 0.216 | 0.214 | 0.212 | 0.222 | 0.218 | 0.227 | 0.226 | 0.22 | 0.217 | 0.227 | 0.23 | 0.221 | 0.222 | 0.229 | 0.221 | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST
0.083 | -81 IN | C | 0.214 | 0.24 | 0.228 | 0.227 | 0.221 | 0.26 | 0.262 | 0.256 | 0.251 | 0.247 | 0.249 | 0.2 | 0.211 | 0.214 | 0.211 | 0.2 | 0.221 | 0.209 | 0.224 | 0.213 | 0.227 | 0.234 | 0.213 | 0.225 | 0.219 | 0.211 | 0.224 | 0.208 | 0.229 | 0.215 | 0.211 | 0.219 | 0.22 | 0.212 | 0.217 | 0.216 | 0.212 | 0.211 | 0.227 | 0.221 | 0.217 | 0.219 | 0.217 | 0.221 | 0.212 | 0.23 | 0.218 | 0.238 | 0.223 | 0.222 | 0.226 | 0.216 | 0.23 | 0.225 | 0.216 | 0.222 | 0.219 | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST
|  | R | 0.217 | 0.235 | 0.23 | 0.224 | 0.22 | 0.246 | 0.255 | 0.256 | 0.258 | 0.249 | 0.265 | 0.217 | 0.227 | 0.22 | 0.228 | 0.21 | 0.22 | 0.222 | 0.223 | 0.236 | 0.211 | 0.231 | 0.221 | 0.23 | 0.231 | 0.234 | 0.232 | 0.225 | 0.223 | 0.215 | 0.211 | 0.243 | 0.222 | 0.212 | 0.214 | 0.215 | 0.233 | 0.216 | 0.22 | 0.213 | 0.213 | 0.22 | 0.207 | 0.215 | 0.215 | 0.226 | 0.214 | 0.237 | 0.227 | 0.222 | 0.214 | 0.234 | 0.226 | 0.246 | 0.22 | 0.231 | 0.218 | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST
A |  | L | 0.231 | 0.231 | 0.224 | 0.252 | 0.221 | 0.254 | 0.258 | 0.27 | 0.26 | 0.268 | 0.252 | 0.233 | 0.227 | 0.23 | 0.237 | 0.211 | 0.211 | 0.216 | 0.211 | 0.233 | 0.22 | 0.219 | 0.222 | 0.232 | 0.223 | 0.193 | 0.221 | 0.223 | 0.221 | 0.221 | 0.219 | 0.243 | 0.219 | 0.222 | 0.22 | 0.224 | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST
0.083 | -90 IN | C | 0.217 | 0.22 | 0.231 | 0.236 | 0.225 | 0.274 | 0.261 | 0.26 | 0.271 | 0.252 | 0.25 | 0.225 | 0.221 | 0.24 | 0.228 | 0.211 | 0.217 | 0.216 | 0.235 | 0.223 | 0.216 | 0.221 | 0.228 | 0.241 | 0.236 | 0.225 | 0.221 | 0.207 | 0.221 | 0.222 | 0.215 | 0.232 | 0.221 | 0.223 | 0.216 | 0.226 | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST
|  | R | 0.248 | 0.223 | 0.243 | 0.227 | 0.214 | 0.251 | 0.264 | 0.258 | 0.273 | 0.244 | 0.247 | 0.225 | 0.221 | 0.232 | 0.23 | 0.214 | 0.215 | 0.211 | 0.234 | 0.22 | 0.217 | 0.229 | 0.23 | 0.224 | 0.23 | 0.214 | 0.221 | 0.228 | 0.225 | 0.227 | 0.229 | 0.235 | 0.223 | 0.218 | 0.211 | 0.224 | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MIN
A | 0.001-0.083 | 0.140-0.149 | 10: OUTSIDE DIAMETER:; 23: 3; 30: INSPECTION RESULTS; 67: APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com |  |  | EXAMPLE PAPER
LEGEND | 0.100-0.109 | 0.150-0.159 | 10: TUBE MATERIAL:; 23: SA-210A1; 35: MAX. THICKNESS |  |  | RIVERDALE MILL
| 0.110-0.119 | 0.160-0.169 | 10: NOMINAL WALL:; 23: 0.203; 35: AVG. THICKNESS |  |  | TUBE WALL THICKNESS SURVEY
| 0.120-0.129 | 0.170-0.179 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS |  |  | NO. 1 RECOVERY BOILER
| 0.130-0.139 | 0.180-0.999 | 10: MILL FLAG:; 23: 0.1; 35: STD DEV.; 46: Job # H449364 P.O. # 0018342455 W.O. # N/A Date: 5/05/2025 |  |  | 03 LEFT WALL W/ PORTS
THICKNESS
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Corrosion
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. CORROSION RATE MEASUREMENTS ARE IN MILS. | [72 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MAX
A |  | L | 8.15 | 1.16 | 1.45 | 0.532 | 2.42 | ND | 0.051 | ND | 8.5 | ND | ND | 0.263 | 1.45 | 6.4 | 0.359 | 0.493 | 0.436 | 0.304 | ND | 4.37 | 4.59 | ND | 0.136 | ND | 1.48 | 0.21 | 0.801 | 2.2 | 5.13 | 1.87 | 3.6 | ND | ND | ND | ND | 1.59 | 3.38 | 4.56 | 8.49 | ND | ND | ND | 2.1 | 2.18 | ND | ND | ND | 0.852 | ND | ND | ND | 1.35 | ND | 0.451 | 4.14 | ND | ND | ND | ND | ND | 1.11 | 0.678 | ND | ND | ND | 0.973 | 0.645 | ND | 2.82
| +16 FT 6 IN | C | 4.39 | 1.63 | 1.86 | ND | ND | 0.779 | ND | ND | ND | 0.26 | 2.12 | ND | 0.196 | ND | ND | 0.576 | ND | 0.213 | 0.62 | ND | ND | 0.514 | ND | ND | 1.17 | ND | 2.18 | ND | 6.66 | 3.92 | 5.19 | ND | ND | ND | ND | ND | 4.57 | 3.37 | 1.08 | ND | ND | ND | ND | 1.26 | ND | ND | ND | 5.66 | 0.229 | ND | 0.373 | 0.814 | ND | 1.72 | 0.665 | 1.33 | ND | ND | ND | ND | 1.31 | ND | ND | ND | ND | 0.964 | ND | ND | 2.75
|  | R | 2.28 | 2.2 | ND | ND | ND | 0.061 | 12.7 | 7.52 | ND | ND | 5.67 | ND | ND | ND | 1.04 | ND | 0.094 | 1.08 | 2.16 | 7.89 | ND | ND | ND | ND | 1.26 | 3.34 | 0.192 | 0.807 | 3.91 | 1.72 | 4.39 | 3.73 | ND | ND | ND | ND | 3.9 | 1.43 | 0.727 | 0.459 | ND | ND | 4.82 | ND | ND | ND | ND | 0.547 | 0.207 | 4.14 | 0.812 | 1.94 | ND | 0.723 | 1.68 | 0.685 | ND | ND | 4.12 | 0.071 | ND | 0.797 | 0.117 | ND | ND | ND | ND | ND | ND
A |  | L | ND | ND | ND | 3.56 | 3.99 | ND | 1.19 | 1.87 | 1.15 | 0.293 | 3.2 | 0.837 | ND | 0.982 | 3.48 | 1.86 | 0.883 | 0.271 | 0.401 | 2.27 | 1.91 | 0.531 | ND | 0.502 | 2.64 | 0.408 | ND | 1.18 | ND | ND | 1.9 | ND | 6.38 | ND | ND | ND | 1.76 | 1.53 | 0.883 | 2.75 | ND | 4.11 | ND | 1.73 | 0.961 | 1.21 | 0.257 | 2.4 | ND | 5.08 | ND | 1.82 | ND | 5.83 | 5.16 | ND | ND | 1.54 | 2.04 | 2.69 | 1.35 | 0.269 | 2.31 | 0.261 | ND | ND | 1.22 | 0.01 | ND
| +15 FT | C | ND | ND | 0.446 | 1.2 | 4.61 | ND | ND | 1.36 | ND | 1.2 | 3.61 | ND | ND | 1.32 | ND | ND | ND | ND | 1.03 | 1.63 | ND | 5.69 | 6.99 | ND | 6.4 | 1.41 | 3.13 | 1.92 | ND | 2.08 | ND | ND | ND | 1.21 | 4.11 | ND | 0.412 | 1.04 | 1.37 | ND | ND | 0.902 | 2.12 | ND | 2.37 | 0.625 | 2.01 | ND | 0.354 | ND | 0.086 | 5.14 | ND | 3.72 | 3.54 | 4.79 | 3.06 | ND | 0.164 | ND | 0.829 | 0.831 | ND | 0.481 | ND | ND | 2.09 | 0.513 | ND
|  | R | ND | 0.896 | 1.53 | 1.84 | 5.22 | ND | ND | 2.65 | ND | 1.21 | ND | 1.55 | 0.598 | 2.36 | 1.71 | ND | ND | 1.48 | 0.857 | 2.63 | 1.03 | 10.9 | 7.68 | ND | 5.93 | 4.18 | 0.765 | 1.81 | 0.719 | ND | 2.61 | 4.29 | ND | 2.05 | ND | 1.09 | ND | 4.99 | 2.7 | 2.33 | 1.51 | 0.808 | 0.397 | 1.28 | 4.42 | 3.42 | 0.641 | 0.633 | 2.54 | 1.12 | ND | ND | 0.828 | 0.002 | 6.62 | 0.642 | 0.46 | ND | 1.95 | 0.636 | 2.89 | ND | ND | 0.157 | ND | ND | 0.029 | 2.54 | ND
A |  | L | 14.6 | 2.33 | 3.05 | ND | 0.873 | 0.001 | ND | 0.651 | ND | ND | 1.22 | ND | 2.65 | 11.7 | 3.73 | 2.11 | 0.765 | 1.14 | 0.69 | 0.555 | 0.841 | 1.33 | 3.99 | 1.18 | ND | 2.29 | 1.58 | ND | 3.58 | 3.2 | 2.27 | ND | 5.32 | 1.57 | 3.82 | 5.03 | 0.791 | ND | 15.7 | 6.28 | 1.69 | 10.7 | 7.5 | 1.18 | 1.36 | 7.85 | ND | 1.16 | 6.88 | 1.92 | 13.4 | 2.17 | 5.7 | 5.63 | ND | 2.45 | 2.19 | 13.3 | 10.6 | 0.576 | 2.81 | 0.674 | ND | 0.054 | ND | 2.1 | 0.176 | 0.683 | ND
| +13 FT 6 IN | C | ND | ND | 3.39 | 0.404 | 1.74 | ND | ND | 0.61 | 0.143 | 0.788 | 6.4 | 1.24 | 1.03 | 0.083 | 4.02 | 1.88 | 0.11 | 0.845 | 3.69 | 4.39 | ND | ND | 0.346 | ND | 4.47 | 7.82 | 5.29 | 1.4 | 1.24 | 10.9 | 2.34 | 2.9 | 5.73 | ND | 1.81 | 3.23 | 9.97 | 0.759 | 1.15 | 1.98 | 6.75 | ND | 0.798 | 6.21 | 2.36 | 1.49 | 7.63 | ND | 6.98 | 4.01 | ND | ND | 3.77 | 2.99 | 6.98 | 2.47 | ND | ND | 1.56 | 1.77 | ND | 1.28 | 3.32 | 4.24 | 0.176 | ND | 0.87 | 2.15 | ND
|  | R | 3 | 2.05 | 3.13 | 2.28 | 2.35 | ND | ND | 1.96 | ND | 0.658 | 1.73 | 0.327 | 2.14 | 2.47 | 2.45 | 2.03 | 1.75 | 4.29 | 2.64 | 2.36 | 3.4 | ND | 1.79 | 5.91 | 3.35 | 3.9 | 5.85 | 2.6 | 14.4 | 11.5 | 15.4 | 1.34 | 6.02 | 0.629 | 2.25 | 1.46 | 13.9 | 0.489 | 13.8 | 2.85 | 5.19 | ND | 17.3 | 5.33 | 12.5 | ND | ND | 8.9 | ND | ND | 6.03 | 0.114 | 3.17 | 1.21 | 2.15 | 3.54 | ND | 12.2 | 5.79 | 0.84 | 2.96 | ND | 2.29 | 6.1 | 0.688 | 1.51 | 5.08 | 5.6 | ND
A |  | L | 4.36 | 1.93 | 0.997 | ND | ND | 5.2 | ND | 1.73 | 4.14 | 6.76 | 3.85 | 1.45 | 1.31 | 3.63 | 2 | 2.11 | 7.94 | ND | 2.36 | 3.9 | 3.64 | 2.27 | 0.715 | 2.9 | 1.89 | 1.49 | 0.874 | 1.8 | 0.956 | 1.21 | 3.19 | ND | 5 | 0.616 | 0.368 | 0.881 | 1.6 | 5.26 | 8.16 | 3.13 | 8.41 | 6.91 | 5.93 | 9.65 | 3.31 | 5.24 | 0.486 | 4.64 | 9.49 | 4.09 | 11.6 | 2.94 | 5.91 | 8.56 | 2.81 | 3.53 | 1.68 | 0.96 | 4.44 | 7.98 | 2.49 | 2.01 | 0.246 | 4.58 | 5.91 | ND | ND | 1.27 | 1.66
| +12 FT | C | 3.23 | ND | 0.078 | ND | 0.792 | ND | 2.78 | 1.02 | 4.95 | 5.7 | 6.79 | 1.86 | 0.088 | ND | 2.43 | 3.44 | 1.21 | ND | ND | 1.63 | 2.39 | 1.22 | 9.73 | 6.64 | 0.079 | 2.8 | 5.59 | 1.29 | 0.736 | 2.65 | 14.4 | 5.31 | 3.97 | 1.64 | 2.12 | 2.87 | ND | 2.71 | 6.21 | 10.1 | 2.51 | ND | 4.92 | 3.24 | 7.62 | 1.57 | ND | 2.58 | 3.15 | 3.13 | 5.1 | 4.63 | 4.74 | 4.69 | 5.76 | 5.15 | 2.34 | 0.975 | 2.45 | 4.88 | ND | 4.08 | ND | 1.92 | 0.555 | ND | 3.88 | 0.94 | 5.18
|  | R | 17.1 | 0.86 | 2.77 | 1.69 | ND | 7.4 | 2.72 | ND | 3.8 | 5.97 | 8.59 | 0.767 | 3.83 | 0.828 | 1.01 | 0.565 | 4.29 | ND | 6.03 | 4.51 | 3.39 | 11.7 | 8.1 | ND | 7.15 | 9 | 3.24 | 9.56 | ND | 1.68 | 4.46 | 1.53 | 0.967 | 2.54 | 4.45 | ND | 4.61 | 2 | 1.14 | 12.2 | 1.27 | 9.13 | 3.4 | 0.35 | 0.251 | 0.334 | ND | 2.45 | 3.06 | 3.59 | 2.31 | 5.47 | 2.65 | 1.28 | 6.7 | 2.04 | 0.636 | 3.99 | 5.51 | 3.63 | 1.55 | 0.401 | 1.4 | 0.1 | 0.208 | 0.967 | 1.99 | 2.39 | ND
A | POSITION 'A' | L | ND | ND | 2.1 | 2.17 | 0.908 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.2 | 0.35 | 0.085 | 2.49 | ND
| OF THE | C | ND | 3.67 | 3.05 | 2.4 | 2.59 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.17 | 2.45 | 3.36 | 1.16 | ND
| OB PORTS | R | ND | 0.445 | 1.92 | 2.05 | 1.61 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.643 | 2.11 | 4.55 | 1.62 | ND
A | POSITION 'B' | L | ND | 2.83 | 2.16 | 1.32 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.44 | 1.71 | 3.26 | ND | ND
| OF THE | C | ND | 2.34 | 2.75 | 1.94 | 2.61 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.03 | 2.27 | 1.32 | 1.35 | ND
| OB PORTS | R | ND | 2.69 | 3.38 | 1.36 | 1.61 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.72 | 2.39 | 2.25 | 1.9 | ND
A | POSITION 'C' | L | ND | 1.38 | 0.862 | 1.98 | 2.37 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.86 | 1.76 | 2 | 2.88 | ND
| OF THE | C | ND | 0.67 | 1.91 | 1.9 | 1.43 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.2 | 1.24 | 0.366 | 3.51 | ND
| OB PORTS | R | ND | 1.76 | 1.01 | 3.84 | 1.22 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.61 | 0.54 | 1.71 | 2.8 | ND
A |  | L | 0.707 | 0.785 | ND | ND | 1.22 | 29.2 | ND | ND | 1.02 | ND | 1.02 | 0.639 | 4.85 | 7.52 | 2.19 | ND | ND | 3.19 | 0.028 | 2.65 | 0.949 | 4.36 | 7.18 | 2.16 | 7.87 | 2.59 | 1.56 | 0.494 | 1.01 | 3.33 | ND | 5.72 | ND | 1.71 | ND | 6.89 | 4.73 | 10.8 | 6.9 | 4.28 | 8.45 | 0.881 | ND | ND | 7.43 | 5.63 | ND | 2.47 | ND | 5.97 | 3.67 | 6.43 | 2.13 | 5.34 | 9.57 | ND | 0.243 | 1.17 | 1.84 | 0.894 | 2.46 | 2.55 | 1.55 | 1.28 | 1.26 | 2.64 | 3.08 | 2.89 | 5.75
| +10 FT 6 IN | C | 0.699 | 0.701 | ND | 0.333 | 1.65 | 33.6 | ND | 1.39 | 0.632 | ND | ND | ND | 5.7 | 0.28 | 1.85 | ND | 2.02 | ND | 4.77 | 3.58 | 2.23 | 7.25 | ND | ND | 4.65 | 2.78 | ND | 0.214 | 2.54 | 2.16 | ND | 1.55 | ND | ND | ND | ND | ND | 0.163 | 7.31 | 4.19 | ND | 14.8 | 3.89 | 6.84 | 3.85 | 6.92 | ND | 1.93 | 2.32 | 2.29 | 4.95 | 2.9 | ND | ND | 6.11 | ND | 1.66 | 5.04 | 0.191 | 4.64 | 2.29 | 0.169 | 2.16 | 1.28 | 1.94 | 2.49 | 3.96 | 2.53 | 7.01
|  | R | 4.89 | 1.82 | ND | 0.925 | ND | 42.5 | ND | 2.5 | ND | ND | ND | 3.34 | 2.47 | 0.095 | 2.66 | 5.31 | 1.55 | 3.88 | ND | 5.4 | 1.16 | 5.94 | ND | 2.16 | 1.45 | 1.47 | 17.7 | ND | 9 | ND | 0.676 | ND | 2.11 | ND | ND | ND | 4.48 | 6.51 | 4.71 | ND | 2.9 | 4.08 | 4.76 | 2.37 | 3.68 | 7.94 | 3.44 | 1.5 | 3.8 | 2.28 | 5.76 | 6.72 | 0.184 | 3.63 | 2.64 | 1.04 | ND | 5.03 | 6.05 | 0.022 | ND | 0.725 | 1.48 | 4.76 | 3.81 | 3.87 | 5.1 | ND | 20.3
A | POSITION 'A' | L | ND | ND | ND | 1.44 | 0.03 | ND | 3.65 | ND | ND | 0.797 | ND | 1.1 | 0.925 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.02 | 2.95 | 2.56 | 3.94 | 2.67 | 5.34 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE MANWAY | C | ND | ND | ND | 2.68 | 0.411 | ND | ND | ND | ND | 0.125 | ND | 5.11 | 0.759 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.61 | 4.83 | 0.456 | 4.47 | ND | 8.66 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| & OSCILLATOR | R | ND | ND | ND | 0.456 | 0.309 | ND | ND | ND | ND | 4.52 | ND | 3.29 | 0.499 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.061 | 2.65 | 2.09 | 4.16 | ND | 10.2 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION 'B' | L | ND | ND | ND | 1.59 | 1.7 | ND | ND | ND | ND | 0.608 | ND | ND | 1.6 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.75 | ND | 1.19 | 1.88 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE MANWAY | C | ND | ND | ND | 2.05 | 3.74 | ND | 3.16 | ND | ND | 4.92 | ND | 5.09 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.3 | 0.536 | ND | 1.33 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| & OSCILLATOR | R | ND | ND | ND | 1.63 | 2.31 | ND | 7.53 | ND | ND | ND | ND | 3.12 | 1.66 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.92 | 3.26 | 3.35 | 0.358 | 9.4 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION 'C' | L | ND | ND | ND | 3.71 | 1.07 | ND | ND | 0.456 | 2.85 | ND | ND | ND | 0.848 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.91 | 3.62 | ND | 0.349 | 4.91 | 1.1 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE MANWAY | C | ND | ND | ND | 2.48 | ND | ND | ND | ND | 0.967 | ND | ND | 2.58 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.095 | 0.565 | 1.68 | 0.546 | ND | 4.63 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| & OSCILLATOR | R | ND | ND | ND | 2.28 | 1.71 | ND | ND | 0.168 | ND | ND | ND | 1.91 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.22 | 1.5 | 3.59 | 0.971 | 3.83 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION 'D' | L | ND | ND | ND | 1.78 | 1.18 | ND | ND | 7.51 | 3.38 | 0.94 | ND | ND | 1.8 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.17 | 1.1 | 3.67 | ND | 7.85 | 12.2 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE MANWAY | C | ND | ND | ND | 0.165 | 1.87 | ND | ND | 10 | 2.9 | ND | ND | 0.358 | 4.92 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.4 | 1.47 | 0.95 | 5.28 | 15.3 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| & OSCILLATOR | R | ND | ND | ND | ND | 1.2 | ND | ND | 9.84 | 0.431 | ND | ND | 5.87 | 3.67 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.52 | 2.45 | 4.56 | 3.89 | 2.68 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION 'E' | L | ND | ND | ND | 0.949 | ND | 7.13 | ND | ND | ND | 0.246 | ND | 2.42 | 0.763 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.11 | 2.71 | ND | 1.75 | 4.52 | 10.1 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE MANWAY | C | ND | ND | ND | 1.91 | ND | 10.2 | 3.19 | 0.931 | ND | 2.68 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5.42 | 1.94 | 4.61 | 1.22 | 2.34 | 13.1 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| & OSCILLATOR | R | ND | ND | ND | 0.638 | 1.46 | 6.93 | 0.1 | ND | ND | 0.581 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.83 | 0.997 | 4.25 | 0.566 | 5.71 | 7.62 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A |  | L | ND | ND | ND | 2.17 | 4.04 | ND | ND | 1.63 | 1.85 | ND | ND | ND | 1.34 | 1.42 | ND | ND | ND | 3.4 | ND | 1.28 | 11.1 | 2.22 | 8.21 | 4.86 | ND | 6.27 | 3.53 | 11.7 | 2.57 | 8.69 | 3.34 | 4.05 | 4.81 | 0.819 | 1.86 | ND | 11.4 | 8.28 | ND | 1.67 | ND | 7.08 | ND | 0.464 | 3.53 | ND | 6.5 | 11.9 | 4.44 | 2.66 | ND | 4.35 | 0.274 | 3.26 | 4.83 | 5.71 | 5.18 | 4.77 | 2.71 | 2.72 | 4.44 | 1.74 | 0.991 | 0.953 | 1.24 | 3.78 | 3.7 | 2.79 | ND
| +9 FT | C | ND | 1.19 | 0.392 | 0.916 | 2.34 | 19.4 | ND | 6.48 | ND | ND | ND | ND | 3.62 | 5.58 | ND | 3.17 | ND | ND | 3.07 | ND | 4.56 | 2.36 | 4.3 | 11.1 | 4.27 | 10.4 | 1.76 | 5.91 | 7.99 | 5.72 | 6.33 | 3.82 | 5.25 | 1.4 | 1.95 | ND | 12.1 | 6.69 | ND | ND | 3.98 | ND | 4.85 | 4.85 | 6.75 | 0.37 | 6.22 | 4.2 | 0.772 | 4.7 | 2.48 | 8.04 | 3.21 | 6.45 | 4.8 | 6.7 | 4 | 4.79 | 1.19 | 0.972 | ND | ND | 1.03 | 2.55 | ND | ND | 2.92 | 5 | 15.9
|  | R | ND | ND | 1.84 | 0.102 | 3.71 | 20.3 | ND | 1.4 | 2.62 | ND | ND | 1.84 | ND | 3.17 | ND | ND | ND | ND | 1.45 | 3.85 | 6.64 | 3.65 | ND | 4.62 | ND | 8.04 | 1.69 | 8.34 | 6.58 | 6.19 | 5.24 | 2.65 | 4.4 | 0.879 | 0.283 | 0.584 | 7.03 | 10.2 | ND | 5.77 | 3.52 | 6.32 | 11.6 | ND | 7.55 | 5.06 | 10.5 | 1.48 | ND | ND | 0.369 | 6.97 | 1.5 | 7.47 | 3.56 | 2.04 | 3.4 | 7.13 | 2.3 | 1.44 | 10.4 | 6.24 | 0.926 | 3.82 | 6.55 | 1.54 | 3.38 | 2.06 | 19.4
A |  | L | 0.888 | 1.14 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.995 | 0.362 | 0.077 | 0.084 | ND | ND | ND | 3.26 | ND | 5.69 | 1.08 | 1.26 | ND | ND | 1.26 | 0.673 | ND | 1.27 | 0.068 | 8.21 | 11.6 | 13.5 | 8.53 | 10.2 | 2.53 | ND | ND | 8.64 | 0.5 | ND | 2.26 | 0.056 | 2.77 | ND | 0.978 | 1.61 | 0.005 | ND | 1.19 | 1.63 | 3.81 | ND | 5.59 | ND | 1.33 | 3.97 | 0.266 | 4.26 | 1.88 | ND | ND | 2.27 | ND | ND | 1.81 | ND | ND | 16.8
| +7 FT 6 IN | C | 0.232 | ND | 0.221 | 2.05 | 1.38 | ND | ND | ND | ND | ND | ND | 0.536 | 4.46 | 2.64 | 0.99 | 1.07 | 1.94 | ND | ND | 0.201 | 8.33 | 2.42 | 2.71 | 0.671 | 4.55 | ND | 3.95 | 1.86 | 8.14 | ND | 1.28 | 10.9 | 10.8 | 10.1 | 5.04 | 7.08 | ND | ND | 9.33 | 1.12 | 3.8 | 4.5 | 0.782 | ND | ND | ND | 2.35 | 3.37 | 0.785 | 1.26 | 3.2 | 0.122 | 1.1 | 1.87 | ND | 1.5 | 0.602 | 1.82 | 6.26 | 0.408 | 1.3 | 3.26 | 1.53 | 0.513 | ND | ND | ND | 0.974 | 18.6
|  | R | 0.091 | ND | ND | 3.08 | ND | ND | ND | ND | ND | ND | ND | 4.29 | 7.46 | ND | 0.484 | 2.28 | ND | ND | 2.05 | 3.5 | 3.84 | 2.07 | 3.32 | 2.06 | ND | 0.53 | ND | 4.58 | 6.86 | 8.36 | 1.63 | 9.82 | 7.86 | 6.17 | 8.78 | 6.71 | ND | 1.67 | 6.68 | 10.3 | 2.35 | 4 | 0.737 | ND | 3.7 | 1.2 | 2.11 | ND | ND | 0.046 | 1.84 | 1.97 | 2.22 | 1.92 | 3.73 | ND | 2.3 | ND | 4.1 | 3.35 | ND | ND | 1.92 | 0.151 | ND | 1.96 | 0.823 | 0.446 | 38
A |  | L | 1.13 | ND | ND | 1.67 | 0.141 | ND | ND | ND | ND | ND | 0.38 | ND | 2.34 | 9.52 | 5.59 | 7.03 | 7.82 | 9.06 | ND | 9.64 | 11.4 | 10.9 | 1.05 | 5.53 | ND | ND | 8.19 | ND | ND | 2.84 | ND | ND | 6.74 | ND | 2.67 | 3.4 | 1.03 | ND | 2.36 | ND | 3.02 | 4.18 | ND | ND | ND | ND | ND | ND | 3.35 | 0.937 | ND | ND | 5.74 | 1.55 | ND | 1.15 | 1.62 | ND | ND | 0.262 | ND | 7.34 | ND | 4.42 | ND | 0.802 | 0.444 | 2.04 | 2.54
| +6 FT | C | ND | 1.47 | ND | 0.08 | ND | ND | ND | ND | ND | ND | 0.858 | ND | 6.35 | 2.21 | 8.98 | 8.72 | 4.51 | 9.7 | 2.33 | 7.66 | 5.2 | 11.6 | 2.47 | 7.44 | ND | 4.08 | 7.89 | ND | ND | ND | ND | 1.83 | 5.59 | ND | 11.5 | 3.65 | ND | ND | 1.39 | 1.29 | 8.42 | 3.66 | 0.894 | ND | ND | ND | ND | ND | 6.63 | ND | ND | 3.12 | 2.12 | ND | 0.603 | ND | ND | 0.34 | ND | 1.03 | ND | 1.54 | ND | 6.02 | ND | 1.04 | 3.06 | 5.71 | ND
|  | R | ND | 1.11 | 1.67 | 0.191 | 0.098 | ND | ND | ND | ND | ND | ND | 1.89 | 3.87 | 9.02 | 6.98 | 4.84 | 8.84 | 11 | ND | 7.01 | 9.06 | 5.33 | 0.535 | 4.81 | ND | 0.152 | 1.67 | 7.67 | ND | 1.12 | 0.554 | ND | 1.15 | 3.49 | 8.05 | ND | ND | ND | 5.79 | 0.86 | 6.97 | 5.21 | 0.698 | 0.422 | ND | ND | ND | ND | 1.15 | 0.021 | ND | 2.46 | 3.51 | 3.83 | 0.035 | 1.49 | 2.06 | ND | 1.72 | 0.087 | ND | 5.44 | ND | 2.38 | ND | 1.1 | 1.23 | 1.17 | ND
A |  | L | 5.25 | 2.99 | 0.096 | 2.12 | 4.64 | 1.56 | 1.54 | 3.61 | 2.59 | ND | 2.46 | 4.82 | ND | 5.36 | 3.7 | 4.77 | 7.35 | 0.243 | 1.47 | 3.15 | ND | 4.11 | 2.78 | 1.53 | 2.31 | ND | ND | ND | 9.33 | 0.16 | ND | 0.544 | ND | 5.57 | 3.3 | ND | 2.84 | ND | ND | 1.54 | 1.13 | 1.88 | ND | 3.24 | 2.08 | 2.39 | ND | ND | ND | 0.826 | 0.313 | ND | ND | ND | 0.394 | ND | ND | 1.21 | 1.01 | 2.85 | 1.97 | 3.45 | ND | 9.69 | 4.16 | ND | 0.075 | 1.88 | 10.8
| +4 FT 6 IN | C | 4.09 | 2.63 | 2.01 | 5.86 | 3.25 | 0.947 | 3.33 | 4.86 | 5.88 | 1.91 | 4.72 | 5.03 | 4.4 | ND | ND | 0.367 | 4.68 | 7.42 | 0.15 | 5.96 | ND | 4.88 | 0.716 | 3.44 | ND | 5.06 | 1.17 | 1.58 | ND | 4.31 | 0.944 | ND | 0.361 | 2.49 | 1.62 | 1.18 | ND | 2.3 | ND | 0.841 | 0.73 | 6.69 | ND | ND | 0.538 | ND | 0.001 | 1.15 | ND | 2.64 | 1.31 | ND | 1.76 | 0.204 | ND | 1.88 | 2.05 | 0.717 | ND | ND | ND | ND | ND | 3.01 | ND | 0.222 | 0.178 | 1.8 | 3.42
|  | R | 8.9 | 2.39 | 6 | 2.63 | 2.4 | 2.47 | 3.09 | 0.964 | 3.09 | 1.18 | 3.06 | 1.11 | 7.15 | 2.73 | 5.17 | 4.65 | 2.57 | 8.2 | ND | 6.2 | ND | 1.08 | 4.7 | 5.74 | ND | ND | 2.32 | 0.794 | ND | 3.74 | 6.08 | 0.693 | 3.71 | 2.15 | ND | 3.55 | ND | ND | ND | 0.741 | 0.925 | 2.85 | 4.52 | 2.49 | ND | 1.26 | ND | 1.25 | ND | 1.13 | 1.83 | 1.82 | ND | 0.983 | ND | 1.54 | 0.393 | 0.982 | ND | 0.482 | ND | 1.83 | ND | 1.78 | 2.86 | 2.37 | 0.985 | 8.09 | ND
A |  | L | 2.85 | 2.32 | 0.944 | 2.08 | ND | 4.02 | 6.53 | ND | ND | ND | 4.32 | ND | 7.59 | ND | 0.641 | 7.25 | ND | 6.41 | 6.2 | ND | ND | ND | 0.369 | 1.44 | ND | 0.064 | 2.35 | 0.106 | ND | 5.58 | 8.92 | 7.26 | ND | 4.18 | 1.69 | ND | ND | ND | 0.01 | 0.95 | 1.38 | 8.22 | 3.28 | 2.65 | 2.74 | 0.585 | 3.01 | 1.78 | ND | 2.83 | ND | ND | 0.792 | 2.71 | ND | 0.736 | 1.25 | ND | ND | 2.01 | 2.47 | 2.74 | 3.75 | ND | ND | 5.19 | ND | ND | ND
| +3 FT | C | 3.19 | 2.9 | ND | 2.4 | ND | 1.71 | 2.58 | ND | ND | 1.5 | 0.591 | ND | ND | ND | 7.06 | 5.13 | 2.49 | 0.505 | ND | ND | ND | 7.82 | 3.48 | ND | 6.83 | 3.71 | ND | 0.263 | ND | 0.242 | 0.678 | 8.86 | ND | 0.818 | ND | 1.23 | ND | 2.07 | ND | ND | 3.28 | 4.66 | 1.26 | 1.08 | 2.02 | 2.83 | 2.19 | 1.74 | 0.309 | ND | 2.99 | 5.48 | 4.44 | 2.31 | 2.16 | 1.3 | 2.24 | 2.48 | ND | 0.835 | ND | ND | 0.968 | 3.32 | 0.764 | ND | 1 | 2.11 | 2.46
|  | R | 3.92 | 2.74 | 0.351 | 3.59 | 1.29 | 2.02 | ND | ND | ND | ND | 1.36 | 1.43 | ND | 2.37 | 8.55 | ND | ND | 4.45 | 2.42 | ND | ND | ND | 4.75 | 1.4 | 6.23 | ND | ND | 1.07 | ND | ND | 8.44 | ND | 3.96 | 4.42 | 0.185 | ND | ND | ND | 0.272 | ND | 0.562 | 3.12 | 1.77 | 2.06 | 0.613 | 2.88 | 0.358 | ND | 3.49 | ND | ND | ND | ND | 2.4 | 2.72 | ND | ND | 1.43 | 0.878 | 2.37 | ND | ND | ND | ND | 4.96 | ND | ND | 1.66 | 0.39
A |  | L | 19 | 4.75 | 1.99 | 8.27 | 1.13 | 2.26 | 2.87 | 1.5 | 4.41 | 0.293 | 1.66 | 1.26 | 2.76 | 1.65 | 3.32 | 1.79 | 7.24 | 3.64 | 3.98 | 3.65 | ND | 0.863 | 1.25 | 0.375 | 7.15 | ND | ND | 0.042 | 9.04 | 1.01 | 2.37 | 6.43 | 0.979 | 1.69 | 3.13 | ND | 4.44 | 4.81 | 4.06 | 2.79 | 2.44 | 1.44 | 2.46 | 2.33 | 3.6 | 3.09 | 3.11 | 4.19 | 2.09 | 2.02 | ND | 2.34 | 3.29 | ND | 0.194 | 1.32 | 2.44 | 2.32 | 0.688 | 3.42 | 1.79 | ND | ND | ND | ND | 1.84 | ND | ND | 1.77
| +1 FT 6 IN | C | 15.8 | 5.79 | 2.46 | 1.54 | ND | ND | 4.13 | 1.36 | ND | 2.44 | ND | 0.863 | 0.837 | ND | 2.21 | 3.26 | 2.61 | 3.26 | 2.22 | 4.54 | 1.72 | ND | 5.47 | 0.275 | ND | ND | ND | 0.815 | 9.49 | ND | 0.944 | 2.65 | 2.29 | 4.18 | 2.5 | 5.25 | 0.78 | ND | 2.23 | 5.01 | 8.26 | 3.61 | 4.22 | 4.46 | 4.89 | 5.04 | 4.91 | 2.04 | 2.86 | 0.938 | 4.14 | 2.82 | 1.76 | ND | 1.39 | 0.366 | 2 | 0.921 | 1.57 | 3.18 | 1.88 | ND | ND | ND | 1.76 | ND | ND | ND | ND
|  | R | 13.9 | 5.6 | 2.38 | 3.29 | 2.05 | 4.37 | 3.41 | 1.33 | 2.13 | 3.23 | ND | 0.126 | 4.92 | 2.11 | 0.98 | 0.502 | 4.67 | 3.16 | 1.14 | 1.28 | 4.38 | ND | ND | 1.43 | 0.284 | 1.67 | ND | 0.211 | 5.39 | ND | 2.64 | 1.37 | 6.73 | 4.8 | 2.83 | ND | 2.86 | ND | 2.33 | 1.04 | 1.47 | 4.2 | 2.03 | 3.89 | 2.64 | 5.89 | 3.62 | 0.971 | 8.02 | 2.52 | 4.76 | 2.72 | 3.22 | 3.18 | 0.617 | 2.45 | 1.24 | 0.836 | 0.919 | 0.33 | ND | 0.65 | 2.89 | ND | 0.749 | 5.71 | 0.78 | ND | 1.19
A |  | L | 0.096 | ND | 1.73 | 2.44 | 0.709 | 0.261 | ND | 0.394 | 1.35 | ND | ND | 0.394 | 2.6 | ND | 1.1 | 1.4 | 1.67 | ND | ND | ND | ND | ND | ND | 1.79 | ND | ND | 2.63 | 0.034 | ND | ND | 0.686 | 1.95 | ND | ND | ND | ND | 0.136 | 1.28 | ND | ND | ND | ND | 2.59 | ND | 1.83 | ND | 3.17 | ND | 1.49 | ND | ND | 2.72 | 0.986 | 3.56 | 2.72 | ND | ND | ND | ND | 1.77 | ND | ND | 0.956 | ND | 0.507 | ND | ND | ND | ND
| 0 REFERENCE | C | ND | ND | ND | ND | 3.91 | ND | ND | 4.15 | ND | ND | ND | ND | 2.84 | ND | 0.317 | ND | 0.151 | ND | ND | 1.7 | ND | ND | 1.5 | ND | ND | 0.183 | ND | 0.32 | ND | ND | 3.57 | 0.78 | 0.642 | ND | 4.26 | ND | 0.2 | ND | ND | ND | 0.63 | 1.74 | 1.48 | ND | 0.822 | ND | 0.829 | ND | 0.283 | 0.259 | ND | 4.99 | 3.47 | 3.68 | 3.03 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.288 | 1.57 | ND | ND
|  | R | ND | 2.16 | 2.78 | 0.779 | 3.86 | ND | ND | 1.26 | ND | ND | ND | ND | 0.509 | ND | 0.428 | 1 | ND | ND | ND | ND | ND | ND | 2.06 | 0.351 | ND | ND | 0.303 | ND | ND | ND | 1.29 | 1.74 | 1.89 | 4.81 | ND | ND | 2.71 | 5.26 | ND | ND | ND | ND | ND | ND | 3.37 | 3.3 | ND | ND | 0.819 | 0.403 | 0.219 | 4.8 | 2.43 | 2.68 | 5.69 | ND | ND | ND | ND | ND | ND | ND | 0.204 | ND | ND | ND | 1.41 | ND | ND
A | POSITION 'A' | L | ND | 0.858 | ND | 4.41 | 6.25 | ND | 2.26 | ND | ND | ND | 1.55 | 4.18 | ND | 4.69 | 1.49 | 2.74 | ND | ND | ND | 2.74 | 3.46 | 3.02 | 2.01 | 2.77 | ND | ND | ND | ND | ND | ND | ND | ND | 1.45 | 1.51 | 2.24 | ND | ND | 2.43 | 1.81 | 4.16 | 2.91 | 1.95 | ND | ND | 0.297 | 4.53 | 1.48 | 0.669 | 2.28 | 1.54 | ND | ND | ND | ND | ND | 8.08 | 0.681 | 1.63 | 4.19 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | 0.393 | ND | 4.67 | 6.67 | ND | 1.56 | ND | ND | ND | 1.92 | 3.69 | 1.37 | 0.621 | 0.493 | 1.27 | ND | ND | 0.555 | 1.25 | 4.06 | 2.39 | 5.13 | 3.68 | ND | ND | ND | ND | ND | ND | ND | ND | 3.35 | ND | 0.569 | ND | 1.17 | 1.21 | 1.15 | ND | 4.33 | 1.86 | ND | ND | 4.36 | 4.95 | 4.61 | 1.73 | 1.94 | 3.38 | ND | ND | ND | ND | 0.835 | 6.3 | 3.5 | 2.25 | 1.23 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| SECONDARIES | R | ND | 0.022 | ND | 4.63 | 3.33 | 2.49 | 1.89 | ND | ND | ND | 4.04 | 2.07 | 4.15 | 0.105 | 3.76 | ND | ND | ND | ND | ND | 2.72 | 1.91 | 0.728 | 3.14 | ND | ND | ND | ND | ND | ND | ND | 0.677 | 6.78 | ND | ND | ND | 1 | 3.56 | 1.87 | 1.84 | 3.26 | ND | ND | ND | 3.99 | 2.86 | 4.93 | 3.06 | 1.31 | 0.784 | ND | ND | ND | ND | ND | 7.57 | ND | 0.685 | 3.92 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION 'B' | L | ND | ND | 1.73 | 1.86 | 1.78 | 2.55 | 3.02 | ND | ND | ND | 0.646 | 4.5 | ND | 1.26 | 1.15 | 3.01 | ND | ND | 0.411 | 1.67 | 1.02 | 1.67 | ND | 2.86 | ND | ND | ND | ND | ND | ND | ND | 1.04 | 2.24 | 0.548 | 2.59 | ND | ND | 1.7 | 3.58 | 3.09 | ND | ND | ND | ND | 0.959 | 1.2 | 1.04 | 3.77 | 4.67 | 1.52 | ND | ND | ND | 2.55 | 1.18 | 4.73 | 1.69 | ND | 4.83 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | 2.89 | 2.77 | 2.12 | 1.58 | 4.56 | 4.25 | ND | ND | ND | 0.57 | 2.84 | 4.03 | 3.27 | 3.58 | 2.1 | ND | ND | 2.7 | 1.14 | 1.07 | 3.44 | 0.759 | 3.74 | ND | ND | ND | ND | ND | ND | ND | 3.94 | 3.93 | ND | 2.37 | ND | ND | 0.917 | 3.98 | 1.56 | ND | ND | ND | ND | 1.28 | 4.5 | 1.46 | 2.87 | 2.89 | 7.55 | ND | ND | ND | ND | 2.84 | 1.17 | 2.96 | 2.84 | 4.26 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| SECONDARIES | R | ND | 3.29 | 2.66 | 1.65 | 0.037 | 3.85 | 1.81 | ND | ND | ND | 2.08 | 0.91 | 4.36 | 3.4 | 2.66 | 0.055 | ND | ND | ND | 0.678 | 1.27 | 1.47 | 2.06 | 3.89 | ND | ND | ND | ND | ND | ND | ND | 3.33 | 1.38 | 0.546 | 0.865 | ND | 0.754 | 1.26 | 3.11 | 1.23 | 2.01 | ND | ND | ND | ND | 0.748 | 3.34 | 1.11 | 2.19 | 1.99 | ND | ND | ND | ND | ND | 2.21 | 2.81 | 2.85 | 0.979 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A |  | L | ND | 0.021 | 2.93 | 1.91 | 9.97 | ND | ND | ND | ND | ND | ND | ND | 2.45 | ND | ND | 0.44 | ND | ND | ND | ND | 1.64 | 3.89 | ND | ND | ND | ND | 0.407 | 1.15 | 0.899 | ND | ND | ND | ND | ND | ND | ND | 2.6 | 3.45 | 4.52 | 5.17 | 3.05 | 2.94 | ND | 3.52 | 0.602 | 0.976 | ND | ND | ND | 0.49 | 1.19 | 0.043 | 3.63 | ND | 2.44 | 8.34 | 2.5 | 1.36 | 0.526 | ND | 1.07 | ND | 3.98 | 0.921 | 0.464 | ND | ND | 3.73 | ND
| -9 IN | C | 0.78 | 0.166 | ND | ND | 9.62 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.868 | 1.75 | 3.05 | 3.52 | ND | 0.174 | ND | 0.52 | ND | ND | ND | ND | 0.686 | 2.73 | 0.075 | 10.5 | ND | ND | ND | 4.85 | ND | 3.48 | ND | 2.18 | 2.2 | 3.75 | ND | 1.94 | 0.08 | 0.804 | 0.484 | 1.38 | ND | ND | 0.119 | 4.73 | 2.71 | 3.2 | 5.71 | ND | 0.938 | ND | ND | ND | 0.635 | ND | 6.41 | 0.842 | ND | 4.45 | ND
|  | R | 2.91 | 0.731 | ND | 2.8 | 9.49 | ND | ND | ND | 0.568 | ND | 1.58 | ND | 0.498 | ND | ND | ND | ND | ND | 1.54 | 0.608 | 4.39 | ND | ND | ND | ND | ND | 0.332 | ND | 1.43 | ND | 1.33 | ND | ND | ND | ND | ND | 2.41 | ND | 2.56 | ND | ND | ND | ND | 0.86 | 0.284 | 1.08 | 1.1 | ND | ND | ND | 0.134 | ND | 0.306 | 6.4 | 1.59 | 1.4 | 5.42 | ND | ND | ND | ND | ND | ND | 5.86 | ND | 0.47 | ND | 10.2 | ND
A | POSITION 'C' | L | ND | ND | ND | ND | 6.11 | 5.18 | 1.53 | ND | ND | ND | 2.11 | 0.202 | ND | ND | 0.755 | 0.719 | ND | ND | ND | 0.596 | 8.19 | 6.17 | 0.905 | 1.37 | ND | ND | ND | ND | ND | ND | ND | 1.48 | ND | 1.87 | ND | ND | 0.071 | ND | 5.57 | 2.76 | 2.47 | ND | ND | ND | 0.027 | 3.77 | 1.62 | 3.76 | 6.19 | 0.215 | ND | ND | ND | ND | ND | 5.94 | 2.29 | 1.1 | 2.15 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | 4.05 | ND | 1.28 | 8.63 | 5.07 | 5.03 | ND | ND | ND | 1.78 | 2.23 | 2.89 | 4.1 | 1.07 | 0.313 | ND | ND | 0.152 | 3.68 | 5.44 | 5.39 | ND | 1.75 | ND | ND | ND | ND | ND | ND | ND | ND | 5.63 | 2.49 | ND | ND | ND | 1.38 | 3.75 | 10.4 | 3.06 | 1.77 | ND | ND | 4.7 | 3.33 | 7.05 | 3.5 | 3.76 | 1.5 | ND | ND | ND | ND | ND | 4.12 | 7.76 | 4.05 | 4.47 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| SECONDARIES | R | ND | 2.52 | ND | 0.538 | 5.47 | 8.21 | 2.02 | ND | ND | ND | ND | 2.34 | 4.22 | 6.53 | 0.844 | 0.292 | ND | ND | ND | 4.13 | 7.79 | 4.69 | 1.27 | 4.3 | ND | ND | ND | ND | ND | ND | ND | 0.492 | 1.73 | ND | 0.223 | ND | ND | 1.55 | 4.11 | 2.55 | 2 | ND | ND | ND | 1.92 | 3.42 | 2.31 | 3.49 | 4.19 | 0.478 | ND | ND | ND | 2.07 | 4.36 | 8.28 | 10.7 | 1.46 | 4.29 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A |  | L | 1.26 | 4.01 | ND | ND | ND | ND | ND | ND | 0.717 | 2.79 | 0.899 | 0.736 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.062 | 0.397 | ND | 1 | 0.221 | 0.198 | ND | ND | ND | ND | 1.54 | 0.242 | 0.481 | ND | ND | 0.516 | ND | 1.18 | 1.88 | 2.31 | ND | 0.6 | ND | 1.61 | 0.724 | ND | ND | ND | ND | 0.098 | ND | ND | ND | ND | ND | 0.548 | ND | ND | ND | 8.01 | 2.31 | ND | 9.62 | 2.58 | 10.9 | ND
| -18 IN | C | 0.827 | 0.471 | 1.38 | ND | 1.32 | ND | ND | ND | ND | 0.419 | 0.576 | 1.54 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.59 | 0.217 | ND | ND | ND | ND | ND | 0.825 | ND | 1.09 | 0.461 | ND | 0.259 | ND | 1.72 | ND | 0.321 | 1.64 | 2.58 | ND | ND | ND | ND | 1.16 | ND | ND | ND | 1.9 | ND | 4.05 | ND | ND | ND | ND | ND | ND | ND | 0.287 | ND | ND | 5.05 | 1.29 | ND | 0.489 | 2.85 | ND
|  | R | 2.68 | ND | 0.415 | ND | ND | ND | ND | ND | 0.132 | 2.02 | 1.75 | ND | 0.545 | ND | ND | 0.152 | ND | ND | ND | ND | ND | ND | ND | ND | 1.06 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.543 | ND | ND | 1.39 | 0.925 | 1.59 | 1.18 | ND | 1.92 | ND | 3.12 | 9.28 | 3.29 | 0.495 | 1.15 | 0.522 | 0.795 | 4.63 | ND | ND | ND | ND | ND | ND | ND | 0.533 | ND | ND | 0.798 | ND | ND | ND | ND | ND | 1.28
A |  | L | 1.22 | ND | ND | ND | 1.37 | 0.913 | 0.049 | 1.11 | 1.24 | 5.51 | 1.11 | 1.92 | ND | ND | 6.54 | ND | ND | 0.693 | 1.03 | 2.05 | 2.56 | 0.51 | 0.056 | 1.22 | 2.16 | 9.05 | 1.15 | 0.945 | 0.161 | 0.778 | 1.79 | 2.77 | 1.28 | ND | 0.539 | 3.63 | 2.93 | 2.42 | ND | 1.67 | ND | ND | ND | 0.348 | ND | 0.556 | 0.884 | 0.669 | ND | 1.75 | 1.29 | 0.804 | 0.702 | 1.89 | ND | ND | ND | ND | 3.35 | ND | 1.81 | 3.31 | 1.22 | 2.19 | ND | ND | ND | 0.592 | 7.08
| -27 IN | C | 2.91 | 1.01 | ND | ND | ND | 1.79 | ND | ND | ND | ND | 3.72 | 0.878 | ND | 0.882 | ND | 0.671 | 0.878 | ND | ND | 0.777 | 0.788 | 0.358 | ND | 0.141 | 0.217 | 1.14 | 2.62 | 1.34 | 1.24 | ND | 0.819 | 2.11 | ND | 1.38 | 1.18 | 1.91 | 1.46 | ND | ND | ND | ND | 2.08 | ND | ND | ND | ND | 12.2 | ND | ND | 0.779 | ND | 1.14 | 0.114 | 1.32 | ND | 0.466 | 0.945 | 0.267 | ND | 1.61 | ND | 1.13 | 1.39 | ND | ND | 3.17 | 0.366 | 1.14 | 3.59
|  | R | ND | 0.339 | ND | 0.422 | ND | 1.46 | 1.03 | 1.53 | 1.31 | ND | 2.27 | ND | ND | ND | 1.83 | ND | 0.364 | 1.22 | 0.713 | ND | ND | 3.01 | 3.68 | 1.25 | ND | 0.084 | 2.42 | 1.86 | 2.5 | ND | 1.43 | 1.71 | 1.51 | ND | ND | ND | 1.67 | 0.086 | ND | 1.51 | 1.74 | ND | ND | ND | ND | ND | ND | ND | 2.25 | 2.1 | 0.533 | 0.692 | 0.1 | 0.184 | ND | ND | 1.83 | 1.75 | 1.12 | ND | 1.29 | 0.502 | ND | ND | ND | ND | 4.21 | ND | ND
A |  | L | ND | 4.7 | 7.18 | ND | 1.33 | 2.05 | 0.228 | ND | 0.14 | ND | 0.058 | ND | ND | ND | 1.46 | ND | ND | 1.84 | 0.536 | 0.576 | 3.2 | 0.871 | 0.597 | ND | 0.652 | 1.98 | ND | ND | 1.27 | 1.71 | 3.52 | 1.57 | 2.09 | ND | ND | 1.99 | 1.55 | 0.862 | 1.73 | 0.679 | ND | ND | ND | ND | ND | ND | 0.689 | ND | 0.319 | 7.89 | 0.354 | ND | ND | 0.394 | 0.818 | 2.43 | 0.223 | 0.115 | 0.054 | ND | 0.081 | 2.58 | 1.8 | 0.369 | ND | 0.407 | ND | ND | ND
| -36 IN | C | 3.96 | 6.26 | ND | ND | 0.817 | 0.943 | ND | 1.37 | 0.241 | 1.26 | ND | ND | ND | 1.15 | 1.33 | ND | ND | 0.234 | ND | 1.68 | ND | ND | ND | ND | 0.16 | 0.767 | ND | ND | ND | 1.44 | 2 | 2.05 | ND | ND | 1.15 | ND | ND | ND | ND | ND | 1.67 | 1.52 | ND | ND | ND | ND | 0.443 | ND | ND | ND | ND | ND | 0.44 | 1.67 | ND | 2.47 | ND | ND | ND | ND | ND | 1.19 | 0.737 | ND | 0.329 | 0.271 | ND | 4.79 | 0.55
|  | R | ND | 1.62 | 0.067 | 1.72 | 1.59 | ND | 0.846 | 0.967 | 0.365 | 0.521 | 0.523 | ND | ND | 1.95 | ND | 1.15 | 0.978 | 1.62 | ND | 0.309 | ND | 3.66 | ND | 0.449 | 1.76 | 0.97 | 1.3 | 0.148 | ND | 2.58 | 0.561 | 1.25 | ND | 1.16 | ND | 1.52 | ND | ND | 1.86 | 0.606 | 1.49 | ND | 0.955 | ND | ND | ND | 0.313 | 0.165 | ND | 1.61 | 1.33 | 1.44 | 1.54 | 5 | 2.14 | 4.33 | 1.3 | ND | 0.653 | ND | ND | ND | 1.58 | ND | 0.107 | 4.46 | 1.46 | ND | 6.91
A |  | L | 1.95 | ND | ND | ND | ND | 2.95 | ND | 4.51 | ND | 0.615 | 1.51 | ND | 0.425 | 0.223 | 2.33 | 1.54 | 0.642 | 2.56 | 4.18 | 0.835 | 0.83 | ND | ND | ND | 0.618 | 0.865 | 0.967 | ND | 0.352 | ND | 1.97 | 0.168 | 5.4 | 2.11 | ND | 0.02 | 1.79 | 0.851 | 2.03 | ND | 3.06 | 0.144 | ND | ND | 0.359 | ND | 1.65 | ND | 1.57 | ND | ND | ND | 1.63 | 1.01 | ND | 2.05 | ND | 0.019 | 2.66 | ND | 1.81 | ND | 2.96 | ND | ND | 1.06 | 0.839 | ND | ND
| -45 IN | C | 13 | 0.101 | 6.2 | ND | ND | ND | ND | ND | 4.29 | ND | 0.262 | 0.201 | 1.12 | 1.42 | ND | 0.682 | 0.819 | ND | ND | ND | 0.778 | ND | 2.95 | 2.33 | ND | 0.042 | ND | ND | 0.036 | 0.68 | 3.08 | 1.51 | ND | 0.885 | 0.566 | 0.411 | 0.105 | 1.22 | ND | ND | 0.255 | ND | ND | ND | 3.16 | ND | ND | ND | 1.95 | ND | ND | 0.35 | 1.24 | 1.34 | 2.01 | 0.583 | 0.119 | ND | ND | 0.463 | ND | ND | 1.1 | ND | 2.6 | 4.73 | ND | 0.709 | 1.55
|  | R | ND | ND | 6.37 | ND | ND | 4.68 | 0.17 | 2.05 | 3.89 | 4.36 | 0.39 | ND | 0.355 | 0.394 | 0.851 | ND | ND | ND | 0.608 | 1.84 | 0.06 | 0.086 | ND | 1.31 | 1.22 | ND | 0.959 | 2.1 | ND | ND | 0.134 | ND | 0.519 | ND | 0.576 | 6.16 | 0.441 | 0.254 | ND | ND | ND | 0.949 | ND | ND | 3.99 | 2.03 | 0.192 | 1.95 | 1.57 | ND | 0.576 | 1.12 | 1.19 | ND | 3.14 | 2.42 | ND | 0.296 | ND | ND | ND | 4.56 | 2.39 | 0.282 | 1.88 | 5.1 | 1.57 | 0.041 | 1.89
A |  | L | ND | 1.06 | ND | ND | ND | 4.3 | ND | 0.954 | 0.25 | ND | 0.185 | 2.08 | ND | 2.4 | 0.626 | ND | 0.975 | 0.744 | ND | 0.559 | ND | ND | 1.2 | ND | 2.61 | ND | 2.83 | 0.369 | 0.096 | ND | 1.64 | 5.9 | ND | 1.01 | 1.4 | 2.59 | ND | ND | 0.841 | ND | ND | ND | ND | 0.357 | ND | ND | ND | ND | ND | ND | ND | 1.04 | 2.54 | 3.17 | ND | 1.58 | 0.194 | 0.232 | 0.942 | 2.28 | 1.83 | 4.68 | 2.49 | 2.19 | 6.04 | 3.27 | 2.85 | 4.44 | ND
| -54 IN | C | ND | ND | ND | ND | ND | 2.35 | ND | 1.49 | 2.41 | ND | ND | ND | ND | ND | ND | 0.117 | ND | 1.3 | 0.783 | ND | ND | ND | 0.616 | ND | ND | ND | 0.27 | ND | 0.513 | ND | 0.261 | 5.94 | ND | ND | ND | ND | ND | ND | ND | 0.02 | 1.51 | 0.106 | ND | ND | ND | 1.77 | 3.55 | 0.92 | ND | ND | 0.115 | ND | 1.67 | 0.771 | 0.423 | ND | 4.02 | ND | ND | 1.38 | 4.98 | 4.64 | 0.371 | 0.105 | 4.19 | 6.5 | 4.66 | 3.43 | 1.14
|  | R | ND | ND | ND | 0.338 | ND | ND | 0.604 | 2.63 | 2.46 | 0.189 | 1.41 | ND | 0.247 | 0.45 | ND | ND | 0.066 | 0.529 | ND | 0.255 | 0.802 | 1.02 | 0.244 | 1.49 | ND | ND | 0.411 | ND | ND | 3.08 | ND | 2.88 | 0.518 | ND | ND | ND | ND | ND | 1.15 | 1.31 | 0.94 | ND | ND | 1.63 | 0.575 | 1.08 | 4.33 | 4.96 | ND | 3.31 | 0.864 | ND | 2.85 | 0.533 | 1.42 | 3.83 | 1.54 | ND | 3.63 | 1.61 | 3.73 | 2.99 | 3 | 4.29 | 8 | 4.48 | 2.98 | 1.8 | 2.45
A | POSITION 'A' | L | ND | ND | ND | 2.55 | ND | 3.47 | ND | ND | 1.34 | 1.66 | ND | ND | 1.55 | ND | 0.882 | 2.27 | ND | 0.082 | 2.49 | ND | 2.6 | 2.91 | ND | 2.35 | 3.19 | ND | 3.9 | 2.33 | ND | 0.311 | 2.82 | ND | 2.47 | 3.01 | ND | 2.26 | 4.33 | ND | ND | 3.1 | ND | 0.201 | 1.44 | ND | ND | 1.51 | ND | 2.92 | 3.58 | ND | ND | 1.99 | ND | ND | 3.84 | ND | ND | 0.984 | ND | 2.32 | 1.73 | ND | 0.509 | 0.873 | ND | 0.247 | 0.92 | ND | ND
| OF THE | C | ND | ND | ND | 2.67 | ND | 2.34 | 2.12 | ND | 2.21 | ND | ND | 2.34 | 1.46 | ND | 0.252 | 2.5 | ND | 2 | 2.17 | ND | 4.08 | 2.25 | ND | 3.2 | 1.32 | ND | 3.22 | 3.54 | ND | 0.983 | 1.78 | ND | 2.7 | 3.51 | ND | 0.862 | 1.14 | ND | 0.266 | 2 | ND | 0.718 | 2.78 | ND | 0.43 | 0.881 | ND | 1.3 | 2.16 | ND | 2.44 | 2.67 | ND | ND | 1.17 | ND | 0.662 | 0.591 | ND | 2.97 | 2.6 | ND | 1.7 | 0.32 | ND | 0.73 | ND | ND | ND
| PRIMARIES | R | ND | ND | ND | 0.767 | ND | 1.87 | 4.36 | ND | 5.57 | 1.08 | ND | 3.85 | 2.09 | ND | 2.32 | 1.99 | ND | 1.26 | ND | ND | 3.94 | 2.22 | ND | 3.8 | 1.72 | ND | 3.36 | 2.28 | ND | ND | 2.31 | ND | 5.48 | 1.91 | ND | 3.19 | 3.39 | ND | ND | 3.59 | ND | 3.68 | 2.62 | ND | 1.2 | 2.91 | ND | 2.73 | ND | ND | 1.44 | 2.61 | ND | 0.944 | 0.46 | ND | 0.702 | 1.64 | ND | 1.08 | 1.46 | ND | ND | 0.854 | ND | 1.94 | ND | ND | ND
A | POSITION 'B' | L | ND | ND | 1.62 | 5.34 | ND | 2.58 | 3.16 | ND | 3.63 | 2.34 | ND | 1.95 | 2.3 | ND | 0.916 | 2.77 | ND | 2.97 | 1.41 | ND | 4.12 | 1.48 | ND | 2.89 | 3.71 | ND | 4.2 | 5.56 | ND | 1.77 | 4 | ND | 2.15 | 2.9 | ND | 3.18 | 3.33 | ND | 3.04 | 3.14 | ND | ND | 3.02 | ND | 1.02 | 2.3 | ND | 2.11 | 3.21 | ND | 0.353 | 3.06 | ND | 4.97 | 1.13 | ND | 2.45 | 2.18 | ND | 2.23 | 3.23 | ND | ND | 2.46 | ND | 1.43 | 1.42 | ND | ND
| OF THE | C | ND | ND | 2.85 | 4.06 | ND | 2.76 | 2.93 | ND | 4.64 | 4.76 | ND | 1.15 | 4.32 | ND | 1.79 | 2.78 | ND | 2.17 | ND | ND | 3.61 | 1.1 | ND | 0.637 | 2.91 | ND | 4.93 | 1.5 | ND | 1.84 | 2.45 | ND | 1.67 | 1.67 | ND | 3.81 | 2.89 | ND | 2.71 | 3.11 | ND | 1.89 | 1.89 | ND | 0.306 | 1.73 | ND | ND | 3.98 | ND | 1.8 | 0.345 | ND | 5.26 | 2.86 | ND | 3.83 | 2.27 | ND | 1.76 | 3.3 | ND | ND | ND | ND | 3.29 | 3.25 | ND | ND
| PRIMARIES | R | ND | ND | 4.57 | 1.26 | ND | 3.5 | 3.39 | ND | 2.81 | 1.13 | ND | 1.88 | 1.94 | ND | 0.943 | 3.39 | ND | 3.05 | 0.709 | ND | 3.13 | 2.17 | ND | 5.11 | 4.37 | ND | 3.01 | 2.74 | ND | 1.71 | 2.04 | ND | 2.26 | 0.812 | ND | 1.95 | 5.4 | ND | 4.94 | 1.09 | ND | 2.99 | 3.68 | ND | 0.549 | 2.36 | ND | 1.45 | 1.14 | ND | 1.39 | 2.09 | ND | 3.88 | 1.82 | ND | 2.18 | 2.85 | ND | 2.74 | 2.26 | ND | 2.37 | ND | ND | 2.59 | 2.13 | ND | ND
A | POSITION 'C' | L | ND | ND | 8.66 | 2.03 | ND | 6.03 | 3.3 | ND | 3.3 | 3.15 | ND | ND | 2.82 | ND | 4.73 | 2.55 | ND | 3.53 | 3.72 | ND | 2.43 | 3.25 | ND | 5.21 | 2.29 | ND | 5.03 | 2.45 | ND | 4.06 | 1.47 | ND | 2.99 | 2.78 | ND | 3.4 | 5.66 | ND | 2.67 | 3 | ND | 0.151 | 3.42 | ND | 4.47 | 0.86 | ND | ND | 2.95 | ND | 1.25 | 3.8 | ND | 5.52 | 3.12 | ND | 3.06 | 3.24 | ND | 2.21 | 3.44 | ND | 1.8 | 1.32 | ND | 1.31 | 1.05 | ND | ND
| OF THE | C | ND | ND | 9.64 | 6.64 | ND | 4.57 | 8.24 | ND | 6.16 | 1.76 | ND | 3.7 | 3.19 | ND | 3.57 | 4.41 | ND | 3.62 | 4.27 | ND | 3.65 | 1.51 | ND | 4.74 | 3.9 | ND | 2.99 | 2.71 | ND | 6.2 | 3.2 | ND | 5.81 | 2.66 | ND | 5.57 | 4.49 | ND | 3.23 | 4.52 | ND | 2.67 | 3.36 | ND | 6.45 | 2.92 | ND | 1.79 | 4.83 | ND | 0.726 | 2.3 | ND | 4.29 | 2.92 | ND | 6.23 | 4.33 | ND | 4.23 | 3.16 | ND | 4.95 | 0.313 | ND | 1.56 | 3.1 | ND | ND
| PRIMARIES | R | ND | ND | 6.86 | 1.85 | ND | 2.57 | 5.04 | ND | 5.44 | ND | ND | 4.4 | 0.662 | ND | 2.65 | 3.14 | ND | 3.67 | 2.88 | ND | 2.87 | 3.31 | ND | 5.44 | 2.23 | ND | 3.37 | 3.32 | ND | 3.93 | 3.49 | ND | 5.82 | 0.405 | ND | 4.63 | 5.29 | ND | 4.88 | 3.3 | ND | 3.1 | 3.26 | ND | 5.17 | 3.69 | ND | 5.56 | 3.2 | ND | 2.24 | 3.04 | ND | 6.94 | 1.17 | ND | 5.36 | 5.38 | ND | 3.7 | 3.93 | ND | 2.02 | ND | ND | 1.17 | ND | ND | ND
A |  | L | ND | 1.58 | ND | 1.93 | 3.83 | 1.85 | 1.39 | 5.26 | ND | 2.99 | 0.714 | 1.15 | 1.87 | ND | 3.39 | 3.57 | 0.543 | ND | ND | 2.8 | 0.906 | 0.665 | 0.661 | 2.2 | 1.18 | 3.9 | 0.234 | ND | ND | ND | 3.03 | 0.414 | ND | ND | 1 | 0.485 | 0.155 | 2.77 | ND | ND | ND | ND | ND | 1.07 | ND | 0.793 | 1.68 | 4.08 | 2.99 | 8.16 | 2.26 | 1.07 | ND | 9.81 | ND | ND | 0.156 | 0.921 | 0.998 | 2.94 | 0.848 | ND | 0.523 | 1.82 | ND | 4.83 | ND | 3.13 | ND
| -63 IN | C | ND | ND | 1.12 | 3.2 | 2.8 | 1.61 | ND | 1.76 | 1.12 | 2.79 | ND | 2.74 | 1.25 | 0.495 | 0.841 | ND | 2.21 | 1.42 | ND | 2.01 | 0.473 | 11.2 | ND | ND | ND | ND | 0.466 | 1.6 | 6.56 | ND | 0.986 | ND | 0.186 | 1.31 | ND | 4.99 | 1.62 | 4.04 | 2.4 | ND | 4.19 | ND | 0.883 | 0.472 | 3.4 | 0.328 | ND | ND | 1.19 | 0.054 | 0.894 | 3.21 | 1.32 | 1.43 | ND | 1.39 | 2.33 | 0.075 | 0.396 | ND | 0.78 | ND | 4.7 | 3.81 | ND | 3.64 | 0.946 | 2.88 | 4.02
|  | R | 3.24 | 6.06 | 3.96 | 1.05 | 3.3 | 9.95 | ND | 3.94 | 2.1 | ND | 3.85 | 3.83 | 1.15 | 2.01 | 2.77 | 0.375 | 4.68 | 2.42 | ND | 4.41 | 1.06 | 2.1 | ND | ND | 1.05 | 0.464 | ND | 2.72 | ND | 1.11 | 1.65 | 0.024 | 1.55 | 0.112 | 2.42 | 2.91 | 6.19 | ND | 1.46 | 3.83 | 4.95 | 0.366 | 3.84 | 2.02 | 1.9 | 3.47 | 0.299 | 1.54 | 0.131 | 3.11 | 0.919 | 1.53 | 3.58 | ND | 3.08 | ND | 2.55 | 3.16 | 0.405 | 1.47 | 2.89 | 3.61 | 3.88 | 4.9 | 1.9 | 3.13 | 6.25 | 3.78 | 0.699
A |  | L | ND | 3.04 | 0.742 | ND | 3.78 | 3.33 | 1.03 | 1.3 | 2.25 | ND | 4.51 | 5.59 | 1.18 | ND | 4.01 | 6.46 | 11.7 | 1.61 | 2.15 | 5.79 | 1.6 | 1.38 | 5.99 | 2.87 | 4.48 | 5.4 | 5.1 | 3.46 | 2.95 | ND | 1.08 | ND | 1.51 | ND | 4.8 | 5.09 | 0.292 | 1.88 | 2.28 | 1.08 | 4.61 | ND | 12.8 | ND | 4.23 | ND | 0.958 | 2.29 | 4.8 | ND | 0.484 | 1.95 | ND | 1.65 | 0.56 | ND | ND | 2.69 | ND | ND | 3.71 | 2.95 | ND | 4.17 | 1.48 | 2.18 | 2.06 | 1.51 | 5.9
| -72 IN | C | 1.1 | 3.86 | 1.92 | 3.53 | 0.184 | 0.287 | 4.22 | 2.88 | 0.388 | 4.62 | 1.07 | 6.86 | 1.4 | 4.44 | 3.44 | 2.88 | 3.92 | ND | 1.21 | 4.97 | 4.88 | 1.61 | 2.31 | 0.538 | 4.61 | 0.272 | 4.32 | 3.25 | 10 | 0.069 | 1.76 | 4 | 3.39 | 3.41 | 2.53 | 2.42 | ND | ND | ND | ND | 3.72 | 2.22 | 3.88 | 0.802 | 1.12 | 0.118 | 1.11 | ND | 2.42 | 0.784 | 0.445 | 0.624 | 0.76 | 1.5 | 1.16 | ND | ND | 1.5 | ND | ND | 3.61 | 6.92 | ND | 1.37 | ND | ND | 2.86 | 6.7 | 3.26
|  | R | ND | 1.79 | 2.18 | 2.05 | 2.6 | 2.76 | 3.91 | 1.48 | 0.725 | 2.36 | 2.08 | 1.66 | 10.2 | 2.61 | 5.23 | 5.34 | 9.05 | 2.42 | 2.46 | 3.85 | 3.37 | ND | 8.56 | 1.55 | 3.84 | 15.3 | 4.08 | 1.74 | 8.3 | 1.11 | 4.11 | 3.74 | 3.65 | ND | 5.17 | 2.48 | 2.25 | 1.6 | 5.48 | ND | 2.35 | 2.74 | 3.25 | ND | 1.2 | ND | 0.68 | ND | 2.31 | 0.101 | 2.01 | 0.777 | ND | 0.988 | ND | ND | ND | 5.73 | ND | 1.07 | 10.9 | 3.01 | 1.15 | 1.48 | 8.31 | 1.69 | 0.417 | 3.72 | 3.55
A |  | L | 11.7 | 2.36 | 12.5 | 2.78 | 6.49 | 2.51 | 7.58 | 3.91 | 9.58 | 2.91 | 2.28 | 4.46 | 4.97 | 1.77 | 0.264 | 2.18 | 1.95 | 8.74 | 3.53 | 1.9 | 5.82 | 0.133 | 1.57 | 2.42 | 3.97 | ND | 2.47 | 1.75 | 2 | 2.53 | 2.83 | 1.97 | 0.313 | 5.97 | 1.19 | ND | 2.69 | 3.43 | ND | ND | ND | 0.329 | 0.405 | 0.753 | 2.3 | 0.651 | 1.1 | 0.641 | ND | ND | 0.472 | ND | ND | 1.62 | 0.796 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| -81 IN | C | ND | ND | 1.84 | ND | 0.555 | 4.05 | 2.62 | 4.08 | 4.15 | 1.69 | 0.933 | 4.65 | 4.04 | 1.6 | 3.31 | 1.94 | ND | 3.31 | 0.956 | 4.16 | ND | 0.252 | 3.15 | ND | 1.76 | 1.52 | 0.744 | 2.01 | 0.001 | 2.86 | 2.94 | 0.231 | 1.26 | 3.07 | 3.31 | 1.56 | 2.31 | 0.707 | ND | ND | ND | ND | 0.548 | ND | 1.03 | ND | 0.206 | ND | ND | 0.632 | ND | 0.741 | ND | 1.16 | 0.126 | 0.287 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
|  | R | ND | ND | 2.74 | ND | 1.16 | 2.33 | 5.11 | 4.35 | 4.35 | 0.785 | 0.707 | ND | 0.954 | 2.49 | ND | 1.94 | 4.09 | 3.99 | 3.84 | 3.93 | 0.419 | 2.56 | 6.07 | 2.29 | 0.104 | ND | 1.71 | ND | 0.51 | 0.744 | 2.47 | ND | 0.258 | 2.45 | 4.15 | 0.828 | ND | 2.76 | ND | 2.61 | ND | ND | 3.54 | ND | 0.601 | ND | 0.844 | ND | ND | 2.02 | 1.81 | ND | ND | ND | 0.115 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A |  | L | 3.81 | 2.81 | 4.85 | ND | 3.99 | 2.39 | 0.929 | 6.05 | 2.3 | ND | 0.208 | ND | 4.07 | ND | ND | ND | ND | 3.54 | ND | ND | 3.49 | 0.465 | ND | ND | 1.19 | 4 | ND | ND | ND | ND | ND | ND | 2.91 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| -90 IN | C | 7.47 | 2.22 | 1.13 | ND | 6.95 | ND | 2.33 | 8.96 | 2.87 | 0.847 | 1.56 | ND | 4.8 | ND | ND | ND | ND | ND | ND | 8.83 | 0.169 | ND | ND | ND | ND | ND | ND | 5.97 | ND | ND | 0.105 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
|  | R | 2.57 | ND | 1.43 | ND | 5.68 | 3.17 | 1.04 | 1.92 | ND | 1.66 | 1.06 | ND | 5.25 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.307 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.12 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MAX
| CORROSION RATE (mpy): |  | 10: NOTE: CORROSION RATES ARE BASED ON COMPARISON OF; 30: TEST RESULTS; 67: APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | < 0 mpy (LOSS) or no data |  | 30: OVERALL CORROSION RATE (mils per year):
| 0-10 mpy (LOSS) |  | 10: 2020, 2022, 2023, 2024, 2025 |  |  | CALCULATED CORROSION RATE
| 10-20 mpy (LOSS) |  | 10: INSPECTION DATA; 30: 2.847
| > 20 mpy (LOSS) |  | 10: ND; 15: NO COMPARISON DATA
CORROSION
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Projection
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. PROJECTED THICKNESS MEASUREMENTS ARE IN INCHES. | [72 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MIN
A |  | L | 0.151 | 0.221 | 0.218 | 0.217 | 0.197 | 0.268 | 0.275 | 0.267 | 0.19 | 0.259 | 0.266 | 0.219 | 0.213 | 0.174 | 0.212 | 0.22 | 0.213 | 0.215 | 0.21 | 0.189 | 0.189 | 0.217 | 0.217 | 0.216 | 0.214 | 0.209 | 0.214 | 0.206 | 0.179 | 0.212 | 0.191 | 0.224 | 0.232 | 0.232 | 0.223 | 0.208 | 0.191 | 0.174 | 0.159 | 0.209 | 0.221 | 0.229 | 0.209 | 0.195 | 0.221 | 0.22 | 0.222 | 0.213 | 0.221 | 0.214 | 0.234 | 0.21 | 0.219 | 0.213 | 0.183 | 0.214 | 0.218 | 0.232 | 0.217 | 0.226 | 0.214 | 0.219 | 0.22 | 0.22 | 0.228 | 0.219 | 0.226 | 0.239 | 0.197
0.083 | +16 FT 6 IN | C | 0.188 | 0.201 | 0.215 | 0.224 | 0.225 | 0.262 | 0.266 | 0.274 | 0.276 | 0.263 | 0.258 | 0.218 | 0.222 | 0.235 | 0.212 | 0.219 | 0.218 | 0.213 | 0.209 | 0.217 | 0.226 | 0.21 | 0.216 | 0.213 | 0.215 | 0.206 | 0.207 | 0.23 | 0.169 | 0.184 | 0.182 | 0.222 | 0.223 | 0.23 | 0.222 | 0.223 | 0.183 | 0.195 | 0.204 | 0.228 | 0.232 | 0.233 | 0.222 | 0.21 | 0.228 | 0.217 | 0.227 | 0.172 | 0.216 | 0.216 | 0.215 | 0.211 | 0.219 | 0.205 | 0.211 | 0.209 | 0.219 | 0.227 | 0.217 | 0.219 | 0.216 | 0.224 | 0.226 | 0.219 | 0.225 | 0.22 | 0.229 | 0.226 | 0.204
|  | R | 0.205 | 0.194 | 0.223 | 0.223 | 0.23 | 0.268 | 0.153 | 0.186 | 0.273 | 0.262 | 0.205 | 0.219 | 0.221 | 0.236 | 0.206 | 0.229 | 0.216 | 0.211 | 0.2 | 0.167 | 0.222 | 0.211 | 0.21 | 0.214 | 0.216 | 0.189 | 0.217 | 0.219 | 0.188 | 0.204 | 0.184 | 0.191 | 0.221 | 0.229 | 0.226 | 0.236 | 0.192 | 0.212 | 0.209 | 0.212 | 0.227 | 0.224 | 0.177 | 0.226 | 0.222 | 0.222 | 0.23 | 0.216 | 0.213 | 0.189 | 0.21 | 0.204 | 0.217 | 0.213 | 0.208 | 0.209 | 0.223 | 0.222 | 0.193 | 0.217 | 0.224 | 0.216 | 0.222 | 0.226 | 0.229 | 0.228 | 0.237 | 0.227 | 0.221
A |  | L | RF | 0.217 | 0.233 | 0.208 | 0.19 | 0.27 | 0.256 | 0.255 | 0.25 | 0.263 | 0.25 | 0.218 | 0.229 | 0.214 | 0.191 | 0.207 | 0.209 | 0.21 | 0.216 | 0.2 | 0.205 | 0.208 | 0.221 | 0.21 | 0.19 | 0.214 | 0.213 | 0.208 | 0.213 | 0.205 | 0.187 | 0.215 | 0.17 | 0.228 | 0.226 | 0.215 | 0.198 | 0.202 | 0.2 | 0.189 | 0.207 | 0.182 | 0.217 | 0.198 | 0.205 | 0.198 | 0.209 | 0.194 | 0.228 | 0.179 | 0.226 | 0.199 | 0.209 | 0.159 | 0.169 | 0.224 | 0.215 | 0.209 | 0.204 | 0.203 | 0.212 | 0.22 | 0.21 | 0.22 | 0.24 | 0.227 | 0.215 | 0.229 | RF
0.083 | +15 FT | C | RF | 0.216 | 0.224 | 0.219 | 0.188 | 0.274 | 0.263 | 0.26 | 0.265 | 0.256 | 0.245 | 0.23 | 0.224 | 0.211 | 0.221 | 0.212 | 0.212 | 0.211 | 0.206 | 0.199 | 0.23 | 0.18 | 0.167 | 0.217 | 0.173 | 0.203 | 0.182 | 0.201 | 0.207 | 0.193 | 0.223 | 0.216 | 0.22 | 0.211 | 0.172 | 0.213 | 0.209 | 0.203 | 0.197 | 0.208 | 0.212 | 0.205 | 0.202 | 0.223 | 0.198 | 0.198 | 0.201 | 0.21 | 0.21 | 0.218 | 0.217 | 0.166 | 0.214 | 0.187 | 0.188 | 0.171 | 0.196 | 0.22 | 0.221 | 0.22 | 0.214 | 0.217 | 0.226 | 0.217 | 0.228 | 0.233 | 0.211 | 0.223 | RF
|  | R | RF | 0.213 | 0.219 | 0.213 | 0.182 | 0.268 | 0.271 | 0.251 | 0.272 | 0.252 | 0.271 | 0.2 | 0.218 | 0.202 | 0.201 | 0.215 | 0.218 | 0.2 | 0.209 | 0.194 | 0.211 | 0.129 | 0.168 | 0.213 | 0.174 | 0.188 | 0.214 | 0.203 | 0.203 | 0.217 | 0.198 | 0.188 | 0.219 | 0.201 | 0.223 | 0.208 | 0.221 | 0.182 | 0.19 | 0.194 | 0.205 | 0.209 | 0.207 | 0.206 | 0.182 | 0.186 | 0.207 | 0.209 | 0.196 | 0.208 | 0.216 | 0.217 | 0.204 | 0.217 | 0.164 | 0.209 | 0.211 | 0.219 | 0.207 | 0.215 | 0.189 | 0.224 | 0.232 | 0.224 | 0.222 | 0.243 | 0.225 | 0.214 | RF
A |  | L | 0.113 | 0.206 | 0.205 | 0.235 | 0.215 | 0.268 | 0.278 | 0.262 | 0.277 | 0.271 | 0.255 | 0.223 | 0.203 | 0.143 | 0.193 | 0.202 | 0.214 | 0.198 | 0.205 | 0.216 | 0.21 | 0.196 | 0.181 | 0.2 | 0.209 | 0.195 | 0.201 | 0.21 | 0.192 | 0.179 | 0.194 | 0.225 | 0.172 | 0.207 | 0.189 | 0.181 | 0.205 | 0.209 | 0.097 | 0.168 | 0.197 | 0.147 | 0.152 | 0.199 | 0.198 | 0.153 | 0.222 | 0.2 | 0.166 | 0.192 | 0.115 | 0.193 | 0.163 | 0.183 | 0.208 | 0.191 | 0.196 | 0.128 | 0.141 | 0.216 | 0.199 | 0.212 | 0.235 | 0.219 | 0.23 | 0.21 | 0.225 | 0.226 | RF
0.083 | +13 FT 6 IN | C | RF | 0.224 | 0.201 | 0.218 | 0.208 | 0.275 | 0.276 | 0.264 | 0.259 | 0.259 | 0.215 | 0.214 | 0.21 | 0.219 | 0.205 | 0.204 | 0.212 | 0.207 | 0.186 | 0.179 | 0.208 | 0.217 | 0.222 | 0.227 | 0.182 | 0.157 | 0.177 | 0.205 | 0.204 | 0.134 | 0.189 | 0.189 | 0.169 | 0.228 | 0.202 | 0.193 | 0.145 | 0.198 | 0.189 | 0.183 | 0.155 | 0.205 | 0.199 | 0.165 | 0.191 | 0.2 | 0.156 | 0.218 | 0.168 | 0.183 | 0.219 | 0.205 | 0.178 | 0.201 | 0.168 | 0.19 | 0.235 | 0.218 | 0.198 | 0.207 | 0.21 | 0.208 | 0.198 | 0.189 | 0.222 | 0.234 | 0.218 | 0.216 | RF
|  | R | 0.181 | 0.207 | 0.201 | 0.206 | 0.207 | 0.272 | 0.288 | 0.252 | 0.267 | 0.258 | 0.249 | 0.221 | 0.202 | 0.199 | 0.196 | 0.196 | 0.197 | 0.179 | 0.19 | 0.193 | 0.192 | 0.21 | 0.2 | 0.177 | 0.187 | 0.192 | 0.177 | 0.198 | 0.125 | 0.147 | 0.109 | 0.199 | 0.17 | 0.211 | 0.191 | 0.2 | 0.119 | 0.201 | 0.111 | 0.175 | 0.171 | 0.21 | 0.093 | 0.167 | 0.125 | 0.205 | 0.207 | 0.147 | 0.209 | 0.213 | 0.161 | 0.21 | 0.188 | 0.199 | 0.196 | 0.19 | 0.231 | 0.133 | 0.172 | 0.212 | 0.2 | 0.227 | 0.201 | 0.183 | 0.222 | 0.215 | 0.188 | 0.193 | RF
A |  | L | 0.178 | 0.211 | 0.218 | 0.225 | 0.223 | 0.227 | 0.276 | 0.245 | 0.222 | 0.209 | 0.228 | 0.204 | 0.204 | 0.192 | 0.198 | 0.193 | 0.158 | 0.208 | 0.197 | 0.177 | 0.186 | 0.194 | 0.199 | 0.187 | 0.191 | 0.197 | 0.203 | 0.189 | 0.198 | 0.2 | 0.21 | 0.207 | 0.178 | 0.202 | 0.209 | 0.202 | 0.184 | 0.163 | 0.143 | 0.167 | 0.138 | 0.146 | 0.148 | 0.13 | 0.173 | 0.161 | 0.193 | 0.165 | 0.135 | 0.182 | 0.125 | 0.184 | 0.157 | 0.15 | 0.182 | 0.176 | 0.19 | 0.201 | 0.174 | 0.159 | 0.195 | 0.2 | 0.221 | 0.187 | 0.185 | 0.234 | 0.229 | 0.217 | 0.216
0.083 | +12 FT | C | 0.193 | 0.229 | 0.219 | 0.22 | 0.208 | 0.252 | 0.24 | 0.251 | 0.218 | 0.216 | 0.214 | 0.211 | 0.211 | 0.222 | 0.199 | 0.195 | 0.201 | 0.214 | 0.219 | 0.193 | 0.187 | 0.203 | 0.138 | 0.169 | 0.203 | 0.193 | 0.179 | 0.193 | 0.194 | 0.191 | 0.108 | 0.17 | 0.19 | 0.197 | 0.202 | 0.19 | 0.207 | 0.173 | 0.157 | 0.115 | 0.174 | 0.225 | 0.156 | 0.167 | 0.142 | 0.183 | 0.192 | 0.178 | 0.176 | 0.179 | 0.16 | 0.167 | 0.169 | 0.173 | 0.17 | 0.168 | 0.189 | 0.204 | 0.195 | 0.174 | 0.214 | 0.186 | 0.218 | 0.206 | 0.22 | 0.235 | 0.197 | 0.219 | 0.181
|  | R | 0.096 | 0.219 | 0.207 | 0.209 | 0.219 | 0.213 | 0.24 | 0.261 | 0.224 | 0.214 | 0.199 | 0.217 | 0.192 | 0.207 | 0.198 | 0.205 | 0.186 | 0.213 | 0.172 | 0.175 | 0.187 | 0.132 | 0.157 | 0.227 | 0.162 | 0.151 | 0.188 | 0.141 | 0.23 | 0.191 | 0.18 | 0.203 | 0.205 | 0.192 | 0.18 | 0.197 | 0.175 | 0.178 | 0.183 | 0.107 | 0.205 | 0.128 | 0.166 | 0.199 | 0.196 | 0.194 | 0.198 | 0.179 | 0.178 | 0.175 | 0.183 | 0.164 | 0.18 | 0.193 | 0.164 | 0.196 | 0.204 | 0.178 | 0.168 | 0.182 | 0.208 | 0.214 | 0.208 | 0.222 | 0.222 | 0.224 | 0.212 | 0.206 | 0.224
A | POSITION 'A' | L | 2: 0.216; 3: 0.2; 4: 0.2; 5: 0.206; 65: 0.209; 66: 0.226; 67: 0.222; 68: 0.205
0.083 | OF THE | C | 2: 0.186; 3: 0.194; 4: 0.2; 5: 0.196; 65: 0.196; 66: 0.206; 67: 0.196; 68: 0.218
| OB PORTS | R | 2: 0.213; 3: 0.204; 4: 0.202; 5: 0.203; 65: 0.215; 66: 0.204; 67: 0.188; 68: 0.208
A | POSITION 'B' | L | 2: 0.194; 3: 0.203; 4: 0.212; 5: 0.235; 65: 0.2; 66: 0.21; 67: 0.197; 68: 0.232
0.083 | OF THE | C | 2: 0.197; 3: 0.196; 4: 0.21; 5: 0.194; 65: 0.208; 66: 0.203; 67: 0.21; 68: 0.213
| OB PORTS | R | 2: 0.198; 3: 0.198; 4: 0.212; 5: 0.203; 65: 0.212; 66: 0.201; 67: 0.204; 68: 0.207
A | POSITION 'C' | L | 2: 0.208; 3: 0.217; 4: 0.21; 5: 0.197; 65: 0.207; 66: 0.208; 67: 0.209; 68: 0.201
0.083 | OF THE | C | 2: 0.214; 3: 0.21; 4: 0.208; 5: 0.209; 65: 0.202; 66: 0.212; 67: 0.222; 68: 0.196
| OB PORTS | R | 2: 0.208; 3: 0.219; 4: 0.194; 5: 0.209; 65: 0.197; 66: 0.216; 67: 0.212; 68: 0.202
A |  | L | 0.196 | 0.222 | 0.224 | 0.223 | 0.208 | 0.013 | 0.27 | 0.279 | 0.252 | 0.257 | 0.236 | 0.23 | 0.194 | 0.163 | 0.192 | 0.203 | 0.206 | 0.172 | 0.205 | 0.179 | 0.191 | 0.174 | 0.147 | 0.19 | 0.16 | 0.174 | 0.188 | 0.195 | 0.198 | 0.183 | 0.206 | 0.177 | 0.21 | 0.205 | 0.226 | 0.17 | 0.156 | 0.123 | 0.14 | 0.163 | 0.141 | 0.187 | 0.237 | 0.233 | 0.146 | 0.157 | 0.216 | 0.197 | 0.216 | 0.155 | 0.186 | 0.153 | 0.2 | 0.174 | 0.142 | 0.216 | 0.203 | 0.201 | 0.199 | 0.211 | 0.203 | 0.202 | 0.214 | 0.214 | 0.216 | 0.206 | 0.204 | 0.207 | 0.18
0.083 | +10 FT 6 IN | C | 0.202 | 0.22 | 0.224 | 0.217 | 0.205 | 0.001 | 0.264 | 0.243 | 0.247 | 0.271 | 0.253 | 0.233 | 0.174 | 0.211 | 0.198 | 0.206 | 0.187 | 0.194 | 0.166 | 0.174 | 0.183 | 0.162 | 0.217 | 0.199 | 0.181 | 0.185 | 0.206 | 0.204 | 0.186 | 0.197 | 0.2 | 0.201 | 0.223 | 0.226 | 0.226 | 0.2 | 0.207 | 0.191 | 0.145 | 0.162 | 0.207 | 0.089 | 0.163 | 0.155 | 0.177 | 0.147 | 0.212 | 0.187 | 0.185 | 0.188 | 0.164 | 0.197 | 0.21 | 0.209 | 0.172 | 0.223 | 0.201 | 0.176 | 0.2 | 0.179 | 0.197 | 0.217 | 0.205 | 0.213 | 0.209 | 0.205 | 0.204 | 0.217 | 0.16
|  | R | 0.183 | 0.212 | 0.233 | 0.216 | 0.225 | 0.001 | 0.28 | 0.242 | 0.264 | 0.264 | 0.25 | 0.193 | 0.201 | 0.215 | 0.187 | 0.179 | 0.189 | 0.183 | 0.207 | 0.169 | 0.194 | 0.176 | 0.197 | 0.188 | 0.203 | 0.196 | 0.101 | 0.222 | 0.151 | 0.204 | 0.203 | 0.215 | 0.197 | 0.225 | 0.225 | 0.206 | 0.168 | 0.148 | 0.169 | 0.221 | 0.187 | 0.154 | 0.162 | 0.179 | 0.171 | 0.144 | 0.169 | 0.197 | 0.173 | 0.194 | 0.162 | 0.167 | 0.198 | 0.187 | 0.196 | 0.204 | 0.216 | 0.179 | 0.186 | 0.216 | 0.22 | 0.215 | 0.21 | 0.194 | 0.204 | 0.198 | 0.192 | 0.243 | 0.067
A | POSITION 'A' | L | 4: 0.207; 5: 0.212; 6: 0.263; 7: 0.232; 8: 0.275; 9: 0.272; 10: 0.253; 11: 0.265; 12: 0.204; 13: 0.207; 32: 0.188; 33: 0.199; 34: 0.203; 35: 0.186; 36: 0.192; 37: 0.166
0.083 | OF THE MANWAY | C | 4: 0.199; 5: 0.206; 6: 0.265; 7: 0.279; 8: 0.261; 9: 0.26; 10: 0.258; 11: 0.279; 12: 0.177; 13: 0.207; 32: 0.182; 33: 0.188; 34: 0.219; 35: 0.188; 36: 0.236; 37: 0.137
| & OSCILLATOR | R | 4: 0.217; 5: 0.211; 6: 0.268; 7: 0.263; 8: 0.267; 9: 0.276; 10: 0.226; 11: 0.279; 12: 0.188; 13: 0.208; 32: 0.211; 33: 0.195; 34: 0.205; 35: 0.191; 36: 0.229; 37: 0.125
A | POSITION 'B' | L | 4: 0.207; 5: 0.2; 6: RT; 7: 0.283; 8: 0.268; 9: 0.293; 10: 0.261; 11: RT; 12: 0.225; 13: 0.207; 32: 0.23; 33: 0.201; 34: 0.229; 35: 0.211; 36: 0.201; 37: 0.203
0.083 | OF THE MANWAY | C | 4: 0.205; 5: 0.186; 6: RT; 7: 0.24; 8: 0.25; 9: 0.261; 10: 0.224; 11: RT; 12: 0.179; 13: 0.228; 32: 0.198; 33: 0.211; 34: 0.226; 35: 0.21; 36: 0.214; 37: 0.197
| & OSCILLATOR | R | 4: 0.207; 5: 0.198; 6: RT; 7: 0.205; 8: 0.245; 9: 0.275; 10: 0.277; 11: RT; 12: 0.19; 13: 0.201; 32: 0.198; 33: 0.19; 34: 0.197; 35: 0.215; 36: 0.134; 37: 0.209
A | POSITION 'C' | L | 4: 0.191; 5: 0.207; 6: RT; 7: RT; 8: 0.272; 9: 0.259; 10: RT; 11: RT; 12: 0.223; 13: 0.208; 32: 0.192; 33: 0.185; 34: 0.233; 35: 0.218; 36: 0.171; 37: 0.189
0.083 | OF THE MANWAY | C | 4: 0.198; 5: 0.221; 6: RT; 7: RT; 8: 0.278; 9: 0.269; 10: RT; 11: RT; 12: 0.196; 13: 0.226; 32: 0.212; 33: 0.209; 34: 0.214; 35: 0.212; 36: 0.237; 37: 0.165
| & OSCILLATOR | R | 4: 0.203; 5: 0.201; 6: RT; 7: RT; 8: 0.281; 9: 0.282; 10: RT; 11: RT; 12: 0.201; 13: 0.216; 32: 0.189; 33: 0.205; 34: 0.199; 35: 0.209; 36: 0.168; 37: 0.237
A | POSITION 'D' | L | 4: 0.209; 5: 0.204; 6: RT; 7: 0.255; 8: 0.208; 9: 0.244; 10: 0.243; 11: RT; 12: 0.218; 13: 0.194; 32: 0.191; 33: 0.198; 34: 0.193; 35: 0.224; 36: 0.149; 37: 0.103
0.083 | OF THE MANWAY | C | 4: 0.218; 5: 0.197; 6: RT; 7: 0.273; 8: 0.194; 9: 0.245; 10: RT; 11: RT; 12: 0.214; 13: 0.172; 32: 0.211; 33: 0.183; 34: 0.215; 35: 0.215; 36: 0.191; 37: 0.081
| & OSCILLATOR | R | 4: 0.222; 5: 0.202; 6: RT; 7: 0.247; 8: 0.196; 9: 0.263; 10: RT; 11: RT; 12: 0.177; 13: 0.183; 32: 0.211; 33: 0.197; 34: 0.21; 35: 0.185; 36: 0.183; 37: 0.195
A | POSITION 'E' | L | 4: 0.218; 5: 0.21; 6: 0.188; 7: 0.249; 8: 0.269; 9: 0.267; 10: 0.25; 11: 0.27; 12: 0.203; 13: 0.208; 32: 0.198; 33: 0.183; 34: 0.229; 35: 0.208; 36: 0.163; 37: 0.117
0.083 | OF THE MANWAY | C | 4: 0.203; 5: 0.23; 6: 0.171; 7: 0.235; 8: 0.249; 9: 0.245; 10: 0.232; 11: 0.251; 12: 0.23; 13: 0.23; 32: 0.178; 33: 0.189; 34: 0.19; 35: 0.211; 36: 0.18; 37: 0.096
| & OSCILLATOR | R | 4: 0.214; 5: 0.202; 6: 0.201; 7: 0.243; 8: 0.28; 9: 0.27; 10: 0.241; 11: 0.265; 12: 0.235; 13: 0.223; 32: 0.2; 33: 0.191; 34: 0.186; 35: 0.218; 36: 0.17; 37: 0.149
A |  | L | 0.21 | 0.228 | 0.225 | 0.208 | 0.19 | RT | RT | 0.256 | 0.243 | RT | RT | 0.227 | 0.204 | 0.199 | 0.214 | 0.198 | 0.222 | 0.177 | 0.194 | 0.181 | 0.125 | 0.177 | 0.143 | 0.164 | 0.205 | 0.154 | 0.179 | 0.113 | 0.192 | 0.15 | 0.192 | 0.174 | 0.18 | 0.215 | 0.203 | 0.196 | 0.109 | 0.145 | 0.186 | 0.185 | 0.188 | 0.151 | 0.19 | 0.19 | 0.184 | 0.2 | 0.152 | 0.125 | 0.17 | 0.19 | 0.19 | 0.173 | 0.193 | 0.182 | 0.174 | 0.164 | 0.171 | 0.186 | 0.188 | 0.19 | 0.176 | 0.198 | 0.203 | 0.207 | 0.21 | 0.195 | 0.198 | 0.197 | RF
0.083 | +9 FT | C | 0.225 | 0.211 | 0.216 | 0.218 | 0.198 | 0.104 | RT | 0.218 | 0.257 | RT | RT | 0.225 | 0.187 | 0.176 | 0.226 | 0.183 | 0.209 | 0.2 | 0.173 | 0.188 | 0.167 | 0.171 | 0.167 | 0.12 | 0.164 | 0.121 | 0.186 | 0.16 | 0.144 | 0.169 | 0.165 | 0.184 | 0.169 | 0.203 | 0.208 | 0.201 | 0.107 | 0.157 | 0.202 | 0.193 | 0.169 | 0.191 | 0.168 | 0.161 | 0.158 | 0.193 | 0.156 | 0.175 | 0.195 | 0.178 | 0.175 | 0.149 | 0.177 | 0.158 | 0.177 | 0.159 | 0.179 | 0.171 | 0.198 | 0.205 | 0.214 | 0.213 | 0.206 | 0.198 | 0.223 | 0.22 | 0.201 | 0.187 | 0.083
|  | R | 0.223 | 0.22 | 0.211 | 0.222 | 0.189 | 0.099 | RT | 0.25 | 0.251 | RT | RT | 0.21 | 0.22 | 0.189 | 0.224 | 0.192 | 0.214 | 0.214 | 0.187 | 0.176 | 0.149 | 0.17 | 0.218 | 0.174 | 0.203 | 0.142 | 0.183 | 0.146 | 0.16 | 0.172 | 0.171 | 0.19 | 0.178 | 0.21 | 0.209 | 0.193 | 0.153 | 0.137 | 0.212 | 0.165 | 0.171 | 0.163 | 0.122 | 0.194 | 0.15 | 0.164 | 0.127 | 0.192 | 0.211 | 0.214 | 0.193 | 0.157 | 0.188 | 0.15 | 0.183 | 0.194 | 0.185 | 0.157 | 0.192 | 0.202 | 0.141 | 0.172 | 0.207 | 0.191 | 0.177 | 0.213 | 0.196 | 0.205 | 0.059
A |  | L | 0.205 | 0.215 | 0.23 | 0.226 | 0.209 | 0.258 | 0.242 | 0.253 | 0.253 | 0.253 | 0.251 | 0.21 | 0.211 | 0.195 | 0.204 | 0.198 | 0.194 | 0.199 | 0.178 | 0.203 | 0.144 | 0.18 | 0.195 | 0.187 | 0.205 | 0.178 | 0.186 | 0.208 | 0.179 | 0.185 | 0.121 | 0.111 | 0.093 | 0.144 | 0.126 | 0.194 | 0.212 | 0.193 | 0.134 | 0.193 | 0.211 | 0.192 | 0.193 | 0.18 | 0.198 | 0.192 | 0.186 | 0.2 | 0.199 | 0.184 | 0.189 | 0.168 | 0.204 | 0.169 | 0.207 | 0.198 | 0.185 | 0.204 | 0.179 | 0.196 | 0.207 | 0.215 | 0.192 | 0.215 | 0.226 | 0.202 | 0.224 | 0.222 | 0.086
0.083 | +7 FT 6 IN | C | 0.209 | 0.221 | 0.219 | 0.208 | 0.208 | 0.249 | 0.257 | 0.246 | 0.242 | 0.259 | 0.257 | 0.207 | 0.182 | 0.176 | 0.195 | 0.187 | 0.172 | 0.199 | 0.205 | 0.192 | 0.129 | 0.177 | 0.185 | 0.186 | 0.168 | 0.174 | 0.169 | 0.181 | 0.129 | 0.195 | 0.181 | 0.123 | 0.12 | 0.133 | 0.176 | 0.155 | 0.211 | 0.197 | 0.138 | 0.192 | 0.184 | 0.172 | 0.194 | 0.205 | 0.195 | 0.201 | 0.189 | 0.177 | 0.195 | 0.19 | 0.177 | 0.195 | 0.193 | 0.188 | 0.207 | 0.191 | 0.206 | 0.194 | 0.17 | 0.208 | 0.2 | 0.188 | 0.2 | 0.212 | 0.228 | 0.21 | 0.22 | 0.204 | 0.062
|  | R | 0.212 | 0.218 | 0.231 | 0.203 | 0.234 | 0.242 | 0.257 | 0.249 | 0.239 | 0.243 | 0.239 | 0.179 | 0.152 | 0.209 | 0.197 | 0.171 | 0.222 | 0.205 | 0.188 | 0.169 | 0.163 | 0.175 | 0.17 | 0.176 | 0.201 | 0.177 | 0.198 | 0.163 | 0.164 | 0.14 | 0.193 | 0.13 | 0.145 | 0.166 | 0.143 | 0.163 | 0.2 | 0.184 | 0.157 | 0.131 | 0.192 | 0.174 | 0.195 | 0.202 | 0.176 | 0.192 | 0.187 | 0.208 | 0.202 | 0.195 | 0.188 | 0.184 | 0.187 | 0.194 | 0.186 | 0.212 | 0.193 | 0.212 | 0.185 | 0.188 | 0.215 | 0.216 | 0.199 | 0.216 | 0.225 | 0.196 | 0.21 | 0.21 | 0.001
A |  | L | 0.214 | 0.221 | 0.227 | 0.206 | 0.218 | 0.261 | 0.275 | 0.265 | 0.261 | 0.251 | 0.249 | 0.216 | 0.195 | 0.136 | 0.173 | 0.151 | 0.148 | 0.133 | 0.195 | 0.124 | 0.114 | 0.113 | 0.18 | 0.166 | 0.181 | 0.177 | 0.136 | 0.194 | 0.186 | 0.166 | 0.197 | 0.179 | 0.152 | 0.2 | 0.2 | 0.171 | 0.207 | 0.196 | 0.196 | 0.2 | 0.189 | 0.185 | 0.226 | 0.205 | 0.22 | 0.215 | 0.222 | 0.225 | 0.192 | 0.196 | 0.204 | 0.209 | 0.176 | 0.202 | 0.213 | 0.197 | 0.195 | 0.211 | 0.208 | 0.206 | 0.223 | 0.163 | 0.215 | 0.184 | 0.21 | 0.201 | 0.204 | 0.194 | 0.196
0.083 | +6 FT | C | 0.204 | 0.208 | 0.232 | 0.217 | 0.225 | 0.262 | 0.265 | 0.263 | 0.263 | 0.26 | 0.244 | 0.211 | 0.167 | 0.199 | 0.14 | 0.138 | 0.168 | 0.131 | 0.178 | 0.145 | 0.169 | 0.111 | 0.175 | 0.159 | 0.194 | 0.164 | 0.14 | 0.188 | 0.196 | 0.191 | 0.187 | 0.175 | 0.169 | 0.212 | 0.118 | 0.175 | 0.225 | 0.205 | 0.204 | 0.201 | 0.141 | 0.19 | 0.208 | 0.207 | 0.22 | 0.217 | 0.226 | 0.219 | 0.166 | 0.217 | 0.214 | 0.179 | 0.2 | 0.219 | 0.205 | 0.209 | 0.215 | 0.206 | 0.218 | 0.204 | 0.214 | 0.215 | 0.219 | 0.175 | 0.212 | 0.202 | 0.184 | 0.173 | 0.214
|  | R | 0.23 | 0.212 | 0.212 | 0.218 | 0.213 | 0.26 | 0.265 | 0.264 | 0.262 | 0.258 | 0.249 | 0.194 | 0.182 | 0.138 | 0.159 | 0.165 | 0.143 | 0.115 | 0.178 | 0.154 | 0.139 | 0.16 | 0.201 | 0.167 | 0.221 | 0.189 | 0.192 | 0.137 | 0.192 | 0.185 | 0.187 | 0.187 | 0.219 | 0.179 | 0.144 | 0.216 | 0.207 | 0.218 | 0.175 | 0.207 | 0.159 | 0.178 | 0.205 | 0.205 | 0.226 | 0.225 | 0.226 | 0.219 | 0.205 | 0.207 | 0.214 | 0.187 | 0.189 | 0.187 | 0.206 | 0.203 | 0.199 | 0.214 | 0.195 | 0.21 | 0.217 | 0.178 | 0.215 | 0.194 | 0.215 | 0.202 | 0.198 | 0.2 | 0.211
A |  | L | 0.172 | 0.202 | 0.232 | 0.211 | 0.197 | 0.25 | 0.258 | 0.235 | 0.244 | 0.265 | 0.24 | 0.191 | 0.211 | 0.176 | 0.186 | 0.189 | 0.151 | 0.201 | 0.191 | 0.181 | 0.224 | 0.166 | 0.17 | 0.18 | 0.177 | 0.192 | 0.189 | 0.214 | 0.219 | 0.181 | 0.192 | 0.192 | 0.208 | 0.174 | 0.184 | 0.209 | 0.191 | 0.198 | 0.21 | 0.215 | 0.212 | 0.199 | 0.217 | 0.199 | 0.191 | 0.193 | 0.204 | 0.212 | 0.211 | 0.217 | 0.208 | 0.201 | 0.213 | 0.207 | 0.213 | 0.214 | 0.211 | 0.206 | 0.217 | 0.192 | 0.204 | 0.19 | 0.214 | 0.16 | 0.195 | 0.205 | 0.214 | 0.191 | 0.147
0.083 | +4 FT 6 IN | C | 0.183 | 0.2 | 0.204 | 0.19 | 0.198 | 0.254 | 0.244 | 0.229 | 0.217 | 0.25 | 0.224 | 0.191 | 0.183 | 0.214 | 0.217 | 0.196 | 0.168 | 0.156 | 0.187 | 0.163 | 0.198 | 0.172 | 0.186 | 0.18 | 0.221 | 0.167 | 0.188 | 0.194 | 0.324 | 0.173 | 0.2 | 0.226 | 0.2 | 0.193 | 0.192 | 0.196 | 0.212 | 0.204 | 0.21 | 0.208 | 0.217 | 0.164 | 0.218 | 0.208 | 0.208 | 0.212 | 0.204 | 0.197 | 0.212 | 0.194 | 0.199 | 0.213 | 0.204 | 0.218 | 0.208 | 0.2 | 0.195 | 0.204 | 0.216 | 0.209 | 0.212 | 0.204 | 0.204 | 0.192 | 0.213 | 0.207 | 0.208 | 0.192 | 0.187
|  | R | 0.15 | 0.209 | 0.185 | 0.206 | 0.202 | 0.244 | 0.246 | 0.254 | 0.244 | 0.254 | 0.229 | 0.2 | 0.168 | 0.198 | 0.169 | 0.175 | 0.182 | 0.14 | 0.196 | 0.159 | 0.195 | 0.193 | 0.16 | 0.167 | 0.199 | 0.206 | 0.195 | 0.206 | 0.323 | 0.183 | 0.172 | 0.185 | 0.193 | 0.196 | 0.213 | 0.184 | 0.207 | 0.21 | 0.215 | 0.21 | 0.214 | 0.193 | 0.186 | 0.207 | 0.215 | 0.207 | 0.211 | 0.198 | 0.217 | 0.2 | 0.199 | 0.194 | 0.217 | 0.216 | 0.207 | 0.199 | 0.21 | 0.212 | 0.212 | 0.21 | 0.218 | 0.206 | 0.222 | 0.193 | 0.188 | 0.197 | 0.205 | 0.158 | 0.23
A |  | L | 0.187 | 0.202 | 0.215 | 0.206 | 0.227 | 0.224 | 0.221 | 0.269 | 0.269 | 0.267 | 0.223 | 0.205 | 0.169 | 0.221 | 0.198 | 0.162 | 0.201 | 0.15 | 0.158 | 0.213 | 0.221 | 0.2 | 0.195 | 0.187 | 0.216 | 0.205 | 0.182 | 0.197 | 0.314 | 0.169 | 0.128 | 0.166 | 0.214 | 0.186 | 0.196 | 0.206 | 0.213 | 0.217 | 0.216 | 0.208 | 0.207 | 0.163 | 0.193 | 0.19 | 0.196 | 0.21 | 0.186 | 0.195 | 0.239 | 0.202 | 0.23 | 0.233 | 0.212 | 0.196 | 0.22 | 0.211 | 0.209 | 0.212 | 0.235 | 0.195 | 0.198 | 0.195 | 0.188 | 0.226 | 0.21 | 0.178 | 0.235 | 0.236 | 0.229
0.083 | +3 FT | C | 0.195 | 0.197 | 0.22 | 0.205 | 0.229 | 0.247 | 0.249 | 0.266 | 0.261 | 0.253 | 0.254 | 0.215 | 0.236 | 0.242 | 0.166 | 0.181 | 0.179 | 0.199 | 0.218 | 0.23 | 0.214 | 0.155 | 0.176 | 0.195 | 0.155 | 0.175 | 0.208 | 0.206 | 0.328 | 0.213 | 0.202 | 0.151 | 0.212 | 0.211 | 0.208 | 0.203 | 0.212 | 0.196 | 0.22 | 0.224 | 0.195 | 0.183 | 0.198 | 0.201 | 0.201 | 0.186 | 0.197 | 0.193 | 0.213 | 0.22 | 0.19 | 0.17 | 0.182 | 0.199 | 0.202 | 0.206 | 0.194 | 0.199 | 0.232 | 0.205 | 0.23 | 0.22 | 0.208 | 0.183 | 0.208 | 0.229 | 0.202 | 0.192 | 0.194
|  | R | 0.177 | 0.2 | 0.219 | 0.194 | 0.207 | 0.244 | 0.273 | 0.269 | 0.263 | 0.267 | 0.245 | 0.204 | 0.213 | 0.196 | 0.157 | 0.217 | 0.313 | 0.166 | 0.176 | 0.219 | 0.233 | 0.205 | 0.162 | 0.183 | 0.158 | 0.204 | 0.197 | 0.212 | 0.34 | 0.195 | 0.14 | 0.227 | 0.186 | 0.181 | 0.206 | 0.215 | 0.219 | 0.217 | 0.212 | 0.22 | 0.213 | 0.194 | 0.197 | 0.197 | 0.211 | 0.19 | 0.208 | 0.221 | 0.19 | 0.221 | 0.216 | 0.218 | 0.218 | 0.197 | 0.195 | 0.213 | 0.224 | 0.205 | 0.204 | 0.198 | 0.212 | 0.223 | 0.22 | 0.221 | 0.174 | 0.229 | 0.216 | 0.203 | 0.209
A |  | L | 0.088 | 0.187 | 0.209 | 0.159 | 0.204 | 0.244 | 0.243 | 0.252 | 0.225 | 0.263 | 0.24 | 0.213 | 0.204 | 0.218 | 0.2 | 0.197 | 0.162 | 0.188 | 0.184 | 0.189 | 0.221 | 0.205 | 0.199 | 0.206 | 0.164 | 0.215 | 0.213 | 0.211 | 0.17 | 0.201 | 0.182 | 0.17 | 0.205 | 0.203 | 0.191 | 0.236 | 0.176 | 0.179 | 0.18 | 0.193 | 0.194 | 0.204 | 0.192 | 0.188 | 0.187 | 0.19 | 0.189 | 0.182 | 0.195 | 0.198 | 0.222 | 0.195 | 0.192 | 0.214 | 0.212 | 0.209 | 0.196 | 0.197 | 0.208 | 0.189 | 0.197 | 0.236 | 0.237 | 0.252 | 0.213 | 0.201 | 0.234 | 0.235 | 0.198
0.083 | +1 FT 6 IN | C | 0.119 | 0.178 | 0.199 | 0.204 | 0.223 | 0.281 | 0.231 | 0.252 | 0.278 | 0.241 | 0.292 | 0.214 | 0.217 | 0.229 | 0.199 | 0.191 | 0.191 | 0.189 | 0.198 | 0.188 | 0.204 | 0.221 | 0.173 | 0.212 | 0.23 | 0.209 | 0.211 | 0.205 | 0.153 | 0.207 | 0.203 | 0.19 | 0.193 | 0.172 | 0.19 | 0.172 | 0.201 | 0.211 | 0.194 | 0.179 | 0.164 | 0.187 | 0.177 | 0.177 | 0.173 | 0.176 | 0.176 | 0.202 | 0.189 | 0.208 | 0.182 | 0.195 | 0.2 | 0.215 | 0.202 | 0.21 | 0.199 | 0.207 | 0.203 | 0.191 | 0.201 | 0.215 | 0.235 | 0.215 | 0.203 | 0.216 | 0.236 | 0.211 | 0.239
|  | R | 0.133 | 0.182 | 0.2 | 0.194 | 0.197 | 0.227 | 0.236 | 0.258 | 0.245 | 0.237 | 0.256 | 0.213 | 0.181 | 0.208 | 0.207 | 0.208 | 0.179 | 0.187 | 0.206 | 0.202 | 0.189 | 0.227 | 0.219 | 0.202 | 0.207 | 0.198 | 0.211 | 0.214 | 0.19 | 0.24 | 0.183 | 0.196 | 0.166 | 0.169 | 0.188 | 0.209 | 0.188 | 0.243 | 0.194 | 0.207 | 0.208 | 0.187 | 0.196 | 0.177 | 0.195 | 0.168 | 0.182 | 0.202 | 0.159 | 0.196 | 0.178 | 0.19 | 0.187 | 0.192 | 0.209 | 0.195 | 0.205 | 0.21 | 0.209 | 0.212 | 0.218 | 0.215 | 0.219 | 0.235 | 0.211 | 0.183 | 0.206 | 0.239 | 0.206
A |  | L | 0.213 | 0.241 | 0.195 | 0.203 | 0.219 | 0.25 | 0.278 | 0.26 | 0.248 | 0.28 | 0.264 | 0.218 | 0.203 | 0.229 | 0.206 | 0.198 | 0.204 | 0.208 | 0.218 | 0.206 | 0.239 | 0.251 | 0.234 | 0.193 | 0.215 | 0.205 | 0.196 | 0.213 | 0.21 | 0.223 | 0.204 | 0.19 | 0.212 | 0.219 | 0.223 | 0.217 | 0.197 | 0.195 | RF | 0.257 | 0.227 | 0.221 | 0.188 | 0.203 | 0.185 | 0.227 | 0.172 | 0.219 | 0.204 | 0.215 | 0.207 | 0.187 | 0.202 | 0.181 | 0.187 | RF | 0.248 | 0.219 | 0.223 | 0.2 | 0.223 | 0.211 | 0.201 | RF | 0.22 | 0.232 | 0.217 | RF | RF
0.083 | 0 REFERENCE | C | 0.216 | 0.219 | 0.206 | 0.231 | 0.189 | 0.278 | 0.278 | 0.231 | 0.283 | 0.296 | 0.263 | 0.225 | 0.198 | 0.227 | 0.212 | 0.21 | 0.204 | 0.228 | 0.201 | 0.203 | 0.23 | 0.246 | 0.197 | 0.211 | 0.213 | 0.205 | 0.216 | 0.201 | 0.214 | 0.207 | 0.185 | 0.206 | 0.21 | 0.21 | 0.169 | 0.217 | 0.201 | 0.208 | 0.238 | 0.244 | 0.192 | 0.184 | 0.192 | 0.213 | 0.199 | 0.227 | 0.192 | 0.239 | 0.2 | 0.202 | 0.201 | 0.166 | 0.174 | 0.176 | 0.186 | 0.221 | 0.228 | 0.261 | 0.217 | 0.219 | 0.221 | 0.229 | 0.238 | RF | RF | 0.219 | 0.196 | 0.251 | 0.221
|  | R | RF | 0.2 | 0.192 | 0.215 | 0.194 | 0.266 | 0.278 | 0.251 | 0.27 | 0.281 | 0.263 | 0.225 | 0.211 | 0.227 | 0.206 | 0.199 | 0.202 | 0.213 | 0.208 | 0.217 | 0.234 | RF | 0.195 | 0.207 | 0.218 | 0.213 | 0.2 | 0.237 | 0.208 | 0.218 | 0.195 | 0.193 | 0.198 | 0.177 | 0.205 | 0.233 | 0.18 | 0.174 | 0.257 | RF | 0.22 | 0.215 | 0.198 | 0.208 | 0.179 | 0.179 | 0.219 | 0.208 | 0.196 | 0.194 | 0.194 | 0.173 | 0.184 | 0.188 | 0.164 | 0.229 | RF | 0.222 | 0.217 | 0.219 | 0.237 | 0.229 | 0.219 | 0.246 | RF | 0.22 | 0.199 | 0.232 | 0.221
A | POSITION 'A' | L |  | 0.206 | 0.225 | 0.183 | 0.165 | 0.262 | 0.24 |  |  |  | 0.242 | 0.183 | 0.223 | 0.183 | 0.204 | 0.186 |  |  | 0.212 | 0.191 | 0.188 | 0.191 | 0.197 | 0.193 | [7 empty] | 0.225 | 0.208 | 0.196 | 0.197 |  | 0.209 | 0.189 | 0.193 | 0.175 | 0.181 | 0.189 |  |  | 0.206 | 0.169 | 0.199 | 0.202 | 0.188 | 0.192 |  |  |  | 0.212 | 0.216 | 0.157 | 0.204 | 0.193 | 0.177 |  |  | 0.206 | 0.216 | 0.228 | 0.222 | 0.229 | 0.222
0.083 | OF THE | C |  | 0.208 | 0.219 | 0.183 | 0.165 | 0.255 | 0.245 |  |  |  | 0.238 | 0.19 | 0.203 | 0.213 | 0.204 | 0.198 |  |  | 0.209 | 0.201 | 0.184 | 0.194 | 0.181 | 0.186 | [7 empty] | 0.215 | 0.192 | 0.229 | 0.199 |  | 0.194 | 0.193 | 0.202 | 0.21 | 0.174 | 0.191 |  |  | 0.168 | 0.16 | 0.168 | 0.197 | 0.186 | 0.178 |  |  |  | 0.226 | 0.202 | 0.164 | 0.178 | 0.191 | 0.196 |  |  | 0.215 | 0.227 | 0.212 | 0.228 | 0.236 | 0.203
| SECONDARIES | R |  | 0.208 | 0.23 | 0.184 | 0.19 | 0.236 | 0.248 |  |  |  | 0.222 | 0.204 | 0.179 | 0.216 | 0.178 | 0.214 |  |  | 0.212 | 0.208 | 0.193 | 0.198 | 0.212 | 0.188 | [7 empty] | 0.202 | 0.156 | 0.219 | 0.209 |  | 0.195 | 0.175 | 0.196 | 0.196 | 0.185 | 0.205 |  |  | 0.168 | 0.177 | 0.169 | 0.181 | 0.193 | 0.194 |  |  |  | 0.213 | 0.216 | 0.152 | 0.206 | 0.201 | 0.187 |  |  | 0.217 | 0.225 | 0.217 | 0.225 | 0.232 | 0.225
A | POSITION 'B' | L |  | 0.227 | 0.198 | 0.205 | 0.211 | 0.225 | 0.234 |  |  |  | 0.252 | 0.19 | 0.228 | 0.21 | 0.201 | 0.184 |  |  | 0.204 | 0.198 | 0.218 | 0.217 | 0.214 | 0.192 | [7 empty] | 0.199 | 0.196 | 0.21 | 0.176 |  | 0.199 | 0.189 | 0.198 | 0.209 | 0.237 | 0.221 |  |  | 0.196 | 0.199 | 0.189 | 0.194 | 0.171 | 0.195 |  |  |  | 0.178 | 0.192 | 0.195 | 0.216 | 0.225 | 0.178 |  |  | 0.204 | 0.228 | 0.228 | 0.227 | 0.221 | 0.21
0.083 | OF THE | C |  | 0.191 | 0.177 | 0.206 | 0.211 | 0.209 | 0.222 |  |  |  | 0.253 | 0.202 | 0.185 | 0.198 | 0.186 | 0.193 |  |  | 0.188 | 0.2 | 0.221 | 0.206 | 0.202 | 0.187 | [7 empty] | 0.181 | 0.187 | 0.208 | 0.178 |  | 0.203 | 0.205 | 0.196 | 0.219 | 0.235 | 0.218 |  |  | 0.184 | 0.163 | 0.193 | 0.183 | 0.186 | 0.151 |  |  |  | 0.193 | 0.186 | 0.218 | 0.206 | 0.187 | 0.184 |  |  | 0.201 | 0.217 | 0.234 | 0.226 | 0.228 | 0.211
| SECONDARIES | R |  | 0.185 | 0.179 | 0.214 | 0.219 | 0.216 | 0.243 |  |  |  | 0.242 | 0.215 | 0.184 | 0.189 | 0.191 | 0.208 |  |  | 0.2 | 0.196 | 0.218 | 0.218 | 0.189 | 0.184 | [7 empty] | 0.184 | 0.21 | 0.195 | 0.191 |  | 0.188 | 0.197 | 0.205 | 0.222 | 0.192 | 0.219 |  |  | 0.201 | 0.183 | 0.187 | 0.198 | 0.187 | 0.187 |  |  |  | 0.196 | 0.212 | 0.211 | 0.208 | 0.19 | 0.207 |  |  | 0.211 | 0.22 | 0.23 | 0.227 | 0.222 | 0.205
A |  | L | 0.212 | 0.221 | 0.189 | 0.204 | 0.149 | 0.26 | 0.269 | 0.266 | 0.284 | 0.279 | 0.263 | 0.226 | 0.203 | 0.238 | 0.218 | 0.207 | 0.21 | 0.224 | 0.217 | 0.215 | 0.207 | 0.187 | 0.213 | 0.212 | 0.224 | 0.207 | 0.209 | 0.205 | 0.206 | 0.236 | 0.207 | 0.215 | 0.225 | 0.219 | 0.211 | 0.204 | 0.183 | 0.177 | 0.17 | 0.175 | 0.18 | 0.183 | 0.214 | 0.179 | 0.197 | 0.196 | 0.2 | 0.228 | 0.219 | 0.202 | 0.194 | 0.206 | 0.178 | 0.206 | 0.19 | 0.144 | 0.203 | 0.203 | 0.21 | 0.213 | 0.203 | 0.216 | 0.194 | 0.213 | 0.208 | 0.222 | 0.223 | 0.186 | RF
0.083 | -9 IN | C | 0.206 | 0.216 | 0.227 | 0.213 | 0.15 | 0.261 | 0.269 | 0.276 | 0.271 | 0.266 | 0.261 | 0.254 | 0.215 | 0.221 | 0.232 | 0.228 | 0.208 | 0.215 | 0.195 | 0.19 | 0.193 | 0.188 | 0.208 | 0.207 | 0.223 | 0.207 | 0.206 | 0.21 | 0.23 | 0.21 | 0.201 | 0.182 | 0.197 | 0.142 | 0.217 | 0.21 | 0.214 | 0.161 | 0.248 | 0.181 | 0.206 | 0.183 | 0.193 | 0.172 | 0.202 | 0.186 | 0.205 | 0.202 | 0.211 | 0.188 | 0.207 | 0.202 | 0.198 | 0.168 | 0.189 | 0.197 | 0.174 | 0.215 | 0.2 | 0.222 | 0.215 | 0.221 | 0.214 | 0.208 | 0.172 | 0.215 | 0.223 | 0.18 | 0.222
|  | R | 0.194 | 0.213 | 0.227 | 0.19 | 0.153 | 0.262 | 0.263 | 0.275 | 0.254 | 0.267 | 0.244 | 0.218 | 0.215 | 0.221 | 0.219 | 0.217 | 0.219 | 0.221 | 0.193 | 0.194 | 0.189 | 0.239 | 0.211 | 0.213 | 0.221 | 0.215 | 0.209 | 0.211 | 0.204 | 0.227 | 0.198 | 0.197 | 0.232 | 0.236 | 0.217 | 0.216 | 0.196 | 0.207 | 0.195 | 0.227 | 0.204 | 0.224 | 0.217 | 0.189 | 0.194 | 0.191 | 0.205 | 0.204 | 0.215 | 0.202 | 0.193 | 0.203 | 0.188 | 0.154 | 0.181 | 0.209 | 0.176 | 0.211 | 0.211 | 0.223 | 0.218 | 0.221 | 0.233 | 0.171 | RF | 0.221 | 0.219 | 0.146 | 0.223
A | POSITION 'C' | L |  | 0.228 | 0.228 | 0.229 | 0.178 | 0.215 | 0.247 |  |  |  | 0.244 | 0.227 | 0.214 | 0.242 | 0.213 | 0.21 |  |  | 0.23 | 0.203 | 0.162 | 0.177 | 0.204 | 0.197 | [7 empty] | 0.192 | 0.209 | 0.2 | 0.214 |  | 0.193 | 0.201 | 0.176 | 0.201 | 0.189 | 0.206 |  |  | 0.202 | 0.171 | 0.195 | 0.19 | 0.173 | 0.198 |  |  |  | 0.18 | 0.2 | 0.174 | 0.209 | 0.21 | 0.197 |  |  | 0.209 | 0.235 | 0.217 | 0.206 | 0.218 | 0.222
0.083 | OF THE | C |  | 0.189 | 0.217 | 0.204 | 0.154 | 0.214 | 0.222 |  |  |  | 0.242 | 0.207 | 0.192 | 0.193 | 0.21 | 0.213 |  |  | 0.203 | 0.182 | 0.183 | 0.182 | 0.21 | 0.196 | [7 empty] | 0.217 | 0.166 | 0.188 | 0.207 |  | 0.203 | 0.187 | 0.192 | 0.14 | 0.186 | 0.182 |  |  | 0.171 | 0.17 | 0.153 | 0.185 | 0.182 | 0.189 |  |  |  | 0.194 | 0.199 | 0.189 | 0.165 | 0.184 | 0.18 |  |  | 0.21 | 0.229 | 0.201 | 0.198 | 0.216 | 0.212
| SECONDARIES | R |  | 0.196 | 0.212 | 0.219 | 0.172 | 0.186 | 0.242 |  |  |  | 0.265 | 0.204 | 0.181 | 0.172 | 0.208 | 0.215 |  |  | 0.211 | 0.171 | 0.159 | 0.181 | 0.194 | 0.175 | [7 empty] | 0.2 | 0.193 | 0.209 | 0.193 |  | 0.205 | 0.183 | 0.19 | 0.195 | 0.192 | 0.214 |  |  | 0.187 | 0.173 | 0.197 | 0.187 | 0.173 | 0.197 |  |  |  | 0.159 | 0.143 | 0.159 | 0.134 | 0.204 | 0.179 |  |  | 0.213 | 0.226 | 0.209 | 0.209 | 0.219 | 0.218
A |  | L | 0.206 | 0.199 | 0.232 | 0.228 | 0.24 | 0.303 | 0.274 | 0.276 | 0.26 | 0.249 | 0.255 | 0.22 | 0.234 | 0.23 | 0.231 | 0.212 | 0.225 | 0.208 | 0.211 | 0.209 | 0.214 | 0.218 | 0.206 | 0.214 | 0.214 | 0.21 | 0.206 | 0.212 | 0.212 | 0.214 | 0.207 | 0.229 | 0.208 | 0.196 | 0.2 | 0.198 | 0.205 | 0.209 | 0.2 | 0.205 | 0.201 | 0.194 | 0.186 | 0.206 | 0.199 | 0.209 | 0.192 | 0.205 | 0.208 | 0.213 | 0.207 | 0.212 | 0.216 | 0.212 | 0.212 | 0.222 | 0.219 | 0.212 | 0.193 | 0.219 | 0.223 | 0.213 | 0.177 | 0.206 | 0.21 | 0.161 | 0.211 | 0.154 | 0.218
0.083 | -18 IN | C | 0.214 | 0.219 | 0.215 | 0.244 | 0.202 | 0.294 | 0.291 | 0.298 | 0.278 | 0.256 | 0.255 | 0.21 | 0.234 | 0.219 | 0.231 | 0.213 | 0.245 | 0.204 | 0.216 | 0.211 | 0.212 | 0.217 | 0.207 | 0.217 | 0.217 | 0.216 | 0.21 | 0.235 | 0.212 | 0.209 | 0.207 | 0.205 | 0.192 | 0.199 | 0.206 | 0.202 | 0.197 | 0.185 | 0.205 | 0.197 | 0.19 | 0.179 | 0.208 | 0.214 | 0.19 | 0.203 | 0.193 | 0.21 | 0.204 | 0.215 | 0.19 | 0.202 | 0.183 | 0.203 | 0.211 | 0.219 | 0.208 | 0.212 | 0.208 | 0.218 | 0.208 | 0.21 | 0.226 | 0.192 | 0.205 | 0.233 | 0.221 | 0.203 | 0.219
|  | R | 0.202 | 0.226 | 0.218 | 0.241 | 0.233 | 0.271 | 0.292 | 0.302 | 0.261 | 0.245 | 0.247 | 0.209 | 0.212 | 0.219 | 0.213 | 0.218 | 0.221 | 0.239 | 0.217 | 0.217 | 0.208 | 0.236 | 0.214 | 0.22 | 0.211 | 0.216 | 0.215 | 0.234 | 0.213 | 0.211 | 0.213 | 0.217 | 0.22 | 0.226 | 0.2 | 0.214 | 0.203 | 0.187 | 0.193 | 0.187 | 0.193 | 0.229 | 0.191 | 0.196 | 0.177 | 0.147 | 0.179 | 0.202 | 0.198 | 0.207 | 0.202 | 0.174 | 0.2 | 0.209 | 0.21 | 0.225 | 0.221 | 0.223 | 0.215 | 0.212 | 0.21 | 0.222 | 0.221 | 0.228 | 0.247 | 0.222 | 0.222 | 0.226 | 0.202
A |  | L | 0.201 | RF | 0.228 | 0.237 | 0.213 | 0.257 | 0.278 | 0.264 | 0.257 | 0.224 | 0.247 | 0.211 | 0.236 | 0.23 | 0.182 | 0.22 | 0.215 | 0.205 | 0.208 | 0.198 | 0.198 | 0.21 | 0.216 | 0.207 | 0.196 | 0.157 | 0.208 | 0.208 | 0.213 | 0.21 | 0.198 | 0.19 | 0.207 | 0.211 | 0.209 | 0.186 | 0.184 | 0.195 | 0.21 | 0.2 | 0.211 | 0.21 | 0.221 | 0.211 | 0.211 | 0.209 | 0.206 | 0.207 | 0.224 | 0.204 | 0.205 | 0.208 | 0.208 | 0.205 | 0.208 | 0.227 | 0.22 | 0.221 | 0.185 | 0.216 | 0.199 | 0.189 | 0.204 | 0.206 | 0.219 | 0.224 | 0.222 | 0.214 | 0.153
0.083 | -27 IN | C | 0.201 | 0.221 | 0.249 | 0.231 | 0.226 | 0.252 | 0.273 | 0.294 | 0.3 | 0.262 | 0.231 | 0.218 | 0.22 | 0.219 | 0.219 | 0.211 | 0.209 | 0.214 | 0.225 | 0.208 | 0.209 | 0.209 | 0.219 | 0.214 | 0.213 | 0.206 | 0.196 | 0.202 | 0.211 | 0.208 | 0.203 | 0.193 | 0.206 | 0.199 | 0.197 | 0.198 | 0.19 | 0.212 | 0.212 | 0.209 | 0.205 | 0.193 | 0.228 | 0.235 | 0.228 | 0.216 | 0.127 | 0.221 | 0.215 | 0.205 | 0.221 | 0.2 | 0.212 | 0.199 | 0.211 | 0.206 | 0.206 | 0.208 | 0.219 | 0.197 | 0.216 | 0.201 | 0.202 | 0.216 | 0.221 | 0.206 | 0.216 | 0.208 | 0.182
|  | R | RF | 0.223 | 0.301 | 0.223 | 0.232 | 0.251 | 0.258 | 0.254 | 0.255 | 0.26 | 0.241 | 0.231 | 0.222 | 0.231 | 0.2 | 0.223 | 0.212 | 0.205 | 0.211 | 0.226 | 0.215 | 0.193 | 0.194 | 0.208 | 0.216 | 0.212 | 0.203 | 0.204 | 0.196 | 0.225 | 0.205 | 0.202 | 0.206 | 0.225 | 0.213 | 0.235 | 0.193 | 0.21 | 0.217 | 0.194 | 0.197 | 0.209 | 0.223 | 0.215 | 0.204 | 0.203 | 0.206 | 0.217 | 0.193 | 0.2 | 0.207 | 0.202 | 0.212 | 0.212 | 0.213 | 0.217 | 0.21 | 0.201 | 0.204 | 0.223 | 0.198 | 0.211 | 0.21 | 0.226 | 0.226 | 0.218 | 0.199 | 0.232 | 0.234
A |  | L | 0.229 | 0.194 | 0.18 | 0.228 | 0.217 | 0.253 | 0.267 | 0.263 | 0.263 | 0.259 | 0.262 | 0.225 | 0.227 | 0.245 | 0.211 | 0.224 | 0.208 | 0.201 | 0.214 | 0.205 | 0.205 | 0.206 | 0.213 | 0.222 | 0.207 | 0.201 | 0.213 | 0.216 | 0.208 | 0.196 | 0.187 | 0.198 | 0.202 | 0.215 | 0.234 | 0.2 | 0.199 | 0.207 | 0.198 | 0.21 | 0.217 | 0.226 | 0.226 | 0.215 | 0.216 | 0.225 | 0.206 | 0.226 | 0.221 | 0.165 | 0.204 | 0.22 | 0.22 | 0.215 | 0.204 | 0.2 | 0.216 | 0.214 | 0.21 | 0.224 | 0.216 | 0.194 | 0.208 | 0.216 | 0.254 | 0.221 | 0.222 | 0.243 | 0.23
0.083 | -36 IN | C | 0.193 | 0.184 | 0.226 | 0.228 | 0.218 | 0.259 | 0.29 | 0.26 | 0.256 | 0.248 | 0.261 | 0.227 | 0.218 | 0.213 | 0.208 | 0.233 | 0.216 | 0.217 | 0.222 | 0.197 | 0.243 | 0.214 | 0.213 | 0.219 | 0.212 | 0.207 | 0.219 | 0.245 | 0.217 | 0.201 | 0.193 | 0.193 | 0.225 | 0.224 | 0.196 | 0.215 | 0.225 | 0.217 | 0.212 | 0.214 | 0.195 | 0.202 | 0.218 | 0.207 | 0.229 | 0.226 | 0.208 | 0.224 | 0.226 | 0.214 | 0.208 | 0.222 | 0.211 | 0.203 | 0.215 | 0.195 | 0.229 | 0.214 | 0.214 | 0.224 | 0.213 | 0.198 | 0.206 | 0.227 | 0.221 | 0.219 | 0.228 | 0.188 | 0.219
|  | R | RF | 0.212 | 0.223 | 0.212 | 0.217 | 0.268 | 0.264 | 0.264 | 0.258 | 0.25 | 0.263 | 0.225 | 0.22 | 0.206 | 0.223 | 0.209 | 0.204 | 0.207 | 0.222 | 0.208 | 0.225 | 0.192 | 0.205 | 0.211 | 0.207 | 0.204 | 0.208 | 0.213 | 0.22 | 0.196 | 0.208 | 0.207 | 0.222 | 0.213 | 0.214 | 0.199 | 0.214 | 0.221 | 0.202 | 0.205 | 0.201 | 0.212 | 0.205 | 0.214 | 0.21 | 0.221 | 0.208 | 0.219 | 0.211 | 0.204 | 0.199 | 0.202 | 0.201 | 0.186 | 0.208 | 0.192 | 0.212 | 0.214 | 0.208 | 0.224 | 0.215 | 0.218 | 0.204 | 0.232 | 0.223 | 0.189 | 0.21 | 0.219 | 0.179
A |  | L | 0.21 | 0.226 | 0.249 | 0.235 | RF | 0.237 | 0.27 | 0.241 | 0.284 | 0.26 | 0.251 | 0.234 | 0.218 | 0.226 | 0.207 | 0.206 | 0.205 | 0.202 | 0.189 | 0.197 | 0.212 | 0.229 | 0.235 | 0.227 | 0.212 | 0.202 | 0.211 | 0.24 | 0.209 | 0.223 | 0.199 | 0.207 | 0.173 | 0.201 | 0.22 | 0.22 | 0.204 | 0.205 | 0.199 | 0.22 | 0.192 | 0.209 | 0.223 | 0.218 | 0.208 | 0.23 | 0.205 | 0.212 | 0.212 | 0.215 | 0.219 | 0.219 | 0.207 | 0.21 | 0.224 | 0.204 | 0.218 | 0.218 | 0.192 | 0.219 | 0.204 | 0.229 | 0.191 | 0.219 | 0.218 | 0.203 | 0.214 | 0.212 | 0.228
0.083 | -45 IN | C | 0.115 | 0.224 | 0.185 | 0.225 | 0.228 | 0.272 | 0.265 | 0.285 | 0.231 | 0.27 | 0.259 | 0.221 | 0.213 | 0.213 | 0.236 | 0.212 | 0.206 | 0.219 | 0.235 | 0.214 | 0.21 | 0.228 | 0.194 | 0.2 | 0.233 | 0.203 | 0.227 | 0.216 | 0.214 | 0.208 | 0.192 | 0.203 | 0.226 | 0.21 | 0.209 | 0.215 | 0.215 | 0.2 | 0.222 | 0.232 | 0.208 | 0.239 | 0.229 | 0.218 | 0.187 | 0.23 | 0.222 | 0.223 | 0.202 | 0.214 | 0.211 | 0.216 | 0.214 | 0.214 | 0.204 | 0.211 | 0.218 | 0.211 | 0.213 | 0.222 | 0.244 | 0.221 | 0.208 | 0.214 | 0.198 | 0.191 | 0.244 | 0.212 | 0.211
|  | R | RF | 0.231 | 0.194 | 0.231 | 0.222 | 0.232 | 0.269 | 0.262 | 0.233 | 0.227 | 0.267 | 0.222 | 0.219 | 0.219 | 0.216 | 0.224 | 0.224 | 0.22 | 0.213 | 0.198 | 0.219 | 0.214 | 0.217 | 0.209 | 0.21 | 0.216 | 0.213 | 0.202 | 0.213 | 0.225 | 0.214 | 0.232 | 0.21 | 0.233 | 0.21 | 0.175 | 0.211 | 0.21 | 0.23 | 0.225 | 0.224 | 0.206 | 0.227 | 0.213 | 0.18 | 0.207 | 0.212 | 0.204 | 0.202 | 0.225 | 0.207 | 0.209 | 0.207 | 0.217 | 0.197 | 0.199 | 0.226 | 0.212 | 0.223 | 0.222 | 0.241 | 0.178 | 0.196 | 0.214 | 0.204 | 0.186 | 0.211 | 0.212 | 0.207
A |  | L | 0.225 | 0.218 | RF | 0.227 | 0.235 | 0.232 | 0.276 | 0.267 | 0.253 | 0.267 | 0.27 | 0.21 | 0.218 | 0.213 | 0.218 | 0.218 | 0.214 | 0.221 | 0.224 | 0.211 | 0.213 | 0.215 | 0.206 | 0.216 | 0.204 | 0.211 | 0.197 | 0.217 | 0.213 | 0.216 | 0.208 | 0.174 | 0.227 | 0.207 | 0.204 | 0.195 | 0.226 | 0.225 | 0.207 | 0.232 | 0.219 | 0.222 | 0.23 | 0.221 | 0.224 | 0.234 | 0.222 | 0.227 | 0.227 | 0.214 | 0.22 | 0.21 | 0.2 | 0.197 | 0.21 | 0.206 | 0.223 | 0.212 | 0.202 | 0.199 | 0.197 | 0.187 | 0.199 | 0.195 | 0.163 | 0.191 | 0.194 | 0.192 | 0.245
0.083 | -54 IN | C | 0.225 | RF | 0.228 | 0.224 | 0.227 | 0.244 | 0.271 | 0.261 | 0.241 | 0.261 | 0.284 | 0.216 | 0.219 | 0.223 | 0.241 | 0.215 | 0.225 | 0.213 | 0.221 | 0.212 | 0.237 | 0.219 | 0.211 | 0.214 | 0.226 | 0.228 | 0.214 | 0.228 | 0.211 | 0.209 | 0.213 | 0.178 | 0.234 | 0.221 | 0.22 | 0.221 | 0.211 | 0.214 | 0.22 | 0.221 | 0.201 | 0.213 | 0.223 | 0.221 | 0.219 | 0.212 | 0.194 | 0.214 | 0.221 | 0.209 | 0.214 | 0.227 | 0.206 | 0.209 | 0.21 | 0.206 | 0.198 | 0.213 | 0.213 | 0.204 | 0.172 | 0.172 | 0.217 | 0.21 | 0.184 | 0.163 | 0.179 | 0.194 | 0.217
|  | R | 0.225 | 0.226 | 0.229 | 0.219 | 0.223 | 0.273 | 0.268 | 0.25 | 0.25 | 0.252 | 0.261 | 0.228 | 0.218 | 0.217 | 0.226 | 0.216 | 0.216 | 0.221 | 0.24 | 0.214 | 0.218 | 0.218 | 0.217 | 0.208 | 0.243 | 0.221 | 0.215 | 0.22 | 0.215 | 0.195 | 0.221 | 0.201 | 0.217 | 0.235 | 0.212 | 0.221 | 0.207 | 0.219 | 0.206 | 0.213 | 0.207 | 0.227 | 0.216 | 0.203 | 0.214 | 0.214 | 0.185 | 0.188 | 0.206 | 0.188 | 0.211 | 0.216 | 0.205 | 0.211 | 0.204 | 0.194 | 0.212 | 0.214 | 0.182 | 0.203 | 0.183 | 0.197 | 0.19 | 0.188 | 0.154 | 0.179 | 0.197 | 0.206 | 0.206
A | POSITION 'A' | L |  |  | 0.219 | 0.209 |  | 0.233 | 0.266 |  | 0.247 | 0.243 |  | 0.229 | 0.21 |  | 0.219 | 0.203 |  | 0.219 | 0.2 |  | 0.203 | 0.197 |  | 0.206 | 0.195 |  | 0.196 | 0.203 |  | 0.219 | 0.196 |  | 0.2 | 0.196 |  | 0.201 | 0.191 |  | 0.209 | 0.198 |  | 0.208 | 0.21 |  | 0.217 | 0.214 |  | 0.198 | 0.195 |  | 0.219 | 0.204 |  | 0.232 | 0.191 |  | 0.223 | 0.214 |  | 0.207 | 0.206 |  | 0.21 | 0.212 |  | 0.217 | 0.215
0.083 | OF THE | C |  |  | 0.218 | 0.205 |  | 0.241 | 0.253 |  | 0.248 | 0.251 |  | 0.204 | 0.207 |  | 0.223 | 0.195 |  | 0.206 | 0.207 |  | 0.191 | 0.202 |  | 0.198 | 0.209 |  | 0.197 | 0.19 |  | 0.212 | 0.202 |  | 0.199 | 0.191 |  | 0.21 | 0.209 |  | 0.207 | 0.206 |  | 0.208 | 0.204 |  | 0.21 | 0.221 |  | 0.211 | 0.197 |  | 0.201 | 0.201 |  | 0.224 | 0.208 |  | 0.217 | 0.207 |  | 0.2 | 0.195 |  | 0.202 | 0.215 |  | 0.215 | 0.22
| PRIMARIES | R |  |  | 0.224 | 0.218 |  | 0.244 | 0.243 |  | 0.224 | 0.244 |  | 0.19 | 0.205 |  | 0.206 | 0.2 |  | 0.21 | 0.224 |  | 0.193 | 0.201 |  | 0.194 | 0.208 |  | 0.197 | 0.203 |  | 0.223 | 0.199 |  | 0.177 | 0.207 |  | 0.191 | 0.194 |  | 0.209 | 0.193 |  | 0.187 | 0.198 |  | 0.197 | 0.202 |  | 0.2 | 0.22 |  | 0.204 | 0.199 |  | 0.211 | 0.217 |  | 0.211 | 0.202 |  | 0.212 | 0.204 |  | 0.217 | 0.211 |  | 0.202 | 0.225
A | POSITION 'B' | L |  |  | 0.21 | 0.182 |  | 0.238 | 0.249 |  | 0.227 | 0.237 |  | 0.201 | 0.2 |  | 0.207 | 0.193 |  | 0.191 | 0.211 |  | 0.183 | 0.206 |  | 0.195 | 0.194 |  | 0.186 | 0.18 |  | 0.199 | 0.191 |  | 0.203 | 0.198 |  | 0.191 | 0.196 |  | 0.188 | 0.202 |  | 0.229 | 0.2 |  | 0.2 | 0.207 |  | 0.201 | 0.191 |  | 0.211 | 0.198 |  | 0.181 | 0.209 |  | 0.196 | 0.201 |  | 0.2 | 0.193 |  | 0.22 | 0.196 |  | 0.196 | 0.207
0.083 | OF THE | C |  |  | 0.203 | 0.191 |  | 0.236 | 0.247 |  | 0.219 | 0.202 |  | 0.205 | 0.183 |  | 0.202 | 0.195 |  | 0.201 | 0.232 |  | 0.193 | 0.213 |  | 0.215 | 0.202 |  | 0.184 | 0.206 |  | 0.193 | 0.203 |  | 0.208 | 0.205 |  | 0.188 | 0.196 |  | 0.192 | 0.201 |  | 0.2 | 0.206 |  | 0.212 | 0.205 |  | 0.22 | 0.182 |  | 0.205 | 0.217 |  | 0.175 | 0.194 |  | 0.187 | 0.198 |  | 0.205 | 0.188 |  | 0.221 | 0.218 |  | 0.182 | 0.192
| PRIMARIES | R |  |  | 0.196 | 0.209 |  | 0.232 | 0.243 |  | 0.234 | 0.244 |  | 0.199 | 0.205 |  | 0.21 | 0.192 |  | 0.195 | 0.221 |  | 0.194 | 0.202 |  | 0.185 | 0.187 |  | 0.197 | 0.196 |  | 0.2 | 0.203 |  | 0.202 | 0.212 |  | 0.2 | 0.177 |  | 0.173 | 0.216 |  | 0.19 | 0.188 |  | 0.21 | 0.199 |  | 0.207 | 0.203 |  | 0.21 | 0.198 |  | 0.183 | 0.199 |  | 0.204 | 0.192 |  | 0.201 | 0.196 |  | 0.192 | 0.22 |  | 0.191 | 0.201
A | POSITION 'C' | L |  |  | 0.152 | 0.207 |  | 0.214 | 0.246 |  | 0.225 | 0.228 |  | 0.214 | 0.194 |  | 0.181 | 0.202 |  | 0.188 | 0.192 |  | 0.198 | 0.197 |  | 0.179 | 0.207 |  | 0.179 | 0.203 |  | 0.187 | 0.209 |  | 0.202 | 0.196 |  | 0.192 | 0.179 |  | 0.198 | 0.202 |  | 0.217 | 0.196 |  | 0.182 | 0.215 |  | 0.226 | 0.193 |  | 0.208 | 0.187 |  | 0.17 | 0.192 |  | 0.201 | 0.194 |  | 0.2 | 0.188 |  | 0.194 | 0.205 |  | 0.198 | 0.208
0.083 | OF THE | C |  |  | 0.142 | 0.158 |  | 0.227 | 0.193 |  | 0.211 | 0.24 |  | 0.188 | 0.187 |  | 0.194 | 0.189 |  | 0.195 | 0.186 |  | 0.191 | 0.21 |  | 0.188 | 0.194 |  | 0.195 | 0.197 |  | 0.179 | 0.194 |  | 0.18 | 0.194 |  | 0.177 | 0.185 |  | 0.197 | 0.189 |  | 0.197 | 0.196 |  | 0.171 | 0.197 |  | 0.211 | 0.182 |  | 0.212 | 0.198 |  | 0.178 | 0.192 |  | 0.176 | 0.185 |  | 0.187 | 0.187 |  | 0.168 | 0.214 |  | 0.2 | 0.188
| PRIMARIES | R |  |  | 0.177 | 0.202 |  | 0.245 | 0.215 |  | 0.216 | 0.256 |  | 0.187 | 0.214 |  | 0.204 | 0.192 |  | 0.199 | 0.197 |  | 0.2 | 0.198 |  | 0.184 | 0.203 |  | 0.196 | 0.189 |  | 0.189 | 0.189 |  | 0.18 | 0.214 |  | 0.184 | 0.173 |  | 0.186 | 0.194 |  | 0.194 | 0.193 |  | 0.181 | 0.19 |  | 0.18 | 0.19 |  | 0.197 | 0.187 |  | 0.16 | 0.203 |  | 0.179 | 0.175 |  | 0.191 | 0.179 |  | 0.189 | 0.207 |  | 0.196 | 0.231
A |  | L | 0.228 | 0.216 | 0.248 | 0.21 | 0.194 | 0.242 | 0.256 | 0.221 | 0.264 | 0.237 | 0.256 | 0.204 | 0.204 | 0.223 | 0.189 | 0.192 | 0.208 | 0.215 | 0.227 | 0.19 | 0.206 | 0.216 | 0.21 | 0.21 | 0.214 | 0.179 | 0.218 | 0.216 | 0.214 | 0.219 | 0.193 | 0.205 | 0.214 | 0.215 | 0.206 | 0.201 | 0.202 | 0.196 | 0.218 | 0.224 | 0.229 | 0.218 | 0.222 | 0.213 | 0.214 | 0.213 | 0.206 | 0.195 | 0.195 | 0.156 | 0.194 | 0.211 | 0.229 | 0.152 | 0.226 | 0.224 | 0.211 | 0.212 | 0.207 | 0.2 | 0.213 | 0.227 | 0.205 | 0.204 | 0.228 | 0.175 | 0.22 | 0.196 | RF
0.083 | -63 IN | C | 0.278 | 0.222 | 0.218 | 0.198 | 0.195 | 0.251 | 0.286 | 0.248 | 0.247 | 0.231 | 0.254 | 0.197 | 0.21 | 0.208 | 0.214 | 0.224 | 0.193 | 0.209 | 0.23 | 0.192 | 0.222 | 0.153 | 0.218 | 0.222 | 0.219 | 0.213 | 0.215 | 0.204 | 0.171 | 0.212 | 0.207 | 0.212 | 0.206 | 0.205 | 0.214 | 0.182 | 0.203 | 0.181 | 0.205 | 0.217 | 0.183 | 0.222 | 0.213 | 0.213 | 0.189 | 0.214 | 0.234 | 0.222 | 0.206 | 0.216 | 0.203 | 0.195 | 0.208 | 0.2 | 0.217 | 0.213 | 0.193 | 0.2 | 0.206 | 0.224 | 0.199 | 0.228 | 0.163 | 0.186 | 0.209 | 0.179 | 0.212 | 0.195 | 0.202
|  | R | 0.195 | 0.177 | 0.195 | 0.212 | 0.195 | 0.198 | 0.263 | 0.229 | 0.244 | 0.264 | 0.233 | 0.186 | 0.21 | 0.202 | 0.202 | 0.217 | 0.181 | 0.209 | 0.234 | 0.181 | 0.215 | 0.208 | 0.232 | 0.224 | 0.216 | 0.21 | 0.22 | 0.198 | 0.214 | 0.21 | 0.208 | 0.214 | 0.207 | 0.219 | 0.193 | 0.192 | 0.167 | 0.217 | 0.209 | 0.19 | 0.177 | 0.213 | 0.191 | 0.201 | 0.203 | 0.199 | 0.211 | 0.213 | 0.205 | 0.191 | 0.203 | 0.21 | 0.185 | 0.214 | 0.197 | 0.223 | 0.202 | 0.185 | 0.21 | 0.207 | 0.19 | 0.186 | 0.186 | 0.185 | 0.199 | 0.188 | 0.175 | 0.198 | 0.215
A |  | L | 0.222 | 0.197 | 0.208 | 0.232 | 0.177 | 0.225 | 0.257 | 0.25 | 0.233 | 0.252 | 0.221 | 0.175 | 0.205 | 0.226 | 0.192 | 0.17 | 0.129 | 0.205 | 0.202 | 0.169 | 0.206 | 0.212 | 0.171 | 0.2 | 0.183 | 0.169 | 0.177 | 0.187 | 0.188 | 0.22 | 0.203 | 0.226 | 0.196 | 0.23 | 0.177 | 0.171 | 0.203 | 0.194 | 0.198 | 0.205 | 0.176 | 0.225 | 0.132 | 0.22 | 0.176 | 0.216 | 0.209 | 0.203 | 0.181 | 0.231 | 0.206 | 0.202 | 0.23 | 0.2 | 0.204 | 0.226 | 0.236 | 0.194 | 0.23 | 0.243 | 0.189 | 0.192 | 0.22 | 0.185 | 0.202 | 0.193 | 0.197 | 0.203 | 0.176
0.083 | -72 IN | C | 0.203 | 0.182 | 0.194 | 0.184 | 0.202 | 0.247 | 0.22 | 0.227 | 0.236 | 0.211 | 0.242 | 0.168 | 0.207 | 0.181 | 0.193 | 0.193 | 0.181 | 0.221 | 0.212 | 0.173 | 0.184 | 0.211 | 0.197 | 0.213 | 0.185 | 0.211 | 0.186 | 0.189 | 0.143 | 0.209 | 0.197 | 0.181 | 0.185 | 0.177 | 0.193 | 0.188 | 0.209 | 0.201 | 0.209 | 0.236 | 0.18 | 0.195 | 0.184 | 0.207 | 0.199 | 0.214 | 0.205 | 0.224 | 0.192 | 0.213 | 0.207 | 0.214 | 0.206 | 0.198 | 0.203 | 0.222 | 0.227 | 0.199 | 0.232 | 0.224 | 0.187 | 0.165 | 0.24 | 0.206 | 0.22 | 0.215 | 0.195 | 0.172 | 0.193
|  | R | 0.232 | 0.199 | 0.202 | 0.195 | 0.19 | 0.237 | 0.226 | 0.241 | 0.245 | 0.225 | 0.234 | 0.197 | 0.153 | 0.195 | 0.181 | 0.179 | 0.149 | 0.206 | 0.204 | 0.176 | 0.197 | 0.226 | 0.166 | 0.209 | 0.199 | 0.114 | 0.191 | 0.201 | 0.158 | 0.201 | 0.182 | 0.189 | 0.189 | 0.207 | 0.178 | 0.19 | 0.197 | 0.2 | 0.179 | 0.223 | 0.19 | 0.192 | 0.192 | 0.216 | 0.207 | 0.217 | 0.207 | 0.224 | 0.195 | 0.211 | 0.199 | 0.215 | 0.218 | 0.202 | 0.24 | 0.216 | 0.224 | 0.176 | 0.233 | 0.207 | 0.14 | 0.188 | 0.206 | 0.202 | 0.16 | 0.202 | 0.216 | 0.19 | 0.191
A |  | L | 0.129 | 0.208 | 0.14 | 0.201 | 0.178 | 0.243 | 0.215 | 0.23 | 0.191 | 0.233 | 0.239 | 0.183 | 0.183 | 0.204 | 0.21 | 0.193 | 0.203 | 0.148 | 0.194 | 0.201 | 0.172 | 0.211 | 0.206 | 0.204 | 0.198 | 0.229 | 0.194 | 0.2 | 0.195 | 0.193 | 0.188 | 0.199 | 0.213 | 0.171 | 0.205 | 0.22 | 0.194 | 0.187 | 0.218 | 0.214 | 0.227 | 0.209 | 0.209 | 0.211 | 0.196 | 0.215 | 0.21 | 0.223 | 0.226 | 0.22 | 0.213 | 0.227 | 0.23 | 0.208 | 0.213 | 0.229 | 0.221 | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST
0.083 | -81 IN | C | 0.214 | 0.24 | 0.208 | 0.227 | 0.211 | 0.227 | 0.245 | 0.227 | 0.222 | 0.239 | 0.246 | 0.179 | 0.182 | 0.209 | 0.193 | 0.197 | 0.221 | 0.188 | 0.21 | 0.182 | 0.227 | 0.217 | 0.196 | 0.225 | 0.211 | 0.205 | 0.213 | 0.195 | 0.218 | 0.19 | 0.189 | 0.214 | 0.206 | 0.194 | 0.188 | 0.202 | 0.192 | 0.202 | 0.227 | 0.221 | 0.217 | 0.219 | 0.207 | 0.221 | 0.203 | 0.23 | 0.218 | 0.238 | 0.223 | 0.214 | 0.226 | 0.211 | 0.23 | 0.217 | 0.212 | 0.219 | 0.219 | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST
|  | R | 0.217 | 0.235 | 0.204 | 0.224 | 0.209 | 0.239 | 0.222 | 0.223 | 0.224 | 0.243 | 0.254 | 0.217 | 0.212 | 0.209 | 0.228 | 0.196 | 0.198 | 0.19 | 0.197 | 0.194 | 0.211 | 0.208 | 0.178 | 0.208 | 0.228 | 0.234 | 0.213 | 0.225 | 0.212 | 0.209 | 0.193 | 0.243 | 0.216 | 0.194 | 0.182 | 0.208 | 0.233 | 0.192 | 0.22 | 0.198 | 0.213 | 0.22 | 0.189 | 0.215 | 0.211 | 0.226 | 0.209 | 0.237 | 0.227 | 0.206 | 0.205 | 0.234 | 0.226 | 0.246 | 0.215 | 0.231 | 0.218 | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST
A |  | L | 0.183 | 0.202 | 0.192 | 0.252 | 0.192 | 0.237 | 0.251 | 0.224 | 0.243 | 0.268 | 0.244 | 0.233 | 0.2 | 0.23 | 0.237 | 0.211 | 0.211 | 0.186 | 0.211 | 0.233 | 0.195 | 0.207 | 0.222 | 0.232 | 0.206 | 0.172 | 0.221 | 0.223 | 0.221 | 0.221 | 0.219 | 0.243 | 0.201 | 0.222 | 0.22 | 0.224 | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST
0.083 | -90 IN | C | 0.161 | 0.206 | 0.21 | 0.236 | 0.175 | 0.274 | 0.243 | 0.2 | 0.238 | 0.245 | 0.236 | 0.225 | 0.192 | 0.24 | 0.228 | 0.211 | 0.217 | 0.216 | 0.235 | 0.162 | 0.21 | 0.221 | 0.228 | 0.241 | 0.236 | 0.225 | 0.221 | 0.165 | 0.221 | 0.222 | 0.208 | 0.232 | 0.221 | 0.223 | 0.216 | 0.226 | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST
|  | R | 0.208 | 0.223 | 0.215 | 0.227 | 0.179 | 0.233 | 0.255 | 0.241 | 0.273 | 0.239 | 0.238 | 0.225 | 0.191 | 0.232 | 0.23 | 0.214 | 0.215 | 0.211 | 0.234 | 0.22 | 0.217 | 0.229 | 0.23 | 0.224 | 0.218 | 0.214 | 0.221 | 0.228 | 0.225 | 0.227 | 0.229 | 0.235 | 0.223 | 0.218 | 0.202 | 0.224 | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MIN
A | 0.001-0.083 | 0.140-0.149 | 10: OUTSIDE DIAMETER:; 23: 3; 30: FUTURE PROJECTION; 67: APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | 0.100-0.109 | 0.150-0.159 | 10: TUBE MATERIAL:; 23: SA-210A1; 35: MAX. THICKNESS
| 0.110-0.119 | 0.160-0.169 | 10: NOMINAL WALL:; 23: 0.203; 35: AVG. THICKNESS |  |  | PROJECTED TUBE WALL THICKNESS - 5 YEARS
| 0.120-0.129 | 0.170-0.179 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS
| 0.130-0.139 | 0.180-0.999 | 10: MILL FLAG:; 23: 0.1; 35: STD DEV.
PROJECTION
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Retirement
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. | [70 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69
A |  | Year | Oct 2038 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2035 | Jan 2044 | Dec 2042 | May 2055 | Nov 2051 | May 2055 | May 2055 | Jul 2044 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Dec 2040 | Jul 2053 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2043 | May 2055 | May 2049 | May 2055 | ND | ND | ND | May 2055 | Mar 2052 | Jun 2050 | May 2039 | May 2055 | ND | ND | Dec 2049 | May 2055 | ND | ND | ND | Jan 2046 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Jul 2054 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055
+16 FT 6 IN
A |  | Year | ND | May 2055 | May 2055 | May 2055 | May 2049 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2034 | Jun 2041 | May 2055 | Jun 2044 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Nov 2054 | Dec 2043 | May 2055 | Jan 2052 | May 2055 | May 2055 | Apr 2050 | May 2055 | May 2055 | May 2055 | Jun 2054 | May 2055 | May 2055 | Oct 2052 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2049 | May 2055 | Jul 2046 | May 2055 | May 2043 | Sep 2042 | Nov 2048 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND
+15 FT
A |  | Year | Jun 2032 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | Jan 2051 | May 2055 | May 2055 | Jul 2035 | May 2055 | May 2055 | May 2055 | Sep 2052 | May 2055 | May 2052 | May 2055 | May 2055 | Jan 2055 | Apr 2046 | Aug 2052 | Nov 2039 | Jun 2046 | May 2055 | Apr 2033 | Jan 2035 | Jan 2032 | May 2055 | Oct 2044 | May 2055 | May 2055 | Nov 2049 | Dec 2032 | May 2055 | Apr 2031 | Dec 2043 | Jan 2041 | Apr 2036 | Dec 2030 | Jul 2043 | Sep 2033 | Apr 2039 | Dec 2039 | Aug 2037 | Jun 2042 | May 2055 | Oct 2032 | May 2055 | Jun 2044 | Jan 2048 | Jul 2042 | May 2055 | May 2055 | Sep 2033 | Oct 2035 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2046 | May 2055 | May 2055 | Dec 2050 | Jan 2050 | ND
+13 FT 6 IN
A |  | Year | Feb 2031 | May 2055 | May 2055 | May 2055 | May 2055 | Nov 2047 | May 2055 | May 2055 | May 2055 | Dec 2048 | Nov 2043 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Nov 2039 | ND | Mar 2045 | Dec 2050 | May 2055 | Jul 2034 | Jan 2036 | May 2043 | Jun 2041 | Dec 2037 | Jun 2047 | Jun 2036 | May 2055 | May 2055 | Feb 2032 | Sep 2046 | Jun 2049 | May 2055 | Apr 2052 | May 2055 | Apr 2050 | Jul 2045 | Oct 2037 | May 2032 | Dec 2036 | Apr 2035 | Jun 2041 | Mar 2035 | Mar 2038 | Apr 2045 | May 2055 | Mar 2048 | Nov 2035 | Jul 2054 | Dec 2033 | Mar 2045 | Nov 2042 | Mar 2038 | Jun 2042 | Dec 2046 | May 2055 | Apr 2054 | Nov 2045 | Nov 2039 | May 2055 | May 2055 | May 2055 | Feb 2053 | Aug 2047 | May 2055 | May 2055 | May 2055 | May 2049
+12 FT
A | POSITION 'A' | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | Jul 2053 | May 2055 | ND
OF THE
OB PORTS
A | POSITION 'B' | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND
OF THE
OB PORTS
A | POSITION 'C' | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND
OF THE
OB PORTS
A |  | Year | Nov 2050 | May 2055 | ND | May 2055 | May 2055 | Jun 2026 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2046 | Jan 2041 | May 2055 | Jun 2048 | May 2055 | May 2055 | Sep 2047 | Apr 2046 | May 2055 | Apr 2041 | Apr 2039 | May 2055 | Feb 2040 | May 2055 | May 2031 | May 2055 | Dec 2037 | May 2055 | May 2055 | Oct 2046 | May 2055 | May 2055 | ND | Jan 2043 | Nov 2045 | Feb 2034 | Sep 2038 | Feb 2049 | Mar 2037 | Oct 2030 | Jan 2047 | Nov 2040 | Dec 2038 | Feb 2038 | Jun 2055 | May 2055 | Jan 2054 | Jul 2042 | Feb 2044 | May 2041 | May 2055 | May 2047 | Jul 2036 | May 2055 | May 2055 | Nov 2048 | Jun 2047 | Feb 2051 | May 2055 | May 2055 | May 2055 | Sep 2053 | May 2055 | May 2055 | Sep 2051 | May 2055 | Jul 2029
+10 FT 6 IN
A | POSITION 'A' | Year | ND | ND | ND | May 2055 | May 2055 | ND | May 2055 | ND | ND | May 2055 | ND | Oct 2048 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | Mar 2052 | May 2055 | Nov 2053 | May 2055 | Jun 2034 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE MANWAY
& OSCILLATOR
A | POSITION 'B' | Year | ND | ND | ND | May 2055 | May 2055 | ND | Jul 2046 | ND | ND | May 2055 | ND | Apr 2049 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | Nov 2035 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE MANWAY
& OSCILLATOR
A | POSITION 'C' | Year | ND | ND | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | Mar 2048 | Jan 2048 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE MANWAY
& OSCILLATOR
A | POSITION 'D' | Year | ND | ND | ND | May 2055 | May 2055 | ND | ND | May 2041 | May 2055 | May 2055 | ND | Jun 2046 | Jun 2048 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | Oct 2052 | Sep 2038 | Apr 2030 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE MANWAY
& OSCILLATOR
A | POSITION 'E' | Year | ND | ND | ND | May 2055 | May 2055 | Nov 2038 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Dec 2047 | May 2055 | Sep 2053 | May 2055 | Jul 2045 | May 2031 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE MANWAY
& OSCILLATOR
A |  | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2031 | ND | Feb 2051 | May 2055 | ND | ND | May 2055 | May 2055 | Jan 2047 | ND | May 2055 | ND | May 2055 | May 2055 | Jun 2054 | Mar 2034 | Mar 2054 | Oct 2037 | Aug 2033 | Apr 2049 | Dec 2033 | May 2055 | Dec 2032 | Dec 2037 | Jan 2038 | May 2043 | Jan 2053 | Nov 2046 | May 2055 | May 2055 | May 2055 | May 2032 | Sep 2035 | ND | Sep 2044 | Dec 2051 | Dec 2039 | Sep 2033 | Jul 2046 | Apr 2039 | Jun 2046 | Jul 2034 | Nov 2033 | Dec 2049 | Aug 2050 | May 2055 | Aug 2038 | May 2055 | May 2039 | Apr 2049 | Sep 2041 | Jun 2047 | Nov 2040 | May 2055 | May 2055 | Nov 2035 | Aug 2044 | May 2055 | May 2055 | Oct 2044 | May 2055 | May 2055 | Apr 2051 | Feb 2029
+9 FT
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | Nov 2052 | Sep 2039 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Dec 2054 | Dec 2035 | May 2055 | May 2055 | May 2055 | Jan 2049 | May 2055 | Mar 2052 | Oct 2047 | Feb 2036 | Mar 2037 | Jan 2035 | Sep 2032 | Feb 2031 | May 2035 | Jul 2034 | Aug 2040 | ND | May 2055 | Apr 2036 | Jan 2035 | May 2055 | Mar 2050 | May 2055 | May 2055 | Aug 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2052 | May 2055 | Sep 2045 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2044 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Feb 2026
+7 FT 6 IN
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | May 2055 | May 2055 | Aug 2043 | Dec 2035 | Sep 2036 | Sep 2036 | Feb 2037 | Apr 2033 | May 2055 | Sep 2034 | Feb 2033 | Oct 2032 | May 2055 | Aug 2040 | ND | Apr 2050 | Oct 2036 | Jun 2037 | ND | May 2055 | May 2055 | May 2055 | Jul 2040 | May 2055 | Jun 2033 | May 2055 | May 2055 | ND | Mar 2046 | May 2055 | Apr 2037 | Jul 2048 | May 2055 | May 2055 | ND | ND | ND | ND | Dec 2042 | May 2055 | ND | May 2055 | Aug 2046 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | Apr 2041 | ND | Sep 2045 | ND | May 2055 | May 2055 | Feb 2046 | May 2055
+6 FT
A |  | Year | Nov 2037 | May 2055 | Jun 2047 | Sep 2048 | Nov 2054 | May 2055 | May 2055 | May 2055 | Mar 2053 | May 2055 | May 2055 | Oct 2051 | Apr 2042 | Oct 2047 | Jan 2047 | Feb 2050 | Aug 2039 | Apr 2037 | May 2055 | Sep 2042 | ND | Jul 2048 | Sep 2046 | Jan 2045 | May 2055 | Dec 2046 | May 2055 | May 2055 | Dec 2044 | May 2051 | Jan 2045 | May 2055 | May 2055 | Oct 2046 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | Jul 2042 | Mar 2053 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | Apr 2038 | May 2055 | May 2055 | May 2055 | Aug 2039 | Apr 2036
+4 FT 6 IN
A |  | Year | May 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2051 | ND | ND | May 2055 | May 2055 | May 2055 | Sep 2041 | May 2055 | Jan 2039 | Apr 2041 | May 2055 | Nov 2040 | Jul 2042 | ND | ND | Aug 2039 | Dec 2046 | May 2055 | Nov 2040 | Feb 2055 | May 2055 | May 2055 | ND | Oct 2045 | Jun 2035 | Feb 2038 | May 2055 | Aug 2052 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2040 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2046 | Sep 2052 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2048 | Aug 2048 | May 2055 | May 2055 | May 2055
+3 FT
A |  | Year | Aug 2030 | Nov 2046 | May 2055 | Jul 2039 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2050 | May 2055 | May 2055 | May 2055 | Apr 2041 | May 2055 | May 2055 | Aug 2053 | Jul 2054 | May 2055 | Oct 2046 | May 2055 | Aug 2041 | May 2055 | ND | May 2055 | Sep 2037 | May 2055 | May 2055 | Nov 2043 | Sep 2042 | Mar 2048 | May 2055 | Jun 2047 | May 2051 | May 2050 | May 2054 | Jul 2049 | Mar 2040 | Jan 2055 | Oct 2052 | Jun 2051 | Oct 2048 | Nov 2044 | Jun 2049 | Jan 2054 | Nov 2039 | May 2055 | Apr 2050 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Nov 2047 | May 2055 | ND | May 2055
+1 FT 6 IN
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | Dec 2049 | Jul 2050 | ND | May 2055 | Aug 2047 | ND | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Dec 2046 | May 2055 | May 2055 | Aug 2044 | ND | ND | ND | ND | May 2055 | ND | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | ND
0 REFERENCE
A | POSITION 'A' | Year | ND | May 2055 | ND | Nov 2051 | Aug 2042 | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2054 | Aug 2053 | Sep 2051 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | Apr 2055 | May 2055 | Jun 2049 | May 2055 | ND | ND | ND | ND | ND | ND | ND | May 2055 | Mar 2041 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Jun 2052 | Jul 2051 | May 2055 | ND | ND | Jan 2050 | Dec 2045 | Dec 2047 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | May 2055 | Jul 2039 | May 2055 | May 2055 | Nov 2052 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
SECONDARIES
A | POSITION 'B' | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | May 2055 | Feb 2054 | Jun 2053 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | Mar 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | May 2055 | Mar 2048 | May 2055 | May 2055 | Feb 2049 | Jun 2039 | ND | ND | ND | May 2055 | May 2055 | Jan 2054 | May 2055 | May 2055 | Mar 2050 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
SECONDARIES
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | Jan 2037 | ND | ND | ND | May 2055 | ND | May 2055 | ND | May 2055 | ND | ND | May 2055 | ND | ND | May 2055 | May 2055 | Jul 2054 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Jan 2036 | ND | ND | May 2055 | Jun 2046 | Aug 2049 | Mar 2048 | May 2055 | May 2055 | May 2055 | Jan 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2041 | May 2055 | Sep 2037 | Jun 2046 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | Jun 2045 | Apr 2044 | May 2055 | ND | Jul 2036 | ND
-9 IN
A | POSITION 'C' | Year | ND | May 2055 | ND | May 2055 | Jul 2038 | Dec 2042 | May 2055 | ND | ND | ND | May 2055 | May 2055 | Aug 2053 | Dec 2043 | May 2055 | May 2055 | ND | ND | May 2055 | Sep 2051 | Jan 2040 | Jul 2045 | May 2055 | Nov 2051 | ND | ND | ND | ND | ND | ND | ND | May 2055 | Mar 2045 | May 2055 | May 2055 | ND | May 2055 | May 2055 | Jan 2047 | Oct 2035 | May 2055 | May 2055 | ND | ND | Feb 2049 | Oct 2053 | May 2040 | May 2055 | Dec 2044 | May 2055 | ND | ND | ND | May 2055 | Apr 2044 | Jul 2039 | Feb 2035 | Apr 2055 | Mar 2052 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
SECONDARIES
A |  | Year | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Mar 2037 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Mar 2050 | Jan 2055 | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | ND | Jan 2042 | Jan 2052 | May 2055 | Jun 2038 | May 2055 | Nov 2036 | May 2055
-18 IN
A |  | Year | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Jun 2045 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2038 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | Dec 2033 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Mar 2040
-27 IN
A |  | Year | May 2055 | Aug 2046 | Dec 2043 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2055 | May 2055 | Oct 2040 | May 2055 | May 2055 | May 2055 | Feb 2051 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2054 | May 2055 | May 2052 | Apr 2044
-36 IN
A |  | Year | Nov 2032 | May 2055 | Dec 2046 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2047 | May 2055 | May 2055 | Apr 2045 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | Oct 2054 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2051 | May 2055 | May 2055 | May 2055 | Jul 2050 | May 2055 | May 2055 | May 2055
-45 IN
A |  | Year | ND | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2045 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Jan 2054 | Aug 2051 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Mar 2048 | Sep 2049 | May 2055 | Oct 2054 | Apr 2039 | Sep 2042 | Jan 2051 | Nov 2054 | May 2055
-54 IN
A | POSITION 'A' | Year | ND | ND | ND | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | Jun 2047 | May 2055 | ND | May 2055 | Mar 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND
OF THE
PRIMARIES
A | POSITION 'B' | Year | ND | ND | Feb 2055 | Oct 2048 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | Jun 2053 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | Oct 2054 | May 2055 | ND | Jun 2050 | Apr 2054 | ND | Oct 2050 | Oct 2047 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | Nov 2047 | ND | Aug 2048 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | Apr 2055 | ND | May 2055 | May 2055 | ND | Nov 2047 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND
OF THE
PRIMARIES
A | POSITION 'C' | Year | ND | ND | Jul 2036 | Aug 2041 | ND | Feb 2052 | Sep 2043 | ND | Feb 2051 | May 2055 | ND | Jan 2054 | May 2055 | ND | Jan 2051 | Jun 2054 | ND | May 2055 | Jun 2054 | ND | May 2055 | May 2055 | ND | Oct 2048 | May 2055 | ND | Jul 2049 | May 2055 | ND | Dec 2045 | May 2055 | ND | Jan 2047 | May 2055 | ND | Mar 2047 | May 2047 | ND | Jun 2051 | Oct 2053 | ND | May 2055 | May 2055 | ND | Jan 2044 | May 2055 | ND | Nov 2047 | Nov 2050 | ND | May 2055 | May 2055 | ND | Jul 2041 | May 2055 | ND | Apr 2045 | Jun 2047 | ND | Dec 2054 | Nov 2054 | ND | Aug 2047 | May 2055 | ND | May 2055 | May 2055 | ND | ND
OF THE
PRIMARIES
A |  | Year | May 2055 | Dec 2045 | May 2055 | May 2055 | May 2055 | Nov 2041 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2051 | May 2055 | ND | Jul 2052 | May 2055 | Aug 2036 | May 2055 | May 2055 | May 2055 | Jan 2055 | May 2055 | May 2055 | Nov 2043 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2050 | Dec 2043 | Oct 2054 | May 2055 | May 2055 | Apr 2049 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2039 | May 2055 | May 2055 | May 2055 | Jun 2037 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2047 | Mar 2051 | May 2055 | Jul 2049 | Jan 2045 | May 2055 | May 2055
-63 IN
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2042 | Apr 2037 | Aug 2052 | Feb 2049 | Oct 2043 | Apr 2034 | May 2055 | May 2055 | Apr 2045 | Feb 2051 | May 2055 | Feb 2040 | May 2055 | Jun 2052 | May 2032 | Oct 2048 | May 2055 | May 2036 | May 2055 | Aug 2054 | Nov 2054 | May 2055 | May 2055 | Oct 2048 | Sep 2047 | May 2055 | May 2055 | Nov 2047 | May 2055 | Aug 2050 | May 2055 | Mar 2034 | May 2055 | Jun 2052 | May 2055 | May 2055 | May 2055 | Nov 2050 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | Aug 2046 | ND | May 2055 | Aug 2035 | Apr 2042 | May 2055 | Oct 2054 | Aug 2039 | May 2055 | May 2055 | Aug 2043 | Mar 2046
-72 IN
A |  | Year | Apr 2034 | May 2055 | Dec 2034 | May 2055 | Jan 2045 | May 2055 | Oct 2047 | May 2055 | Sep 2041 | May 2055 | May 2055 | Feb 2051 | Jul 2050 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2037 | May 2055 | Apr 2054 | Sep 2045 | May 2055 | Feb 2046 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Mar 2045 | Apr 2054 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
-81 IN
A |  | Year | Oct 2040 | May 2055 | Dec 2052 | ND | Sep 2043 | May 2055 | May 2055 | May 2043 | May 2055 | May 2055 | May 2055 | ND | Jan 2051 | ND | ND | ND | ND | May 2055 | ND | May 2039 | May 2055 | May 2055 | ND | ND | May 2055 | Aug 2052 | ND | Feb 2044 | ND | ND | May 2055 | ND | May 2055 | ND | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
-90 IN
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69
| PROJECTED TO REACH TMIN: |  | 10: NOTE: CORROSION RATE IS BASED ON COMPARISON OF; 30: EARLIEST DATE OF PROJECTED RETIREMENT:; 67: APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | + 5 YEARS (or no data)
| WITHIN 5 YEARS |  | 10: 2020, 2022, 2023, 2024, 2025 | PROJECTED TUBE RETIREMENT DATE
| WITHIN 3 YEARS |  | 10: INSPECTION DATA; 30: February 2026
| WITHIN 1 YEAR |  | 10: ND; 15: NO COMPARISON DATA
RETIREMENT
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Low (hidden)
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. LOW THICKNESS MEASUREMENTS ARE IN INCHES. | [72 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MIN
A |  | LOWEST | bar: 1
0.083 | +16 FT 6 IN
A |  | LOWEST | bar: 1; 69
0.083 | +15 FT
A |  | LOWEST | bar: 1; 69
0.083 | +13 FT 6 IN
A |  | LOWEST | bar: 1
0.083 | +12 FT
A | POSITION 'A' | LOWEST
0.083 | OF THE
OB PORTS
A | POSITION 'B' | LOWEST
0.083 | OF THE
OB PORTS
A | POSITION 'C' | LOWEST
0.083 | OF THE
OB PORTS
A |  | LOWEST | bar: 6; 69
0.083 | +10 FT 6 IN
A | POSITION 'A' | LOWEST
0.083 | OF THE MANWAY
& OSCILLATOR
A | POSITION 'B' | LOWEST | bar: 6; 11
0.083 | OF THE MANWAY
& OSCILLATOR
A | POSITION 'C' | LOWEST | bar: 6 to 7; 10 to 11
0.083 | OF THE MANWAY
& OSCILLATOR
A | POSITION 'D' | LOWEST | bar: 6; 10 to 11
0.083 | OF THE MANWAY
& OSCILLATOR
A | POSITION 'E' | LOWEST
0.083 | OF THE MANWAY
& OSCILLATOR
A |  | LOWEST | bar: 6 to 7; 10 to 11; 69
0.083 | +9 FT
A |  | LOWEST | bar: 69
0.083 | +7 FT 6 IN
A |  | LOWEST
0.083 | +6 FT
A |  | LOWEST
0.083 | +4 FT 6 IN
A |  | LOWEST
0.083 | +3 FT
A |  | LOWEST
0.083 | +1 FT 6 IN
A |  | LOWEST
0.083 | 0 REFERENCE
A | POSITION 'A' | LOWEST
0.083 | OF THE
SECONDARIES
A | POSITION 'B' | LOWEST
0.083 | OF THE
SECONDARIES
A |  | LOWEST
0.083 | -9 IN
A | POSITION 'C' | LOWEST
0.083 | OF THE
SECONDARIES
A |  | LOWEST
0.083 | -18 IN
A |  | LOWEST
0.083 | -27 IN
A |  | LOWEST
0.083 | -36 IN
A |  | LOWEST
0.083 | -45 IN
A |  | LOWEST
0.083 | -54 IN
A | POSITION 'A' | LOWEST
0.083 | OF THE
PRIMARIES
A | POSITION 'B' | LOWEST
0.083 | OF THE
PRIMARIES
A | POSITION 'C' | LOWEST
0.083 | OF THE
PRIMARIES
A |  | LOWEST
0.083 | -63 IN
A |  | LOWEST
0.083 | -72 IN
A |  | LOWEST | bar: 58 to 69
0.083 | -81 IN
A |  | LOWEST | bar: 37 to 69
0.083 | -90 IN
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MIN
A | 0.001-0.083 | 0.140-0.149 | 10: OUTSIDE DIAMETER:; 23: 3; 30: INSPECTION RESULTS; 67: APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | 0.100-0.109 | 0.150-0.159 | 10: TUBE MATERIAL:; 23: SA-210A1; 35: MAX. THICKNESS
| 0.110-0.119 | 0.160-0.169 | 10: NOMINAL WALL:; 23: 0.203; 35: AVG. THICKNESS |  |  | TUBE WALL THICKNESS SURVEY (LOW VALUE)
| 0.120-0.129 | 0.170-0.179 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS
| 0.130-0.139 | 0.180-0.999 | 10: MILL FLAG:; 23: 0.1; 35: STD DEV.
LOW THICKNESS
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com