## Thickness
2025 |  | RF - REFRACTORY; RT - RECESSED TUBE; | [66 empty] | OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. THICKNESS MEASUREMENTS ARE IN INCHES. | [66 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | AVG | MIN
C | POSITION 'A' | L | 6: 0.179; 7: 0.187; 8: 0.188; 9: 0.169; 10: 0.159; 11: 0.175; 29: 0.185; 30: 0.204; 31: 0.182; 32: 0.177; 33: 0.169; 34: 0.177; 51: 0.17; 52: 0.177; 53: 0.176; 54: 0.166; 55: 0.176
0.099 | OF THE | C | 6: 0.174; 7: 0.18; 8: 0.177; 9: 0.18; 10: 0.165; 11: 0.18; 29: 0.183; 30: 0.166; 31: 0.172; 32: 0.18; 33: 0.167; 34: 0.18; 51: 0.182; 52: 0.174; 53: 0.181; 54: 0.173; 55: 0.177; 56: 0.18
| TERTIARIES | R | 6: 0.176; 7: 0.184; 8: 0.177; 9: 0.177; 10: 0.16; 11: 0.182; 29: 0.175; 30: 0.164; 31: 0.174; 32: 0.176; 33: 0.165; 34: 0.176; 51: 0.178; 52: 0.176; 53: 0.182; 54: 0.167; 55: 0.179; 56: 0.182
C | POSITION 'B' | L | 6: 0.178; 7: 0.176; 8: 0.172; 9: 0.178; 10: RT; 11: 0.174; 29: 0.178; 30: RT; 31: 0.183; 32: 0.181; 33: RT; 34: 0.188; 51: 0.194; 52: 0.171; 53: 0.175; 54: RT; 55: 0.177; 56: 0.18
0.099 | OF THE | C | 6: 0.179; 7: 0.177; 8: 0.173; 9: 0.184; 10: RT; 11: 0.18; 29: 0.176; 30: RT; 31: 0.178; 32: 0.18; 33: RT; 34: 0.181; 51: 0.17; 52: 0.171; 53: 0.18; 54: RT; 55: 0.175; 56: 0.185
| TERTIARIES | R | 6: 0.18; 7: 0.179; 8: 0.177; 9: 0.176; 10: RT; 11: 0.178; 29: 0.177; 30: RT; 31: 0.176; 32: 0.175; 33: RT; 34: 0.184; 51: 0.176; 52: 0.179; 53: 0.181; 54: RT; 55: 0.177; 56: 0.18
C | POSITION 'C' | L | 6: 0.169; 7: 0.182; 8: 0.176; 9: 0.178; 10: 0.169; 11: 0.175; 29: 0.179; 30: 0.169; 31: 0.185; 32: 0.182; 33: 0.173; 34: 0.189; 51: 0.181; 52: 0.173; 53: 0.177; 54: 0.179; 55: 0.183; 56: 0.179
0.099 | OF THE | C | 6: 0.171; 7: 0.175; 8: 0.183; 9: 0.183; 10: 0.162; 11: 0.174; 29: 0.181; 30: 0.171; 31: 0.18; 32: 0.18; 33: 0.166; 34: 0.182; 51: 0.181; 52: 0.178; 53: 0.181; 54: 0.169; 55: 0.176; 56: 0.179
| TERTIARIES | R | 6: 0.177; 7: 0.179; 8: 0.172; 9: 0.183; 10: 0.165; 11: 0.172; 29: 0.177; 30: 0.168; 31: 0.168; 32: 0.184; 33: 0.176; 34: 0.185; 51: 0.174; 52: 0.177; 53: 0.183; 54: 0.177; 55: 0.181; 56: 0.178
B |  | L | 0.219 | 0.223 | 0.219 | 0.223 | 0.219 | 0.219 | 0.222 | 0.212 | 0.227 | 0.221 | 0.218 | 0.222 | 0.222 | 0.216 | 0.221 | 0.22 | 0.213 | 0.227 | 0.214 | 0.219 | 0.225 | 0.221 | 0.223 | 0.217 | 0.218 | 0.226 | 0.242 | 0.224 | 0.235 | 0.221 | 0.235 | 0.23 | 0.22 | 0.236 | 0.227 | 0.231 | 0.241 | 0.241 | RF | 0.23 | 0.236 | 0.224 | 0.231 | 0.231 | 0.236 | 0.222 | 0.232 | 0.23 | 0.229 | 0.226 | 0.224 | 0.225 | 0.23 | RF | 0.235 | 0.221 | 0.224 | 0.236 | 0.226 | 0.222 | RF | RF
0.083 | +16 FT 6 IN | C | 0.218 | 0.222 | 0.222 | 0.222 | 0.228 | 0.226 | 0.22 | 0.214 | 0.213 | 0.222 | 0.219 | 0.223 | 0.229 | 0.224 | 0.215 | 0.216 | 0.216 | 0.221 | 0.224 | 0.221 | 0.22 | 0.22 | 0.224 | 0.219 | 0.219 | 0.231 | 0.23 | 0.232 | 0.224 | 0.241 | 0.241 | 0.235 | 0.227 | 0.227 | 0.239 | 0.229 | 0.224 | RF | 0.229 | 0.229 | 0.227 | 0.233 | 0.238 | 0.228 | 0.23 | 0.231 | 0.224 | 0.224 | 0.227 | 0.228 | 0.223 | 0.229 | 0.224 | RF | 0.223 | 0.227 | 0.234 | 0.225 | 0.228 | 0.216 | RF | 0.25
|  | R | 0.219 | 0.228 | 0.212 | 0.227 | 0.221 | 0.222 | 0.214 | 0.222 | 0.214 | 0.215 | 0.221 | 0.214 | 0.225 | 0.226 | 0.211 | 0.209 | 0.22 | 0.214 | 0.224 | 0.22 | 0.21 | 0.225 | 0.225 | 0.22 | 0.224 | 0.232 | 0.243 | 0.239 | 0.224 | 0.233 | 0.23 | 0.234 | 0.233 | 0.237 | 0.238 | 0.233 | 0.226 | RF | 0.224 | 0.23 | 0.234 | 0.234 | 0.233 | 0.229 | 0.227 | 0.228 | 0.224 | 0.242 | 0.238 | 0.228 | 0.226 | 0.222 | RF | 0.227 | 0.225 | 0.23 | 0.225 | 0.242 | 0.231 | RF | 0.22 | RF
B |  | L | 0.224 | 0.213 | 0.219 | 0.211 | 0.207 | 0.211 | 0.213 | 0.215 | 0.215 | 0.212 | 0.21 | 0.216 | 0.219 | 0.226 | 0.221 | 0.216 | 0.22 | 0.218 | 0.23 | 0.209 | 0.221 | 0.226 | 0.214 | 0.217 | 0.219 | 0.22 | 0.228 | 0.22 | 0.214 | 0.224 | 0.226 | 0.221 | 0.223 | 0.224 | 0.222 | 0.226 | 0.22 | 0.219 | 0.221 | 0.213 | 0.216 | 0.22 | 0.21 | 0.212 | 0.218 | 0.215 | 0.213 | 0.216 | 0.213 | 0.217 | 0.222 | 0.225 | 0.216 | 0.216 | 0.217 | 0.208 | 0.222 | 0.206 | 0.209 | 0.213 | 0.216 | 0.22
0.083 | +15 FT | C | 0.221 | 0.215 | 0.216 | 0.216 | 0.217 | 0.217 | 0.214 | 0.216 | 0.215 | 0.212 | 0.206 | 0.212 | 0.225 | 0.22 | 0.215 | 0.212 | 0.216 | 0.219 | 0.221 | 0.208 | 0.22 | 0.212 | 0.217 | 0.22 | 0.219 | 0.22 | 0.23 | 0.226 | 0.211 | 0.219 | 0.218 | 0.225 | 0.221 | 0.22 | 0.225 | 0.23 | 0.216 | 0.215 | 0.219 | 0.218 | 0.222 | 0.217 | 0.217 | 0.214 | 0.221 | 0.219 | 0.218 | 0.215 | 0.21 | 0.22 | 0.222 | 0.224 | 0.218 | 0.223 | 0.222 | 0.211 | 0.211 | 0.207 | 0.218 | 0.213 | 0.226 | 0.221
|  | R | 0.212 | 0.221 | 0.217 | 0.209 | 0.214 | 0.208 | 0.211 | 0.209 | 0.215 | 0.215 | 0.211 | 0.208 | 0.217 | 0.218 | 0.215 | 0.214 | 0.216 | 0.222 | 0.217 | 0.213 | 0.22 | 0.217 | 0.212 | 0.223 | 0.226 | 0.223 | 0.222 | 0.229 | 0.218 | 0.22 | 0.223 | 0.221 | 0.222 | 0.215 | 0.215 | 0.215 | 0.22 | 0.221 | 0.213 | 0.222 | 0.221 | 0.224 | 0.218 | 0.224 | 0.228 | 0.218 | 0.218 | 0.222 | 0.214 | 0.223 | 0.22 | 0.219 | 0.218 | 0.218 | 0.221 | 0.221 | 0.225 | 0.216 | 0.223 | 0.221 | 0.225 | 0.218
B |  | L | 0.219 | 0.22 | 0.213 | 0.22 | 0.219 | 0.214 | 0.205 | 0.216 | 0.204 | 0.218 | 0.216 | 0.217 | 0.215 | 0.212 | 0.216 | 0.212 | 0.215 | 0.219 | 0.214 | 0.218 | 0.219 | 0.212 | 0.216 | 0.22 | 0.219 | 0.219 | 0.219 | 0.22 | 0.212 | 0.223 | 0.219 | 0.22 | 0.218 | 0.219 | 0.219 | 0.216 | 0.212 | 0.211 | 0.213 | 0.21 | 0.212 | 0.207 | 0.201 | 0.204 | 0.208 | 0.223 | 0.215 | 0.218 | 0.216 | 0.212 | 0.213 | 0.216 | 0.215 | 0.205 | 0.207 | 0.208 | 0.21 | 0.212 | 0.21 | 0.216 | 0.203 | 0.212
0.083 | +13 FT 6 IN | C | 0.224 | 0.213 | 0.208 | 0.215 | 0.214 | 0.207 | 0.212 | 0.193 | 0.204 | 0.209 | 0.21 | 0.201 | 0.206 | 0.208 | 0.218 | 0.217 | 0.205 | 0.22 | 0.21 | 0.21 | 0.221 | 0.219 | 0.216 | 0.223 | 0.214 | 0.216 | 0.219 | 0.217 | 0.217 | 0.221 | 0.216 | 0.222 | 0.222 | 0.223 | 0.22 | 0.214 | 0.218 | 0.215 | 0.205 | 0.201 | 0.21 | 0.208 | 0.207 | 0.22 | 0.208 | 0.214 | 0.22 | 0.212 | 0.215 | 0.215 | 0.212 | 0.216 | 0.213 | 0.215 | 0.206 | 0.204 | 0.217 | 0.212 | 0.212 | 0.213 | 0.212 | 0.216
|  | R | 0.228 | 0.223 | 0.215 | 0.214 | 0.214 | 0.209 | 0.215 | 0.209 | 0.211 | 0.219 | 0.21 | 0.208 | 0.214 | 0.215 | 0.222 | 0.221 | 0.216 | 0.213 | 0.218 | 0.226 | 0.231 | 0.216 | 0.219 | 0.22 | 0.212 | 0.219 | 0.226 | 0.216 | 0.224 | 0.219 | 0.225 | 0.223 | 0.221 | 0.217 | 0.224 | 0.211 | 0.215 | 0.207 | 0.21 | 0.204 | 0.21 | 0.219 | 0.207 | 0.21 | 0.224 | 0.213 | 0.212 | 0.215 | 0.217 | 0.214 | 0.213 | 0.215 | 0.212 | 0.204 | 0.211 | 0.209 | 0.217 | 0.222 | 0.222 | 0.221 | 0.209 | 0.212
B |  | L | 0.212 | 0.229 | 0.222 | 0.222 | 0.218 | 0.208 | 0.218 | 0.193 | 0.208 | 0.196 | 0.205 | 0.188 | 0.202 | 0.208 | 0.194 | 0.208 | 0.193 | 0.213 | 0.209 | 0.216 | 0.214 | 0.216 | 0.22 | 0.217 | 0.217 | 0.215 | 0.219 | 0.212 | 0.221 | 0.209 | 0.221 | 0.221 | 0.215 | 0.217 | 0.218 | 0.215 | 0.211 | 0.213 | 0.219 | 0.202 | 0.211 | 0.198 | 0.207 | 0.212 | 0.209 | 0.217 | 0.209 | 0.215 | 0.205 | 0.213 | 0.203 | 0.206 | 0.214 | 0.212 | 0.211 | 0.209 | 0.208 | 0.213 | 0.222 | 0.215 | 0.213 | 0.214
0.083 | +12 FT | C | 0.224 | 0.224 | 0.217 | 0.219 | 0.208 | 0.209 | 0.212 | 0.201 | 0.217 | 0.203 | 0.207 | 0.204 | 0.193 | 0.209 | 0.2 | 0.219 | 0.201 | 0.21 | 0.212 | 0.214 | 0.225 | 0.214 | 0.214 | 0.214 | 0.219 | 0.214 | 0.217 | 0.213 | 0.216 | 0.219 | 0.217 | 0.222 | 0.212 | 0.214 | 0.224 | 0.207 | 0.215 | 0.199 | 0.211 | 0.211 | 0.21 | 0.206 | 0.202 | 0.206 | 0.203 | 0.216 | 0.217 | 0.203 | 0.209 | 0.199 | 0.211 | 0.204 | 0.216 | 0.219 | 0.211 | 0.211 | 0.212 | 0.21 | 0.224 | 0.211 | 0.215 | 0.215
|  | R | 0.217 | 0.22 | 0.214 | 0.214 | 0.217 | 0.209 | 0.208 | 0.206 | 0.213 | 0.199 | 0.201 | 0.203 | 0.2 | 0.207 | 0.194 | 0.201 | 0.203 | 0.209 | 0.214 | 0.217 | 0.219 | 0.219 | 0.22 | 0.22 | 0.218 | 0.213 | 0.222 | 0.213 | 0.225 | 0.217 | 0.218 | 0.217 | 0.211 | 0.216 | 0.219 | 0.214 | 0.213 | 0.207 | 0.222 | 0.212 | 0.206 | 0.217 | 0.203 | 0.21 | 0.21 | 0.219 | 0.218 | 0.203 | 0.206 | 0.207 | 0.207 | 0.211 | 0.21 | 0.212 | 0.211 | 0.216 | 0.216 | 0.213 | 0.211 | 0.221 | 0.214 | 0.208
B | POSITION 'A' | L | 2: 0.232; 3: 0.236; 4: 0.239; 5: 0.221; 58: 0.221; 59: 0.219; 60: 0.234; 61: 0.22
0.083 | OF THE | C | 2: 0.227; 3: 0.233; 4: 0.233; 5: 0.221; 58: 0.219; 59: 0.222; 60: 0.227; 61: 0.216
| OB PORTS | R | 2: 0.226; 3: 0.224; 4: 0.223; 5: 0.22; 58: 0.222; 59: 0.229; 60: 0.227; 61: 0.214
B | POSITION 'B' | L | 2: 0.222; 3: 0.227; 4: 0.222; 5: 0.221; 58: 0.22; 59: 0.243; 60: 0.218; 61: 0.217
0.083 | OF THE | C | 2: 0.217; 3: 0.225; 4: 0.221; 5: 0.224; 58: 0.222; 59: 0.219; 60: 0.22; 61: 0.22
| OB PORTS | R | 2: 0.217; 3: 0.219; 4: 0.223; 5: 0.223; 58: 0.225; 59: 0.222; 60: 0.22; 61: 0.221
B | POSITION 'C' | L | 2: 0.222; 3: 0.23; 4: 0.223; 5: 0.215; 58: 0.22; 59: 0.233; 60: 0.233; 61: 0.216
0.083 | OF THE | C | 2: 0.222; 3: 0.228; 4: 0.22; 5: 0.217; 58: 0.221; 59: 0.226; 60: 0.229; 61: 0.213
| OB PORTS | R | 2: 0.221; 3: 0.228; 4: 0.233; 5: 0.217; 58: 0.223; 59: 0.226; 60: 0.22; 61: 0.214
B |  | L | 0.209 | 0.22 | 0.224 | 0.226 | 0.219 | 0.212 | 0.224 | 0.205 | 0.216 | 0.209 | 0.198 | 0.19 | 0.194 | 0.192 | 0.194 | 0.199 | 0.183 | 0.21 | 0.196 | 0.207 | 0.205 | 0.214 | 0.213 | 0.218 | 0.216 | 0.223 | 0.225 | 0.218 | 0.218 | 0.217 | 0.227 | 0.22 | 0.215 | 0.223 | 0.212 | 0.206 | 0.208 | 0.21 | 0.214 | 0.214 | 0.209 | 0.216 | 0.197 | 0.195 | 0.217 | 0.211 | 0.218 | 0.219 | 0.204 | 0.197 | 0.204 | 0.218 | 0.209 | 0.207 | 0.208 | 0.221 | 0.208 | 0.215 | 0.216 | 0.22 | 0.219 | 0.214
0.083 | +10 FT 6 IN | C | 0.212 | 0.211 | 0.226 | 0.222 | 0.213 | 0.214 | 0.206 | 0.203 | 0.209 | 0.193 | 0.207 | 0.197 | 0.198 | 0.2 | 0.199 | 0.202 | 0.19 | 0.21 | 0.202 | 0.203 | 0.211 | 0.214 | 0.218 | 0.213 | 0.215 | 0.225 | 0.218 | 0.22 | 0.214 | 0.21 | 0.226 | 0.218 | 0.214 | 0.221 | 0.209 | 0.208 | 0.203 | 0.218 | 0.209 | 0.216 | 0.209 | 0.208 | 0.207 | 0.201 | 0.193 | 0.212 | 0.206 | 0.205 | 0.202 | 0.202 | 0.209 | 0.211 | 0.21 | 0.207 | 0.213 | 0.212 | 0.217 | 0.223 | 0.214 | 0.214 | 0.216 | 0.223
|  | R | 0.216 | 0.216 | 0.226 | 0.22 | 0.212 | 0.209 | 0.209 | 0.213 | 0.191 | 0.198 | 0.202 | 0.187 | 0.192 | 0.2 | 0.191 | 0.204 | 0.189 | 0.199 | 0.197 | 0.219 | 0.219 | 0.212 | 0.218 | 0.209 | 0.217 | 0.219 | 0.216 | 0.214 | 0.217 | 0.218 | 0.224 | 0.229 | 0.218 | 0.222 | 0.218 | 0.217 | 0.218 | 0.205 | 0.215 | 0.222 | 0.213 | 0.212 | 0.215 | 0.209 | 0.204 | 0.216 | 0.212 | 0.217 | 0.219 | 0.218 | 0.218 | 0.218 | 0.218 | 0.212 | 0.218 | 0.219 | 0.217 | 0.226 | 0.219 | 0.217 | 0.225 | 0.223
B |  | L | 0.226 | 0.217 | 0.243 | 0.228 | 0.223 | 0.215 | 0.216 | 0.216 | 0.208 | 0.207 | 0.213 | 0.202 | RF | 0.189 | 0.21 | 0.214 | 0.207 | 0.226 | 0.225 | 0.216 | 0.228 | 0.216 | 0.242 | 0.225 | 0.227 | 0.225 | 0.233 | 0.231 | 0.218 | RF | RF | 0.238 | 0.221 | 0.231 | 0.215 | 0.22 | 0.211 | 0.203 | 0.208 | 0.219 | 0.207 | 0.2 | 0.214 | 0.217 | 0.219 | 0.219 | 0.211 | 0.224 | 0.214 | 0.225 | 0.222 | 0.211 | 0.21 | RF | 0.215 | 0.218 | 0.209 | 0.221 | 0.217 | 0.228 | 0.23 | 0.229
0.083 | +9 FT | C | 0.22 | RF | 0.234 | 0.233 | 0.228 | 0.215 | 0.208 | 0.204 | 0.218 | 0.204 | 0.21 | 0.202 | RF | 0.204 | 0.203 | 0.218 | 0.206 | 0.224 | 0.222 | 0.212 | 0.214 | 0.219 | 0.218 | 0.221 | 0.218 | 0.22 | 0.221 | 0.226 | 0.236 | RF | RF | 0.242 | 0.232 | 0.24 | 0.237 | 0.206 | 0.211 | 0.209 | RF | 0.201 | 0.236 | 0.207 | 0.226 | 0.206 | 0.2 | 0.202 | 0.207 | 0.221 | 0.213 | 0.219 | 0.221 | 0.209 | 0.215 | RF | 0.217 | 0.217 | 0.223 | 0.228 | 0.221 | 0.22 | 0.213 | 0.225
|  | R | 0.225 | 0.216 | 0.236 | 0.232 | 0.221 | 0.22 | 0.203 | 0.21 | 0.211 | 0.204 | 0.214 | 0.212 | RF | 0.208 | 0.212 | 0.205 | 0.209 | 0.219 | 0.224 | 0.207 | 0.23 | 0.222 | 0.218 | 0.229 | 0.223 | 0.228 | 0.218 | 0.223 | 0.229 | RF | 0.232 | RF | 0.229 | 0.216 | 0.217 | 0.212 | 0.199 | 0.207 | RF | 0.22 | 0.212 | 0.208 | 0.23 | 0.208 | 0.202 | 0.216 | 0.213 | 0.217 | 0.212 | 0.219 | 0.215 | 0.213 | 0.225 | RF | 0.224 | 0.223 | 0.229 | 0.23 | 0.233 | 0.227 | 0.224 | 0.22
B | POSITION 'A' | L | 29: 0.229; 30: 0.226; 31: 0.229; 32: 0.23; 33: 0.222; 34: 0.218
0.083 | OF THE | C | 29: 0.227; 30: 0.236; 31: 0.232; 32: 0.222; 33: 0.219; 34: 0.221
| OSCILLATOR | R | 29: 0.234; 30: 0.224; 31: 0.227; 32: 0.225; 33: 0.222; 34: 0.224
B | POSITION 'B' | L | 29: 0.222; 30: 0.23; 31: 0.224; 32: 0.226; 33: 0.221; 34: 0.212
0.083 | OF THE | C | 29: 0.227; 30: 0.228; 31: 0.226; 32: 0.227; 33: 0.224; 34: 0.227
| OSCILLATOR | R | 29: 0.232; 30: 0.223; 31: 0.225; 32: 0.229; 33: 0.219; 34: 0.226
B | POSITION 'C' | L | 29: 0.225; 30: 0.22; 31: 0.233; 32: 0.238; 33: 0.218; 34: 0.227
0.083 | OF THE | C | 29: 0.225; 30: 0.226; 31: 0.228; 32: 0.229; 33: 0.221; 34: 0.232
| OSCILLATOR | R | 29: 0.228; 30: 0.225; 31: 0.232; 32: 0.233; 33: 0.224; 34: 0.225
B | POSITION 'D' | L | 29: 0.222; 30: 0.211; 31: 0.231; 32: 0.244; 33: 0.231; 34: 0.218
0.083 | OF THE | C | 29: 0.22; 30: 0.226; 31: 0.235; 32: 0.244; 33: 0.218; 34: 0.214
| OSCILLATOR | R | 29: 0.229; 30: 0.223; 31: 0.233; 32: 0.235; 33: 0.213; 34: 0.217
B | POSITION 'E' | L | 29: 0.222; 30: 0.223; 31: 0.223; 32: 0.234; 33: 0.226; 34: 0.211
0.083 | OF THE | C | 29: 0.219; 30: 0.217; 31: 0.222; 32: 0.231; 33: 0.212; 34: 0.221
| OSCILLATOR | R | 29: 0.237; 30: 0.216; 31: 0.232; 32: 0.241; 33: 0.212; 34: 0.224
B |  | L | 0.236 | RF | 0.222 | 0.225 | 0.223 | 0.218 | 0.209 | 0.212 | 0.221 | 0.214 | 0.211 | 0.213 | RF | 0.208 | 0.208 | 0.203 | 0.202 | 0.209 | 0.208 | 0.207 | 0.204 | 0.206 | 0.21 | 0.219 | 0.209 | 0.222 | 0.206 | 0.224 | 0.209 | 0.217 | 0.223 | 0.228 | 0.223 | 0.217 | 0.207 | 0.187 | 0.216 | 0.191 | 0.195 | 0.204 | 0.219 | 0.206 | 0.207 | 0.212 | 0.21 | 0.209 | 0.216 | 0.205 | 0.221 | 0.218 | 0.22 | 0.205 | 0.202 | RF | 0.226 | 0.209 | 0.225 | 0.224 | 0.213 | 0.243 | 0.219 | RF
0.083 | +7 FT 6 IN | C | 0.23 | RF | 0.22 | 0.214 | 0.213 | 0.218 | 0.216 | 0.221 | 0.209 | 0.215 | 0.213 | 0.221 | RF | 0.225 | 0.215 | 0.203 | 0.212 | 0.204 | 0.197 | 0.195 | 0.206 | 0.208 | 0.205 | 0.214 | 0.212 | 0.227 | 0.207 | 0.214 | 0.231 | 0.229 | 0.223 | 0.217 | 0.215 | 0.197 | 0.211 | 0.206 | 0.202 | 0.197 | RF | 0.21 | 0.207 | 0.208 | 0.208 | 0.209 | 0.21 | 0.205 | 0.214 | 0.21 | 0.217 | 0.207 | 0.211 | 0.229 | 0.207 | RF | 0.207 | 0.214 | 0.206 | 0.224 | 0.224 | 0.224 | 0.222 | 0.239
|  | R | 0.232 | 0.222 | 0.211 | 0.216 | 0.227 | 0.225 | 0.217 | 0.216 | 0.211 | 0.2 | 0.212 | 0.223 | RF | 0.21 | 0.212 | 0.197 | 0.205 | 0.204 | 0.218 | 0.201 | 0.218 | 0.207 | 0.21 | 0.208 | 0.221 | 0.213 | 0.202 | 0.213 | 0.211 | 0.204 | 0.222 | 0.213 | 0.22 | 0.223 | 0.2 | 0.196 | 0.208 | 0.205 | RF | 0.199 | 0.195 | 0.21 | 0.211 | 0.207 | 0.202 | 0.208 | 0.196 | 0.214 | 0.212 | 0.215 | 0.206 | 0.208 | 0.214 | RF | 0.209 | 0.216 | 0.214 | 0.215 | 0.217 | 0.224 | RF | 0.239
B |  | L | 0.208 | RF | 0.215 | 0.223 | 0.21 | 0.213 | 0.231 | 0.213 | 0.225 | 0.21 | 0.212 | 0.199 | RF | 0.204 | 0.22 | 0.22 | 0.215 | 0.21 | 0.212 | 0.193 | 0.196 | 0.193 | 0.209 | 0.198 | 0.195 | 0.191 | 0.207 | 0.201 | 0.194 | 0.212 | 0.195 | 0.219 | 0.194 | 0.193 | 0.2 | 0.196 | 0.206 | 0.204 | RF | 0.214 | 0.198 | 0.194 | 0.199 | 0.2 | 0.181 | 0.192 | 0.197 | 0.201 | 0.199 | 0.202 | 0.204 | 0.2 | 0.204 | 0.211 | 0.218 | 0.215 | 0.218 | 0.218 | 0.211 | 0.218 | 0.227 | 0.208
0.083 | +6 FT | C | 0.216 | RF | 0.21 | 0.226 | 0.222 | 0.215 | 0.219 | 0.209 | 0.227 | 0.204 | 0.209 | 0.215 | RF | 0.208 | 0.199 | 0.197 | 0.195 | 0.21 | 0.181 | 0.182 | 0.196 | 0.205 | 0.193 | 0.189 | 0.193 | 0.192 | 0.201 | 0.213 | 0.187 | 0.184 | 0.219 | 0.204 | 0.192 | 0.207 | 0.199 | 0.204 | 0.209 | 0.212 | RF | 0.208 | 0.206 | 0.206 | 0.209 | 0.181 | 0.2 | 0.188 | 0.197 | 0.198 | 0.211 | 0.198 | 0.21 | 0.201 | 0.205 | 0.22 | 0.211 | 0.214 | 0.207 | 0.225 | 0.223 | 0.222 | 0.214 | 0.207
|  | R | 0.212 | 0.192 | 0.211 | 0.217 | 0.207 | 0.221 | 0.214 | 0.224 | 0.214 | 0.209 | 0.202 | 0.214 | RF | 0.217 | 0.204 | 0.204 | 0.194 | 0.205 | 0.205 | 0.214 | 0.209 | 0.207 | 0.2 | 0.198 | 0.201 | 0.2 | 0.212 | 0.193 | 0.203 | 0.191 | 0.205 | 0.196 | 0.194 | 0.204 | 0.187 | 0.196 | 0.206 | 0.206 | RF | 0.193 | 0.205 | 0.194 | 0.192 | 0.189 | 0.21 | 0.205 | 0.214 | 0.204 | 0.202 | 0.208 | 0.206 | 0.218 | 0.201 | 0.22 | 0.21 | 0.225 | 0.209 | 0.213 | 0.218 | 0.23 | 0.208 | 0.205
B |  | L | 0.208 | RF | 0.212 | 0.224 | 0.208 | 0.205 | 0.22 | 0.206 | 0.203 | 0.212 | 0.215 | 0.198 | RF | 0.207 | 0.213 | 0.202 | 0.207 | 0.202 | 0.199 | 0.202 | 0.19 | 0.208 | 0.211 | 0.203 | 0.205 | 0.212 | 0.188 | 0.191 | 0.208 | 0.21 | 0.194 | 0.205 | 0.206 | 0.202 | 0.203 | 0.201 | 0.201 | 0.198 | 0.202 | 0.209 | 0.21 | 0.2 | 0.199 | 0.212 | 0.201 | 0.205 | 0.225 | 0.21 | 0.205 | 0.208 | 0.209 | 0.209 | 0.203 | 0.217 | 0.202 | 0.208 | 0.205 | 0.21 | 0.21 | 0.208 | 0.216 | 0.223
0.083 | +4 FT 6 IN | C | 0.217 | RF | 0.215 | 0.218 | 0.22 | 0.216 | 0.215 | 0.219 | 0.212 | 0.198 | 0.212 | 0.208 | 0.206 | 0.202 | 0.202 | 0.186 | 0.187 | 0.201 | 0.203 | 0.172 | 0.196 | 0.198 | 0.204 | 0.2 | 0.187 | 0.208 | 0.191 | 0.204 | 0.201 | 0.2 | 0.195 | 0.2 | 0.187 | 0.195 | 0.194 | 0.188 | 0.193 | 0.202 | 0.208 | 0.206 | 0.199 | 0.195 | 0.205 | RF | 0.199 | 0.22 | 0.207 | 0.207 | 0.21 | 0.213 | 0.216 | 0.194 | 0.203 | 0.205 | 0.203 | 0.206 | 0.206 | 0.206 | 0.215 | 0.212 | 0.212 | 0.212
|  | R | RF | RF | 0.216 | 0.213 | 0.214 | 0.21 | 0.214 | 0.208 | 0.199 | 0.192 | 0.203 | 0.213 | 0.206 | 0.201 | 0.2 | 0.199 | 0.205 | 0.197 | 0.2 | 0.202 | 0.197 | 0.198 | 0.202 | 0.218 | 0.199 | 0.2 | 0.198 | 0.212 | 0.194 | 0.198 | 0.197 | 0.184 | 0.2 | 0.204 | 0.199 | 0.203 | 0.195 | 0.203 | 0.203 | 0.215 | 0.201 | 0.2 | RF | 0.215 | 0.206 | 0.211 | 0.189 | 0.21 | 0.214 | 0.204 | 0.215 | 0.204 | 0.202 | 0.204 | 0.198 | 0.21 | 0.21 | 0.211 | 0.216 | 0.215 | 0.221 | 0.205
B |  | L | 0.237 | 0.255 | 0.211 | 0.2 | 0.212 | 0.23 | 0.23 | 0.224 | 0.218 | 0.211 | 0.211 | 0.207 | 0.235 | 0.216 | 0.214 | 0.204 | 0.198 | 0.21 | 0.212 | 0.203 | 0.211 | 0.213 | 0.208 | 0.212 | 0.207 | 0.198 | 0.219 | 0.219 | 0.21 | 0.207 | 0.201 | 0.219 | 0.194 | 0.214 | 0.216 | 0.203 | 0.212 | RF | 0.207 | 0.198 | 0.193 | 0.202 | 0.207 | 0.21 | 0.192 | 0.199 | 0.208 | 0.195 | 0.199 | 0.196 | 0.206 | 0.19 | 0.208 | RF | 0.213 | 0.198 | 0.205 | 0.217 | 0.207 | 0.221 | RF | 0.231
0.083 | +3 FT | C | 0.214 | RF | 0.204 | 0.231 | 0.217 | 0.211 | 0.232 | 0.219 | 0.209 | 0.209 | 0.211 | 0.21 | 0.21 | 0.212 | 0.213 | 0.213 | 0.2 | 0.207 | 0.186 | 0.19 | 0.197 | 0.22 | 0.196 | 0.195 | 0.205 | 0.187 | 0.217 | 0.214 | 0.196 | 0.169 | 0.185 | 0.198 | 0.205 | 0.179 | 0.213 | 0.198 | 0.216 | 0.2 | 0.193 | 0.214 | 0.213 | 0.171 | 0.191 | 0.214 | 0.182 | 0.192 | 0.198 | 0.197 | 0.214 | 0.195 | 0.194 | 0.195 | 0.202 | RF | 0.217 | 0.196 | 0.205 | 0.216 | 0.226 | 0.221 | RF | RF
|  | R | RF | 0.191 | 0.197 | 0.21 | 0.206 | 0.206 | 0.208 | 0.217 | 0.209 | 0.22 | 0.224 | 0.206 | 0.214 | 0.192 | 0.209 | 0.199 | 0.186 | 0.193 | 0.189 | 0.197 | 0.208 | 0.202 | 0.19 | 0.198 | 0.198 | 0.2 | 0.211 | 0.218 | 0.213 | 0.187 | 0.205 | 0.217 | 0.192 | 0.204 | 0.2 | 0.187 | 0.202 | 0.201 | 0.196 | 0.198 | 0.201 | 0.182 | 0.203 | 0.203 | 0.187 | 0.198 | 0.204 | 0.199 | 0.199 | 0.195 | 0.19 | 0.203 | 0.207 | RF | 0.218 | 0.217 | 0.21 | 0.219 | 0.227 | RF | RF | RF
B |  | L | 0.246 | 0.211 | 0.209 | 0.232 | 0.214 | 0.224 | 0.206 | 0.207 | 0.228 | 0.216 | 0.222 | 0.231 | RF | 0.207 | 0.214 | 0.199 | 0.217 | 0.214 | 0.214 | 0.209 | 0.223 | 0.209 | 0.21 | 0.215 | 0.209 | 0.218 | 0.213 | 0.218 | 0.209 | 0.222 | 0.234 | 0.186 | 0.223 | 0.218 | 0.244 | 0.22 | 0.214 | 0.245 | RF | 0.23 | 0.212 | 0.21 | 0.214 | 0.213 | 0.206 | 0.212 | 0.212 | 0.209 | 0.219 | 0.211 | 0.212 | 0.213 | 0.214 | 0.201 | 0.204 | 0.204 | 0.217 | 0.21 | 0.217 | 0.217 | 0.232 | 0.234
0.083 | +1 FT 6 IN | C | 0.206 | 0.199 | 0.215 | 0.224 | 0.215 | 0.221 | 0.206 | 0.223 | 0.213 | 0.213 | 0.204 | 0.198 | RF | 0.203 | 0.208 | 0.206 | 0.197 | 0.209 | 0.2 | 0.216 | 0.213 | 0.203 | 0.208 | 0.204 | 0.198 | 0.22 | 0.218 | 0.21 | 0.202 | 0.205 | 0.224 | 0.228 | 0.204 | 0.243 | 0.222 | 0.207 | 0.209 | RF | 0.222 | 0.208 | 0.19 | 0.211 | 0.223 | 0.201 | 0.228 | 0.208 | 0.217 | 0.22 | 0.203 | 0.195 | 0.204 | 0.198 | 0.194 | RF | 0.194 | 0.204 | 0.214 | 0.209 | 0.209 | 0.219 | RF | RF
|  | R | 0.21 | 0.239 | 0.22 | 0.223 | 0.215 | 0.207 | 0.206 | 0.203 | 0.225 | 0.209 | 0.208 | 0.214 | RF | 0.199 | 0.207 | 0.207 | 0.192 | 0.208 | 0.208 | 0.204 | 0.203 | 0.202 | 0.211 | 0.201 | 0.208 | 0.195 | 0.21 | 0.205 | 0.231 | 0.233 | 0.185 | 0.207 | 0.213 | 0.184 | 0.192 | 0.21 | 0.204 | RF | 0.2 | 0.217 | 0.196 | 0.201 | 0.177 | 0.183 | 0.164 | 0.168 | 0.185 | 0.183 | 0.18 | 0.201 | 0.206 | 0.179 | 0.188 | 0.217 | 0.189 | 0.195 | 0.197 | 0.217 | 0.215 | 0.224 | 0.235 | RF
B |  | L | 0.213 | 0.248 | 0.217 | 0.212 | 0.205 | 0.209 | 0.196 | 0.197 | 0.197 | 0.2 | 0.203 | 0.204 | 0.195 | 0.201 | 0.204 | 0.202 | 0.189 | 0.201 | 0.206 | 0.208 | 0.219 | 0.206 | 0.212 | 0.206 | 0.208 | 0.214 | 0.215 | 0.217 | 0.209 | 0.215 | 0.211 | 0.212 | 0.216 | 0.242 | 0.204 | 0.207 | 0.237 | 0.214 | 0.209 | 0.211 | 0.211 | 0.211 | 0.216 | 0.217 | 0.212 | 0.207 | 0.213 | 0.208 | 0.213 | 0.207 | 0.204 | 0.194 | 0.194 | 0.188 | 0.196 | 0.231 | 0.175 | 0.181 | 0.193 | 0.179 | 0.194 | 0.2
0.083 | 0 REFERENCE | C | 0.212 | RF | 0.217 | 0.213 | 0.211 | 0.204 | 0.206 | 0.203 | 0.2 | 0.202 | 0.203 | 0.203 | 0.197 | 0.201 | 0.202 | 0.202 | 0.196 | 0.209 | 0.203 | 0.2 | 0.205 | 0.208 | 0.209 | 0.206 | 0.202 | 0.214 | 0.245 | 0.21 | 0.208 | 0.244 | 0.205 | RF | RF | 0.247 | 0.199 | 0.236 | 0.214 | 0.208 | 0.183 | 0.184 | 0.222 | 0.218 | 0.243 | 0.21 | 0.178 | 0.203 | 0.206 | 0.206 | 0.176 | 0.212 | 0.187 | 0.214 | 0.2 | 0.228 | 0.188 | 0.154 | 0.204 | 0.174 | 0.183 | 0.187 | 0.201 | 0.211
|  | R | RF | 0.217 | 0.215 | 0.219 | 0.203 | 0.197 | 0.196 | 0.195 | 0.19 | 0.183 | 0.187 | 0.193 | 0.225 | 0.193 | 0.23 | 0.194 | 0.194 | 0.196 | 0.193 | 0.19 | 0.214 | 0.202 | 0.235 | 0.192 | 0.194 | 0.206 | 0.207 | 0.206 | 0.193 | 0.206 | 0.2 | 0.213 | 0.201 | 0.237 | 0.193 | 0.212 | 0.194 | 0.204 | 0.194 | 0.213 | 0.185 | 0.225 | 0.171 | 0.18 | 0.203 | 0.175 | 0.2 | 0.218 | 0.175 | 0.175 | 0.174 | 0.179 | 0.169 | 0.168 | 0.165 | 0.152 | 0.17 | 0.189 | 0.243 | 0.195 | 0.214 | RF
B | POSITION 'A' | L | 30: 0.211; 31: 0.212; 32: 0.234; 33: 0.208; 34: 0.217; 35: 0.22
0.083 | OF THE | C | 30: 0.208; 31: 0.215; 32: 0.216; 33: 0.203; 34: 0.207; 35: 0.202
| SECONDARIES | R | 30: 0.204; 31: 0.205; 32: 0.232; 33: 0.232; 34: 0.221; 35: 0.209
B | POSITION 'B' | L | 30: 0.212; 31: 0.221; 32: 0.217; 33: 0.214; 34: 0.207; 35: 0.213
0.083 | OF THE | C | 30: 0.205; 31: 0.206; 32: 0.216; 33: 0.255; 34: 0.233; 35: 0.203
| SECONDARIES | R | 30: 0.211; 31: 0.206; 32: 0.209; 33: 0.191; 34: 0.193; 35: 0.193
B |  | L | RF | RF | 0.216 | 0.207 | 0.207 | 0.2 | 0.2 | 0.205 | 0.205 | 0.206 | 0.208 | 0.205 | 0.205 | 0.206 | 0.208 | 0.199 | 0.206 | 0.209 | 0.217 | 0.204 | 0.209 | 0.212 | 0.214 | 0.214 | 0.209 | 0.218 | 0.208 | 0.208 | 0.203 | 0.206 | 0.207 | 0.217 | 0.209 | 0.228 | 0.224 | 0.21 | 0.216 | 0.217 | 0.219 | 0.213 | 0.208 | 0.209 | 0.206 | 0.208 | 0.202 | 0.202 | 0.201 | 0.213 | 0.199 | 0.2 | 0.218 | 0.192 | 0.221 | 0.197 | 0.203 | 0.183 | 0.189 | 0.184 | 0.242 | 0.211 | 0.202 | 0.224
0.083 | -9 IN | C | 0.215 | 0.215 | 0.212 | 0.225 | 0.211 | 0.208 | 0.202 | 0.204 | 0.2 | 0.204 | 0.202 | 0.192 | 0.208 | 0.202 | 0.216 | 0.205 | 0.194 | 0.212 | 0.2 | 0.199 | 0.203 | 0.196 | 0.207 | 0.209 | 0.198 | 0.203 | 0.198 | 0.204 | 0.206 | 0.199 | 0.21 | 0.215 | RF | RF | 0.199 | 0.181 | 0.209 | 0.212 | 0.211 | 0.205 | 0.196 | 0.202 | 0.198 | 0.188 | 0.197 | 0.181 | 0.188 | 0.19 | 0.182 | 0.188 | 0.19 | 0.194 | 0.2 | 0.191 | 0.182 | 0.181 | 0.191 | 0.179 | RF | 0.193 | 0.219 | 0.221
|  | R | RF | 0.218 | 0.218 | 0.224 | 0.204 | 0.207 | 0.209 | 0.194 | 0.201 | 0.201 | 0.204 | 0.197 | 0.198 | 0.199 | 0.204 | 0.198 | 0.2 | 0.218 | 0.195 | 0.2 | 0.2 | 0.205 | 0.208 | 0.199 | 0.201 | 0.196 | 0.206 | 0.204 | 0.213 | 0.217 | 0.221 | 0.213 | 0.214 | 0.207 | 0.178 | 0.207 | 0.218 | 0.219 | 0.207 | 0.197 | 0.192 | 0.201 | 0.196 | 0.198 | 0.195 | 0.197 | 0.194 | 0.187 | 0.187 | 0.183 | 0.184 | 0.188 | 0.178 | 0.213 | 0.179 | 0.184 | 0.178 | 0.171 | 0.239 | 0.216 | RF | RF
B | POSITION 'C' | L | 30: 0.209; 31: 0.213; 32: 0.224; 33: 0.224; 34: 0.225; 35: 0.214
0.083 | OF THE | C | 30: 0.209; 31: 0.214; 32: 0.207; 33: 0.219; 34: 0.22; 35: 0.224
| SECONDARIES | R | 30: 0.217; 31: 0.217; 32: 0.206; 33: 0.219; 34: 0.195; 35: 0.199
B |  | L | 0.23 | 0.22 | 0.216 | 0.221 | 0.204 | 0.203 | 0.213 | 0.216 | 0.21 | 0.204 | 0.21 | 0.203 | 0.207 | 0.21 | 0.208 | 0.203 | 0.203 | 0.201 | 0.207 | 0.205 | 0.21 | 0.213 | 0.206 | 0.209 | 0.204 | 0.21 | 0.216 | 0.215 | 0.217 | 0.212 | 0.215 | 0.221 | 0.219 | 0.215 | 0.212 | 0.222 | 0.214 | 0.209 | 0.209 | 0.204 | 0.212 | 0.201 | 0.204 | 0.197 | 0.188 | 0.2 | 0.19 | 0.212 | 0.203 | 0.203 | 0.203 | 0.198 | 0.196 | 0.21 | 0.195 | 0.202 | 0.194 | 0.203 | 0.235 | 0.199 | 0.194 | 0.223
0.083 | -18 IN | C | 0.228 | 0.208 | 0.212 | 0.213 | 0.212 | 0.196 | 0.215 | 0.211 | 0.215 | 0.207 | 0.207 | 0.206 | 0.212 | 0.211 | 0.206 | 0.196 | 0.214 | 0.21 | 0.213 | 0.205 | 0.204 | 0.214 | 0.209 | 0.211 | 0.212 | 0.213 | 0.201 | 0.216 | 0.221 | 0.214 | 0.204 | 0.208 | 0.226 | 0.214 | 0.208 | 0.22 | 0.204 | 0.193 | 0.203 | 0.197 | 0.22 | 0.188 | 0.192 | 0.182 | 0.189 | 0.193 | 0.19 | 0.203 | 0.194 | 0.196 | 0.184 | 0.194 | 0.198 | 0.184 | 0.182 | 0.198 | 0.194 | 0.199 | 0.239 | 0.207 | 0.217 | 0.217
|  | R | 0.231 | 0.21 | 0.216 | 0.211 | 0.209 | 0.201 | 0.202 | 0.209 | 0.212 | 0.213 | 0.205 | 0.199 | 0.209 | 0.21 | 0.211 | 0.202 | 0.205 | 0.204 | 0.208 | 0.205 | 0.202 | 0.21 | 0.22 | 0.196 | 0.212 | 0.195 | 0.206 | 0.208 | 0.216 | 0.216 | 0.206 | 0.216 | 0.196 | 0.232 | 0.204 | 0.214 | 0.222 | 0.201 | 0.182 | 0.198 | 0.199 | 0.176 | 0.19 | 0.194 | 0.193 | 0.194 | 0.191 | 0.191 | 0.187 | 0.191 | 0.184 | 0.188 | 0.191 | 0.184 | 0.188 | 0.191 | 0.199 | 0.195 | 0.24 | 0.209 | 0.216 | 0.221
B |  | L | 0.329 | RF | 0.325 | 0.332 | 0.314 | 0.323 | 0.32 | 0.329 | 0.317 | 0.307 | 0.31 | 0.318 | 0.31 | 0.315 | 0.331 | 0.328 | 0.322 | 0.307 | 0.321 | 0.313 | 0.315 | 0.334 | 0.323 | 0.327 | 0.332 | 0.319 | 0.322 | 0.325 | 0.327 | 0.32 | 0.324 | 0.316 | 0.317 | 0.323 | 0.323 | 0.313 | 0.316 | 0.326 | 0.323 | 0.314 | 0.316 | 0.316 | 0.314 | 0.314 | 0.319 | 0.306 | 0.306 | 0.313 | 0.307 | 0.304 | 0.307 | 0.299 | 0.306 | 0.321 | 0.321 | 0.321 | 0.323 | 0.317 | 0.32 | 0.326 | 0.323 | RF
0.083 | -27 IN | C | 0.329 | 0.319 | 0.314 | 0.321 | 0.316 | 0.324 | 0.333 | 0.319 | 0.316 | 0.302 | 0.303 | 0.307 | 0.317 | 0.321 | 0.325 | 0.317 | 0.33 | 0.31 | 0.318 | 0.316 | 0.309 | 0.322 | 0.319 | 0.331 | 0.325 | 0.321 | 0.325 | RF | 0.311 | 0.329 | 0.323 | 0.317 | 0.307 | 0.309 | 0.311 | 0.299 | 0.296 | 0.309 | 0.313 | 0.307 | 0.309 | 0.305 | 0.306 | 0.304 | 0.306 | 0.292 | 0.308 | 0.296 | 0.294 | 0.305 | 0.303 | 0.293 | 0.304 | 0.304 | 0.32 | 0.321 | RF | RF | 0.326 | 0.333 | 0.316 | 0.321
|  | R | RF | 0.319 | 0.325 | 0.323 | 0.327 | 0.323 | 0.328 | 0.324 | 0.321 | 0.31 | RF | 0.311 | 0.327 | 0.324 | 0.332 | 0.326 | 0.337 | 0.318 | 0.342 | 0.317 | 0.309 | 0.309 | 0.32 | 0.333 | 0.314 | 0.316 | 0.311 | 0.326 | 0.325 | 0.327 | 0.314 | 0.311 | 0.306 | 0.306 | 0.316 | 0.31 | 0.3 | 0.306 | 0.319 | 0.284 | 0.308 | 0.308 | 0.314 | 0.306 | 0.314 | 0.305 | 0.314 | 0.3 | 0.308 | 0.31 | 0.311 | 0.297 | 0.321 | 0.323 | RF | RF | RF | 0.329 | RF | RF | 0.32 | 0.33
A |  | L | 0.341 | RF | 0.324 | 0.33 | RF | RF | 0.32 | 0.327 | 0.331 | 0.299 | 0.316 | 0.317 | 0.305 | 0.325 | 0.326 | 0.319 | 0.327 | 0.315 | 0.313 | 0.306 | 0.32 | 0.331 | 0.319 | 0.324 | 0.326 | 0.32 | 0.308 | 0.315 | 0.324 | 0.319 | 0.329 | 0.318 | 0.309 | 0.31 | 0.324 | 0.321 | 0.324 | 0.317 | 0.326 | 0.317 | 0.318 | 0.321 | 0.311 | 0.315 | 0.32 | 0.316 | 0.312 | 0.323 | 0.32 | 0.309 | 0.319 | 0.314 | 0.318 | 0.327 | 0.328 | 0.324 | 0.335 | 0.328 | RF | 0.325 | RF | RF
0.083 | -36 IN | C | RF | RF | 0.326 | RF | RF | 0.337 | RF | 0.318 | 0.308 | 0.318 | 0.308 | 0.324 | RF | 0.323 | 0.321 | 0.324 | 0.335 | 0.308 | 0.316 | 0.313 | 0.329 | 0.334 | 0.321 | 0.321 | 0.326 | 0.316 | 0.319 | 0.312 | 0.319 | 0.315 | 0.321 | 0.317 | 0.314 | 0.312 | 0.328 | 0.319 | 0.315 | 0.322 | 0.327 | 0.295 | 0.313 | 0.314 | 0.31 | 0.307 | 0.321 | 0.298 | 0.306 | 0.321 | 0.324 | 0.317 | 0.32 | 0.308 | 0.32 | RF | 0.33 | 0.329 | 0.324 | 0.325 | 0.324 | 0.324 | RF | 0.322
|  | R | RF | RF | 0.318 | RF | RF | 0.33 | RF | RF | 0.31 | 0.327 | 0.319 | 0.309 | 0.326 | 0.329 | 0.32 | 0.316 | 0.331 | 0.32 | 0.317 | 0.315 | 0.33 | 0.329 | 0.321 | 0.324 | 0.327 | 0.324 | 0.324 | 0.313 | 0.315 | 0.319 | 0.321 | 0.323 | 0.308 | 0.306 | 0.326 | 0.321 | 0.311 | 0.313 | 0.328 | 0.307 | 0.315 | 0.318 | 0.331 | 0.322 | 0.322 | 0.323 | 0.308 | 0.319 | 0.31 | 0.314 | 0.325 | 0.318 | 0.323 | 0.322 | 0.321 | 0.324 | RF | 0.332 | 0.321 | 0.331 | RF | RF
A |  | L | 0.331 | RF | RF | 0.345 | RF | 0.321 | 0.333 | 0.324 | 0.327 | 0.32 | 0.324 | 0.319 | RF | 0.356 | 0.315 | 0.33 | 0.32 | 0.318 | 0.346 | 0.313 | 0.343 | 0.324 | 0.331 | 0.316 | 0.346 | 0.351 | 0.324 | 0.328 | 0.33 | 0.32 | 0.333 | 0.328 | 0.311 | 0.324 | 0.33 | 0.311 | 0.309 | 0.319 | 0.323 | 0.341 | 0.321 | 0.329 | 0.305 | 0.303 | 0.317 | 0.31 | 0.301 | 0.35 | 0.31 | 0.311 | 0.324 | 0.313 | 0.311 | 0.331 | 0.319 | 0.31 | 0.321 | 0.322 | 0.317 | 0.32 | 0.33 | 0.323
0.083 | -45 IN | C | 0.331 | RF | 0.312 | RF | 0.317 | RF | 0.326 | 0.326 | 0.325 | 0.315 | 0.305 | 0.328 | 0.328 | RF | 0.344 | 0.327 | 0.326 | 0.313 | 0.345 | 0.317 | 0.323 | 0.341 | 0.329 | 0.326 | 0.332 | 0.313 | 0.332 | 0.332 | 0.337 | 0.317 | 0.322 | 0.316 | 0.337 | 0.328 | 0.321 | 0.306 | 0.303 | 0.324 | 0.32 | 0.301 | 0.32 | 0.321 | 0.319 | 0.32 | 0.327 | 0.289 | 0.308 | 0.31 | 0.336 | 0.313 | 0.318 | 0.293 | 0.314 | 0.314 | 0.308 | 0.319 | 0.32 | 0.342 | 0.318 | 0.302 | 0.319 | 0.331
|  | R | 0.332 | RF | 0.369 | RF | 0.32 | 0.327 | 0.386 | 0.342 | 0.33 | 0.336 | 0.307 | 0.332 | 0.318 | 0.313 | 0.331 | 0.335 | 0.35 | 0.313 | RF | 0.296 | 0.339 | 0.323 | 0.325 | 0.332 | 0.322 | 0.327 | 0.332 | 0.359 | 0.338 | 0.339 | 0.328 | 0.319 | 0.316 | 0.365 | 0.325 | 0.306 | 0.311 | 0.327 | 0.326 | 0.304 | 0.327 | 0.351 | 0.312 | 0.321 | 0.32 | 0.313 | 0.32 | 0.306 | 0.31 | 0.324 | 0.327 | 0.302 | 0.322 | 0.317 | 0.314 | 0.33 | 0.324 | 0.311 | 0.329 | 0.331 | 0.338 | 0.334
A |  | L | 0.321 | 0.322 | 0.32 | 0.324 | 0.322 | 0.324 | RF | 0.307 | 0.313 | 0.324 | RF | 0.311 | 0.326 | 0.306 | 0.31 | 0.311 | 0.313 | RF | 0.322 | 0.294 | 0.301 | 0.327 | 0.302 | 0.302 | 0.316 | 0.293 | 0.302 | 0.317 | RF | 0.311 | 0.323 | 0.326 | 0.31 | RF | RF | 0.301 | 0.293 | 0.306 | 0.314 | 0.317 | 0.317 | 0.323 | 0.302 | RF | 0.319 | 0.304 | 0.296 | 0.314 | 0.32 | 0.308 | RF | 0.295 | 0.308 | 0.31 | 0.31 | 0.312 | 0.306 | 0.309 | RF | 0.306 | 0.311 | 0.304
0.083 | -54 IN | C | 0.326 | 0.318 | 0.311 | RF | 0.308 | RF | RF | RF | 0.322 | 0.327 | 0.299 | 0.306 | 0.299 | 0.298 | 0.316 | RF | RF | 0.304 | 0.305 | 0.285 | 0.307 | RF | 0.278 | RF | RF | 0.305 | 0.301 | RF | RF | RF | 0.317 | RF | 0.301 | RF | 0.316 | 0.301 | 0.296 | RF | 0.311 | 0.291 | RF | 0.311 | RF | 0.297 | RF | RF | RF | 0.307 | 0.307 | RF | RF | 0.277 | RF | 0.31 | 0.314 | RF | RF | 0.302 | RF | 0.306 | RF | 0.322
|  | R | 0.323 | 0.314 | RF | RF | 0.311 | RF | 0.31 | RF | 0.307 | 0.312 | RF | 0.315 | 0.311 | 0.305 | 0.31 | RF | RF | 0.325 | RF | 0.323 | 0.324 | 0.311 | 0.322 | 0.309 | 0.301 | 0.299 | 0.31 | 0.324 | 0.301 | 0.306 | 0.325 | RF | 0.309 | 0.31 | 0.315 | 0.301 | 0.301 | RF | 0.308 | 0.312 | 0.318 | 0.309 | 0.309 | 0.293 | RF | 0.303 | 0.31 | RF | 0.301 | RF | RF | RF | RF | 0.306 | 0.31 | RF | RF | RF | RF | 0.306 | 0.318 | 0.327
A |  | L | 0.329 | 0.316 | 0.318 | 0.319 | 0.301 | 0.317 | 0.318 | 0.331 | 0.304 | 0.313 | 0.307 | 0.31 | RF | 0.315 | 0.317 | 0.314 | 0.309 | 0.312 | 0.283 | 0.301 | 0.324 | 0.311 | 0.33 | 0.3 | 0.311 | 0.318 | 0.325 | 0.337 | 0.325 | 0.329 | 0.35 | 0.329 | 0.323 | 0.315 | 0.304 | 0.314 | 0.32 | 0.315 | 0.319 | 0.301 | 0.326 | 0.332 | 0.325 | 0.316 | 0.331 | 0.311 | 0.309 | 0.314 | 0.306 | 0.298 | 0.308 | 0.307 | 0.319 | 0.296 | 0.321 | 0.324 | 0.342 | 0.316 | 0.373 | RF | RF | 0.321
0.083 | -63 IN | C | 0.322 | RF | 0.316 | 0.321 | 0.304 | 0.327 | 0.315 | 0.313 | 0.303 | 0.302 | 0.295 | 0.335 | 0.301 | 0.29 | 0.311 | 0.338 | 0.323 | 0.321 | 0.298 | 0.318 | 0.321 | 0.315 | 0.324 | 0.321 | 0.341 | 0.307 | 0.333 | 0.323 | 0.313 | 0.319 | 0.322 | 0.319 | 0.317 | 0.315 | 0.316 | 0.313 | 0.294 | 0.303 | 0.303 | 0.299 | 0.323 | 0.307 | 0.301 | 0.296 | 0.329 | 0.302 | 0.3 | 0.304 | 0.295 | 0.295 | 0.293 | 0.309 | 0.3 | 0.292 | 0.32 | 0.327 | 0.318 | 0.317 | RF | RF | RF | 0.338
|  | R | 0.32 | 0.327 | 0.32 | 0.319 | 0.334 | 0.323 | 0.326 | 0.329 | 0.329 | 0.319 | 0.327 | 0.308 | 0.309 | 0.315 | 0.323 | 0.335 | 0.309 | 0.337 | 0.336 | 0.318 | 0.314 | 0.316 | 0.307 | 0.335 | 0.311 | 0.306 | 0.326 | 0.349 | 0.324 | 0.337 | 0.329 | 0.326 | 0.345 | 0.322 | 0.327 | 0.313 | 0.318 | 0.318 | 0.306 | 0.329 | 0.309 | 0.301 | 0.301 | 0.312 | 0.293 | 0.317 | 0.3 | 0.292 | 0.301 | 0.303 | 0.308 | 0.311 | 0.297 | 0.302 | 0.301 | 0.342 | 0.321 | 0.316 | RF | RF | RF | 0.321
A | POSITION 'A' | L |  |  | 0.331 | 0.327 |  | 0.336 | 0.325 |  | 0.32 | 0.305 |  | 0.307 | 0.306 |  | 0.33 | 0.322 |  | 0.311 | 0.319 |  | 0.326 | 0.318 |  | 0.323 | 0.324 |  |  | 0.317 | 0.321 |  | 0.328 | 0.324 |  | 0.32 | 0.315 |  |  | 0.326 | 0.327 |  | 0.321 | 0.321 |  | 0.316 | 0.314 |  | 0.316 | 0.331 |  | 0.328 | 0.315 |  | 0.32 | 0.319 |  | 0.338 | 0.322 |  | 0.327 | 0.315
0.083 | OF THE | C |  |  | 0.33 | 0.323 |  | 0.325 | 0.326 |  | 0.309 | 0.311 |  | 0.297 | 0.304 |  | 0.317 | 0.313 |  | 0.306 | 0.314 |  | 0.317 | 0.331 |  | 0.319 | 0.318 |  |  | 0.31 | 0.32 |  | 0.329 | 0.322 |  | 0.297 | 0.307 |  |  | 0.321 | 0.319 |  | 0.322 | 0.316 |  | 0.309 | 0.321 |  | 0.297 | 0.321 |  | 0.315 | 0.314 |  | 0.317 | 0.308 |  | 0.337 | 0.319 |  | 0.318 | 0.327
| PRIMARIES | R |  |  | 0.32 | 0.333 |  | 0.329 | 0.312 |  | 0.307 | 0.329 |  | 0.335 | 0.318 |  | 0.322 | 0.315 |  | 0.31 | 0.326 |  | 0.318 | 0.31 |  | 0.309 | 0.322 |  |  | 0.304 | 0.306 |  | 0.312 | 0.32 |  | 0.303 | 0.316 |  |  | 0.317 | 0.331 |  | 0.311 | 0.313 |  | 0.301 | 0.332 |  | 0.319 | 0.306 |  | 0.324 | 0.317 |  | 0.316 | 0.315 |  | 0.326 | 0.328 |  | 0.321 | 0.32
A | POSITION 'B' | L |  |  | 0.31 | 0.322 |  | 0.316 | 0.327 |  | 0.314 | 0.317 |  | 0.3 | 0.315 |  | 0.329 | 0.318 |  | 0.32 | 0.306 |  | 0.31 | 0.328 |  | 0.313 | 0.321 |  |  | 0.322 | 0.327 |  | 0.329 | 0.329 |  | 0.314 | 0.319 |  |  | 0.308 | 0.309 |  | 0.315 | 0.33 |  | 0.301 | 0.325 |  | 0.295 | 0.322 |  | 0.315 | 0.31 |  | 0.308 | 0.318 |  | 0.309 | 0.311 |  | 0.314 | 0.312
0.083 | OF THE | C |  |  | 0.312 | 0.316 |  | 0.313 | 0.315 |  | 0.331 | 0.311 |  | 0.308 | 0.309 |  | 0.335 | 0.321 |  | 0.307 | 0.313 |  | 0.314 | 0.317 |  | 0.316 | 0.317 |  |  | 0.303 | 0.323 |  | 0.322 | 0.327 |  | 0.312 | 0.329 |  |  | 0.329 | 0.318 |  | 0.317 | 0.323 |  | 0.317 | 0.323 |  | 0.306 | 0.304 |  | 0.297 | 0.304 |  | 0.313 | 0.305 |  | 0.309 | 0.357 |  | 0.358 | 0.307
| PRIMARIES | R |  |  | 0.328 | 0.314 |  | 0.327 | 0.324 |  | 0.314 | 0.307 |  | 0.309 | 0.305 |  | 0.308 | 0.319 |  | 0.313 | 0.315 |  | 0.306 | 0.32 |  | 0.307 | 0.308 |  |  | 0.304 | 0.331 |  | 0.306 | 0.317 |  | 0.3 | 0.317 |  |  | 0.322 | 0.312 |  | 0.312 | 0.312 |  | 0.32 | 0.312 |  | 0.308 | 0.302 |  | 0.303 | 0.317 |  | 0.319 | 0.311 |  | 0.314 | 0.322 |  | 0.359 | 0.306
A | POSITION 'C' | L |  |  | 0.303 | 0.319 |  | 0.322 | 0.315 |  | 0.319 | 0.308 |  | 0.316 | 0.319 |  | 0.327 | 0.318 |  | 0.307 | 0.323 |  | 0.302 | 0.319 |  | 0.31 | 0.326 |  |  | 0.315 | 0.327 |  | 0.326 | 0.323 |  | 0.328 | 0.32 |  |  | 0.33 | 0.322 |  | 0.325 | 0.316 |  | 0.322 | 0.317 |  | 0.322 | 0.318 |  | 0.323 | 0.339 |  | 0.301 | 0.315 |  | 0.322 | 0.33 |  | 0.307 | 0.322
0.083 | OF THE | C |  |  | 0.312 | 0.31 |  | 0.329 | 0.304 |  | 0.317 | 0.311 |  | 0.317 | 0.316 |  | 0.317 | 0.306 |  | 0.302 | 0.309 |  | 0.309 | 0.31 |  | 0.31 | 0.322 |  |  | 0.315 | 0.318 |  | 0.321 | 0.329 |  | 0.316 | 0.316 |  |  | 0.346 | 0.323 |  | 0.305 | 0.311 |  | 0.326 | 0.312 |  | 0.309 | 0.319 |  | 0.314 | 0.311 |  | 0.312 | 0.315 |  | 0.32 | 0.317 |  | 0.319 | 0.318
| PRIMARIES | R |  |  | 0.313 | 0.32 |  | 0.328 | 0.303 |  | 0.307 | 0.316 |  | 0.325 | 0.299 |  | 0.33 | 0.305 |  | 0.313 | 0.314 |  | 0.318 | 0.315 |  | 0.311 | 0.295 |  |  | 0.32 | 0.332 |  | 0.324 | 0.309 |  | 0.313 | 0.33 |  |  | 0.319 | 0.326 |  | 0.334 | 0.305 |  | 0.327 | 0.305 |  | 0.302 | 0.308 |  | 0.307 | 0.305 |  | 0.305 | 0.304 |  | 0.335 | 0.325 |  | 0.315 | 0.322
A |  | L | 0.357 | RF | 0.335 | 0.342 | 0.332 | 0.343 | 0.321 | 0.343 | 0.326 | 0.329 | 0.341 | 0.321 | 0.325 | 0.329 | 0.323 | 0.327 | 0.332 | 0.352 | 0.353 | 0.351 | 0.335 | 0.351 | 0.33 | RF | RF | RF | 0.326 | RF | 0.352 | 0.328 | 0.333 | 0.331 | 0.324 | 0.336 | 0.332 | 0.336 | 0.327 | 0.36 | 0.355 | 0.333 | 0.337 | 0.317 | 0.364 | 0.33 | 0.331 | 0.317 | 0.345 | 0.333 | 0.32 | 0.346 | 0.347 | 0.319 | 0.342 | 0.331 | 0.348 | 0.334 | 0.355 | 0.346 | 0.338 | 0.359 | 0.353 | 0.354
0.083 | -72 IN | C | 0.354 | RF | 0.336 | 0.387 | 0.333 | 0.324 | 0.321 | 0.329 | 0.322 | 0.325 | 0.346 | 0.322 | 0.328 | 0.36 | 0.323 | 0.327 | 0.356 | 0.322 | 0.313 | 0.332 | 0.354 | 0.333 | 0.352 | RF | RF | 0.325 | RF | RF | 0.348 | 0.336 | 0.324 | 0.316 | 0.337 | 0.331 | 0.358 | 0.352 | 0.347 | 0.356 | 0.346 | 0.318 | 0.335 | 0.333 | 0.33 | 0.319 | 0.348 | 0.312 | 0.317 | 0.321 | 0.318 | 0.324 | 0.324 | 0.34 | 0.323 | 0.322 | 0.331 | 0.346 | 0.332 | 0.344 | 0.343 | 0.339 | 0.352 | 0.359
|  | R | 0.355 | RF | 0.347 | 0.35 | 0.332 | 0.339 | 0.34 | 0.329 | 0.334 | 0.337 | 0.331 | 0.33 | 0.322 | 0.335 | 0.332 | 0.325 | 0.335 | 0.323 | 0.335 | 0.316 | 0.332 | 0.353 | 0.347 | RF | RF | RF | 0.331 | 0.334 | 0.351 | 0.333 | 0.338 | 0.33 | 0.341 | 0.352 | 0.337 | 0.352 | 0.35 | 0.327 | 0.327 | 0.324 | 0.325 | 0.346 | 0.325 | 0.324 | 0.33 | 0.318 | 0.332 | 0.324 | 0.33 | 0.327 | 0.339 | 0.345 | 0.317 | 0.325 | 0.336 | 0.343 | 0.343 | 0.349 | 0.359 | 0.353 | 0.353 | 0.359
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | AVG | MIN
C | 0.001-0.099 | 0.141-0.150 | 10: OUTSIDE DIAMETER:; 23: 2.969; 30: INSPECTION RESULTS
LEGEND | 0.100-0.110 | 0.151-0.160 | 10: TUBE MATERIAL:; 23: SA-178A; 35: MAX. THICKNESS
| 0.111-0.120 | 0.161-0.170 | 10: NOMINAL WALL:; 23: 0.18; 35: AVG. THICKNESS
| 0.121-0.130 | 0.171-0.180 | 10: ASME MIN:; 23: 0.099; 35: MIN. THICKNESS
| 0.131-0.140 | 0.181-0.999 | 10: MILL FLAG:; 23: 0.11; 35: STD DEV.
B | 0.001-0.083 | 0.124-0.133 | 10: OUTSIDE DIAMETER:; 23: 3; 30: INSPECTION RESULTS
LEGEND | 0.084-0.093 | 0.134-0.143 | 10: TUBE MATERIAL:; 23: SA210A1; 35: MAX. THICKNESS
| 0.094-0.103 | 0.144-0.153 | 10: NOMINAL WALL:; 23: 0.203; 35: AVG. THICKNESS
| 0.104-0.113 | 0.154-0.163 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS
| 0.114-0.123 | 0.164-0.999 | 10: MILL FLAG:; 23: 0.1; 35: STD DEV.
A | 0.001-0.083 | 0.140-0.149 | 10: OUTSIDE DIAMETER:; 23: 3; 30: INSPECTION RESULTS |  |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com | EXAMPLE PAPER
LEGEND | 0.100-0.109 | 0.150-0.159 | 10: TUBE MATERIAL:; 23: SA-210A1; 35: MAX. THICKNESS |  |  |  | RIVERDALE MILL
| 0.110-0.119 | 0.160-0.169 | 10: NOMINAL WALL:; 23: 0.3; 35: AVG. THICKNESS |  |  |  | TUBE WALL THICKNESS SURVEY
| 0.120-0.129 | 0.170-0.179 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS |  |  |  | NO. 1 RECOVERY BOILER
| 0.130-0.139 | 0.180-0.999 | 10: MILL FLAG:; 23: 0.2; 35: STD DEV.; 46: Job # H449364 P.O. # 0018342455 W.O. # N/A Date: 5/05/2025 |  |  |  | 04 REAR WALL W/ PORTS
THICKNESS
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Corrosion
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. CORROSION RATE MEASUREMENTS ARE IN MILS. | [66 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | AVG | MAX
C | POSITION 'A' | L | ND | ND | ND | ND | ND | ND | ND | ND | 2.55 | 8.53 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 9.56 | 1.71 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.888 | ND | ND | 2.08 | 8.53 | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | 0.178 | 0.948 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 11.7 | 0.413 | 0.297 | 11.9 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.03 | ND | ND | ND | ND | ND | ND | ND | ND
| TERTIARIES | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | 12.3 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 13.3 | 1.13 | ND | 9.28 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.07 | ND | ND | ND | ND | ND | ND | ND | ND
C | POSITION 'B' | L | ND | ND | ND | ND | ND | 0.059 | ND | ND | ND | ND | 0.768 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.815 | 1 | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | 0.655 | ND | 0.742 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.12 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| TERTIARIES | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.399 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
C | POSITION 'C' | L | ND | ND | ND | ND | ND | 1.32 | ND | ND | 0.575 | 4.74 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 10.3 | ND | 0.197 | 10.9 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.48 | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | 9.48 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.279 | 11.7 | ND | ND | 7.13 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.115 | ND | 0.012 | ND | ND | ND | ND | ND | ND
| TERTIARIES | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.84 | 0.186 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.11 | 10.3 | 2.41 | ND | 8.35 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.043 | ND | ND | ND | ND | ND | ND
B |  | L | 1.52 | 4.1 | 2.65 | 1.25 | 0.654 | 0.672 | 0.476 | 4.7 | 1.25 | ND | 1.41 | 2.23 | 0.631 | 3.18 | 3.01 | 3.03 | 1.99 | ND | 2.22 | 1.5 | 0.039 | 2.51 | 1.47 | 1.93 | 1.23 | ND | 0.726 | 3.56 | ND | 1.46 | 0.571 | ND | 0.132 | ND | 1.62 | ND | ND | ND | 1.34 | 1.36 | 0.538 | ND | 1.62 | ND | ND | 0.639 | 0.417 | ND | ND | 0.631 | ND | 1.45 | ND | 0.895 | 0.713 | 2.21 | 0.595 | ND | 1.08 | 0.149 | 5.39 | 6.66
| +16 FT 6 IN | C | 2.54 | 1.91 | 0.611 | 1.77 | 2.49 | 1.7 | 0.821 | 4.11 | 3.48 | 1.2 | 1.34 | ND | 1.33 | 1.92 | 3.3 | 2.42 | 0.973 | 1.79 | 0.803 | 0.865 | 1.13 | 1.84 | 8.99 | 1.91 | 0.344 | ND | 1.31 | 1.38 | 0.021 | ND | ND | ND | ND | 1.01 | 0.359 | ND | ND | 6.06 | ND | ND | 1.15 | ND | ND | ND | ND | ND | 0.478 | ND | 0.295 | 0.501 | 0.683 | 2.11 | 0.282 | 0.333 | 2.4 | 0.448 | 0.016 | 2.73 | 0.537 | 1.33 | 1.02 | ND
|  | R | 0.703 | ND | 3.24 | 0.73 | 1.75 | 0.019 | 1.67 | 0.786 | 3.16 | 1.76 | 0.877 | 1.11 | 0.815 | ND | 3.3 | 1.94 | 1.29 | 3.25 | 2.18 | 2.18 | 2.16 | 1 | ND | ND | 0.296 | ND | 0.475 | ND | 0.265 | ND | 1.09 | ND | ND | ND | 0.565 | ND | ND | 1.23 | 0.302 | ND | 0.461 | ND | ND | ND | 0.627 | ND | 0.269 | ND | ND | 0.458 | ND | 2.63 | 1.96 | 0.069 | 1.78 | 0.722 | 0.722 | ND | 0.657 | ND | 1.41 | ND
B |  | L | 1.16 | 2.89 | 4.63 | 6.87 | 3.71 | 1.9 | 2.55 | 3.43 | 2.56 | 3.86 | 3.58 | 1.36 | 4.69 | 0.729 | 3.55 | 0.668 | 1.51 | 3.58 | 2.83 | 4.94 | 5.56 | 1.86 | 5.52 | 3.24 | 4.43 | 2.8 | 3.76 | ND | 2.29 | 2.79 | 0.859 | 1.69 | ND | ND | 3.07 | 2.21 | 2.04 | 5.67 | 4.09 | 4.83 | 2.34 | 2.6 | 1.87 | 5.56 | 1.62 | 2.13 | 3.74 | 2.51 | 2.24 | 1.67 | 2.39 | ND | 3.1 | 1.97 | 1.41 | 1.53 | 1.92 | 7.93 | 4.28 | 1.34 | 3.43 | ND
| +15 FT | C | ND | 0.907 | 0.309 | 3.15 | 0.94 | 0.968 | ND | 1.92 | 1.53 | 3.98 | 4.02 | 1.81 | ND | 1.19 | 3.14 | 2.47 | ND | 3.41 | 1.64 | 3.58 | 2.79 | 1.67 | 2.3 | 3.04 | 2.28 | 0.821 | 0.247 | 0.6 | 2 | 0.699 | 6.74 | 0.985 | 1.56 | 0.321 | 1.64 | 0.746 | 2.07 | 1.71 | 0.025 | 2.51 | 1.75 | 4.35 | 1.53 | 6.1 | 1.04 | 0.662 | 2.99 | 2.07 | 1.33 | 3.18 | 1.34 | ND | ND | ND | ND | 3.26 | 3.44 | 4.41 | 2.98 | 2.61 | 1.84 | 0.552
|  | R | 7.87 | 4.34 | 2.25 | 7.45 | 4.52 | 2.58 | 4.04 | 5.18 | 2.71 | 4.27 | 3.12 | ND | 1.33 | 4.35 | 4.08 | 0.881 | 1.9 | 3.83 | 2.12 | 0.55 | 2.42 | 1.83 | 2.09 | 1.45 | 0.839 | ND | 1.02 | 2.97 | 0.533 | 1.66 | 1.38 | 1.11 | 2.67 | 5.22 | 2.28 | 3.41 | 4.12 | ND | 7.96 | 3.9 | 1.84 | ND | 2.21 | 1.85 | 1.54 | 1.07 | 0.337 | 1.09 | 1.85 | 1.11 | 0.97 | 1.53 | 1.02 | 1.89 | 0.337 | ND | 1.56 | 3.02 | 3.16 | 0.869 | 1.54 | 1.54
B |  | L | 3.25 | 3.3 | 2.95 | 6.63 | 8.21 | 9.06 | 5.59 | 3.83 | 6.39 | 3.98 | 8.81 | 4.84 | 11.1 | 14 | 0.973 | 11.9 | 4.84 | 4.63 | 6.84 | 0.56 | 1.98 | 4.29 | 12.4 | 1.78 | 0.632 | 3.47 | 1.79 | 9.31 | 3.35 | 0.844 | 1.59 | 3.13 | 4.42 | 2.37 | 1.21 | 4.91 | 5.66 | 3.77 | 3.19 | 5.22 | 3.41 | 4.9 | 5.13 | 5.22 | 6.5 | 0.043 | 0.625 | 4.49 | ND | 5.24 | 3.93 | 5.65 | 0.503 | 2.39 | 2.37 | 3.93 | 1.92 | 2.84 | 4.52 | 2.43 | 3.32 | 5.53
| +13 FT 6 IN | C | 6.78 | 2.38 | 3.31 | 9.59 | 1.34 | 4.65 | 0.584 | 4.29 | 6.76 | 2.33 | 1.57 | 4.26 | 3.33 | 11.3 | 6.1 | 3.79 | 3.68 | 2.74 | 3.63 | 2.76 | 3.41 | 2.65 | 2.04 | 2.6 | 1.86 | 2.71 | 2.43 | 4.91 | 1.26 | 5.89 | 3.89 | 1.83 | 2.72 | 1.49 | 1.08 | 2.61 | ND | 3.01 | 3.97 | 4.24 | 7.47 | 4.43 | 5.18 | 3.94 | 3.26 | 2.42 | 0.043 | 1.78 | 1.86 | 4.67 | 6.72 | 2.31 | 1.83 | 0.094 | 3.94 | 2.72 | 1.76 | 4.14 | 2 | 7.18 | 4.29 | 2.57
|  | R | 7.04 | 0.589 | ND | 1.3 | 1.4 | 3.3 | 1.44 | 2.64 | 9.55 | 1.47 | 1.8 | 7.16 | 1.64 | 2.16 | 3.56 | 2.3 | 8.65 | 5.47 | 1.43 | ND | ND | 3.83 | ND | 2.47 | 2.34 | 1.04 | 3.83 | 2.51 | 1.47 | 6.15 | 4.55 | 0.932 | 1.71 | 6.6 | 4.44 | 2.72 | 2.04 | 3.78 | 2.87 | 3.62 | 2.32 | 1.44 | 2.15 | 3.49 | ND | 4.15 | 1.59 | 2.11 | 2.67 | 3.36 | 2.58 | 3.17 | 1.43 | 2.59 | 3.33 | 1.66 | 0.509 | 0.828 | 1.65 | 3.74 | 2.66 | 5.23
B |  | L | 7.57 | 4.9 | 0.479 | 2.23 | 1.35 | 0.756 | 0.192 | 3.34 | 3.14 | 3.57 | 2.43 | 4.51 | 4.92 | 2.77 | 5.92 | 2.47 | 5.35 | 1.76 | 3.15 | 0.397 | 3.97 | 2.37 | 3.76 | 2.69 | ND | 2.97 | 1.64 | 7.4 | 0.052 | 2.6 | 3.17 | 3.01 | 4.18 | 2.31 | 2.36 | 2.36 | 1.15 | ND | 1.98 | 4.65 | 3.71 | 3 | 0.523 | 3.46 | 4.22 | 4.38 | 3.28 | 2.6 | 4.11 | 2.64 | 4.38 | 3.28 | 1.01 | 2.53 | 2.9 | 1.67 | 1.91 | 5.1 | ND | 2.61 | 0.095 | 6.3
| +12 FT | C | 4.27 | 0.702 | 3.32 | 1.35 | 3.33 | 0.038 | 0.889 | 4.52 | 1.54 | 2.25 | 3.41 | 4.02 | 2.42 | 1.75 | 3.01 | 1.44 | 2.12 | 2.54 | 2.93 | 0.937 | 1.75 | 1.71 | 4.62 | 1.94 | 3.02 | 1.95 | 2.51 | 2.96 | 1.68 | 0.862 | 2.55 | 1.53 | 3.85 | 1.62 | 2.14 | 3.34 | 1.41 | 3.76 | 2.56 | ND | 1.19 | 3.19 | 5.16 | 4.43 | 3.13 | 2.28 | 0.947 | 3.91 | 4.48 | 5.83 | 3.29 | 3.45 | 2.46 | 1.1 | 4.78 | 0.856 | 2.26 | 3.32 | ND | 2.22 | 1.35 | 4.03
|  | R | 3.8 | 0.019 | 1.16 | 2.01 | 2.31 | 5.8 | 2.86 | 1.39 | 0.305 | 4 | 1.84 | 10 | 4.77 | 3.12 | 5.64 | 3.81 | 3.48 | 3.41 | 2 | 1.3 | 4.26 | 3.03 | 8.48 | 1.21 | 1.81 | 0.56 | 1.82 | 2.32 | 1.03 | 1.53 | 1.95 | 3.78 | 4.17 | 1.36 | 2.73 | 1.38 | 3.67 | 1.56 | ND | 0.353 | 2.42 | 1.34 | 4.01 | ND | 0.236 | 2.01 | 0.814 | 3.71 | 4.26 | 2.26 | 0.954 | 5.64 | 5.02 | 1.65 | 10.6 | 1.61 | 1.69 | 3.37 | 3.82 | ND | 0.144 | 2.51
B | POSITION 'A' | L | ND | ND | ND | ND | 2.81 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.73 | 0.702 | ND | 0.119 | ND
| OF THE | C | ND | 1.52 | ND | ND | 1.36 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4.82 | 0.808 | 0.627 | 1.76 | ND
| OB PORTS | R | ND | ND | 1.68 | ND | 3.32 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.08 | 0.91 | 0.034 | 1.48 | ND
B | POSITION 'B' | L | ND | 1.18 | ND | 1.89 | 2.63 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.05 | ND | 3.74 | 1.53 | ND
| OF THE | C | ND | 0.235 | ND | ND | 0.552 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.45 | 3.57 | ND | 0.424 | ND
| OB PORTS | R | ND | ND | 0.099 | 0.381 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.969 | 1.03 | 1.09 | 0.385 | ND
B | POSITION 'C' | L | ND | 1.65 | ND | ND | 2.1 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.52 | ND | ND | 1.04 | ND
| OF THE | C | ND | 1.55 | ND | 0.659 | 1 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.16 | 2.67 | ND | 1.94 | ND
| OB PORTS | R | ND | 3.13 | ND | 0.292 | 1.64 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.78 | 0.198 | 0.983 | 5.41 | ND
B |  | L | 2.19 | 3.8 | 2.61 | 0.331 | 2.98 | 2.45 | ND | 3.79 | 0.516 | 1.94 | 4.66 | 3.56 | 3.21 | 3.22 | 5.63 | 4.55 | 5.59 | 1.5 | 4.03 | 3.7 | 11.6 | 3.01 | 2.97 | 0.858 | 4.27 | 1.69 | 3.22 | 0.895 | 9.29 | 2.39 | 1.71 | 2.36 | 0.147 | 0.615 | 3.71 | 2.89 | 2.27 | ND | 4.46 | 5.64 | 3.65 | 5.92 | 8.1 | 3.99 | 2.22 | 4.64 | 2.31 | 3.21 | 1.8 | 5.35 | 3.94 | 0.98 | 2.17 | 5.51 | 1.91 | 0.731 | 3.6 | 2.82 | 2.61 | 2.61 | 0.632 | 2.08
| +10 FT 6 IN | C | 4.9 | 3.02 | 0.312 | ND | 3.16 | 1.71 | 2.46 | 2.8 | 1.46 | 2.1 | ND | 3.04 | 4 | 6.4 | 2.27 | 3.67 | 4.13 | ND | 3.12 | 4.46 | 4.6 | 1.94 | 1.01 | 2.38 | 5.32 | 0.492 | 1.97 | ND | 2.16 | 4.57 | 1.8 | 2.47 | 1.57 | 0.15 | 3.8 | 3.85 | 3.57 | 1.19 | 6.12 | 6.03 | 2.19 | 2.71 | 1.79 | 2.14 | 4.52 | 0.738 | 3.05 | 4.52 | 4.97 | 2.75 | 4.78 | 2.34 | 1.96 | 7.14 | 3.12 | 1.86 | 0.404 | 0.035 | 2.26 | 0.799 | 1.71 | 0.543
|  | R | 1.25 | 3.15 | ND | ND | 1.48 | 1.42 | 1.82 | 5.87 | 5.54 | 3.08 | 6.68 | 2.75 | 4.11 | 5.68 | 1.48 | 3.24 | 3.37 | 5.63 | 4.2 | 1.21 | 4.83 | 3.41 | 2.83 | 3.54 | 3.73 | 3.01 | 1.03 | 2.1 | 2.63 | 4.77 | 2.35 | ND | 1.32 | 0.363 | 1.42 | 0.241 | 4.83 | 0.889 | 2.96 | 3.07 | 3.65 | 1.77 | 1.55 | 2.65 | 5.11 | 0.606 | 4.17 | 0.248 | 7.39 | 2.75 | 0.901 | 3.94 | 0.842 | 2.07 | 1.87 | 3.61 | 3.11 | 1.42 | 2.89 | 1.27 | ND | ND
B |  | L | ND | 0.922 | ND | 0.019 | 1.22 | 1.58 | 4.92 | ND | 3.16 | ND | 6.31 | 0.26 | 5.38 | 6.91 | 0.253 | 1.7 | 5.35 | ND | ND | 0.549 | 0.517 | 1.73 | ND | 1.66 | 1.32 | 2.68 | 2.39 | ND | 3.93 | 4.65 | 13.5 | 0.75 | ND | 0.919 | 2.04 | 5.12 | 2.01 | 2.65 | 2.78 | 3.79 | 2.04 | 4.37 | ND | 5.25 | 2.34 | ND | 2.19 | 0.963 | 3.84 | 0.501 | ND | 0.065 | 0.748 | 1.85 | ND | 1.18 | 1.99 | 3.61 | 0.214 | 0.154 | 3.51 | 0.062
| +9 FT | C | 0.757 | 2.36 | ND | ND | ND | 1.5 | 2.47 | 2.94 | 1.71 | 1.54 | 3.62 | 1.68 | 4.5 | ND | 0.116 | 0.777 | 4.15 | ND | ND | 0.921 | 2.06 | 3.38 | 3.39 | 2.84 | ND | 2.99 | ND | 0.548 | 1.59 | 7.52 | 13.1 | ND | 5.43 | ND | ND | 5.14 | 0.839 | ND | 2.17 | 3.36 | ND | 1.35 | ND | 6.49 | 6.37 | 4.46 | 4.15 | 0.292 | 1.6 | 0.529 | ND | ND | 0.056 | 1.75 | ND | 0.918 | ND | 0.184 | 1 | 1.1 | 1.91 | 0.969
|  | R | ND | ND | ND | 1.61 | 0.224 | 0.377 | 3.12 | 0.734 | 2.04 | 2.42 | ND | 0.623 | 4.83 | ND | 1.9 | 1.31 | 1.45 | ND | 0.017 | 2.88 | 0.599 | 1.2 | 6.92 | ND | 2.37 | ND | 5.6 | 0.958 | 4.56 | 3.14 | 1.29 | 7.14 | ND | 4.34 | 1.63 | 4.73 | 2.87 | 1.65 | 1.05 | ND | 0.606 | 4.36 | ND | 1.8 | 4.04 | 0.869 | 5.14 | 5.97 | 7.29 | 3.1 | 3.49 | ND | 1.74 | ND | ND | 1.52 | ND | 1.84 | ND | ND | ND | 2.42
B | POSITION 'A' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.17 | ND | ND | 0.465 | ND | 3.23 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.92 | ND | 0.159 | 2.36 | 0.668 | 1.89 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.13 | ND | 1.07 | 1.52 | 0.049 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B | POSITION 'B' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.34 | ND | 2.88 | 1.76 | 4 | 0.635 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.53 | 0.185 | 0.82 | 1.93 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.089 | 1.54 | 0.308 | 1.07 | 5.51 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B | POSITION 'C' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.07 | ND | 0.097 | ND | 1.91 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.47 | ND | 3.54 | 1.57 | 0.681 | 0.153 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.961 | ND | 0.527 | ND | ND | 1.87 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B | POSITION 'D' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.607 | 2.15 | 0.738 | ND | ND | 1.25 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.61 | ND | 1.33 | ND | 1.1 | 1.57 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.416 | 1.53 | ND | ND | 1.36 | 2.75 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B | POSITION 'E' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.792 | ND | 1.65 | ND | ND | 4.77 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.61 | 3.04 | 1.2 | 0.505 | 0.591 | 4.23 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.33 | ND | ND | 1.45 | 0.196 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B |  | L | 0.482 | 10 | 0.272 | 0.347 | ND | 0.411 | ND | ND | ND | 0.303 | 1.99 | ND | 6.05 | 1.51 | 0.17 | 5.98 | 0.733 | 1.93 | 0.921 | 2.76 | 0.913 | 2.52 | 1.34 | 1.09 | ND | ND | 4.68 | ND | 4.97 | 1.11 | 0.056 | ND | 2.14 | ND | 2.41 | 7.62 | 1.53 | 0.287 | 5.84 | ND | ND | ND | ND | 0.917 | 5.75 | ND | ND | 2.29 | 0.553 | ND | ND | 2.26 | 2.44 | 4.02 | ND | 2.36 | ND | ND | 2.38 | ND | 3.35 | 6.91
| +7 FT 6 IN | C | ND | 4.41 | ND | 0.632 | 1.87 | 0.437 | 0.454 | ND | 0.534 | 0.172 | ND | ND | ND | ND | ND | 1.02 | ND | 2.84 | ND | 1.55 | ND | 0.576 | 1.55 | ND | ND | ND | 3.85 | 4.11 | 1.87 | ND | 1.78 | 1.28 | ND | 5.18 | 2.03 | 0.091 | 1.11 | 0.464 | 1.85 | 1.12 | 1 | 0.579 | 1.29 | 0.226 | 3.72 | 0.282 | 0.495 | 0.633 | ND | 1.73 | 0.778 | ND | 1.05 | ND | 2.75 | 0.91 | 1.91 | ND | 1.08 | 0.598 | 1.52 | 0.622
|  | R | ND | 3.74 | 1.78 | 1.21 | ND | ND | ND | ND | ND | 2.58 | 0.16 | ND | 1.21 | ND | ND | 1.36 | ND | 3.02 | ND | 0.64 | ND | 1.87 | 1.21 | 1.2 | ND | 0.314 | 4.02 | 2.14 | 1.38 | 0.896 | 1.02 | 2.6 | 0.93 | ND | 2.42 | 5.97 | 0.523 | ND | 1.56 | 1.75 | 1.9 | ND | ND | 0.686 | 4.19 | 0.837 | 1.01 | ND | 0.691 | 0.861 | 1.92 | 1.89 | 1.96 | 1.47 | 2.34 | 1.21 | 1.53 | 1.92 | 2.78 | ND | 1.26 | ND
B |  | L | 5.23 | 2.98 | ND | 0.746 | 0.971 | 1.19 | ND | ND | ND | 0.106 | 0.12 | 1.97 | ND | 1.88 | ND | ND | ND | 2.04 | ND | 3.18 | 4.4 | 4.52 | 2.89 | 4.72 | 0.363 | 2.53 | 1.98 | ND | 3.38 | ND | ND | 3.86 | 2.79 | 1.87 | 1.77 | ND | 1.35 | 0.674 | 3.1 | 0.464 | 2.19 | 1.61 | 0.505 | ND | 2.39 | 1.17 | 1.93 | ND | 1.9 | 0.117 | ND | 1.5 | 0.824 | ND | ND | ND | ND | 0.397 | 2.26 | 1.61 | 0.515 | 3.37
| +6 FT | C | 1.12 | 4.9 | ND | ND | ND | ND | ND | 0.963 | ND | 1.06 | ND | ND | 0.178 | ND | 0.318 | 1.82 | 0.993 | 1.08 | 0.901 | 2.52 | 2.72 | 5.07 | 6.07 | 5.25 | 0.341 | 1.68 | 1.1 | ND | 6.58 | 6.96 | ND | 5.04 | 3.23 | 0.636 | 1.98 | 0.055 | ND | ND | 4.89 | ND | 1.14 | ND | ND | 5.48 | ND | 1.83 | 1.11 | 1.95 | 0.723 | 2.05 | 0.577 | 2.4 | 2.95 | ND | 1.77 | ND | 1 | 0.512 | 0.301 | ND | ND | 1.45
|  | R | 2.37 | 5.28 | ND | ND | 1.38 | ND | 0.115 | ND | ND | ND | 0.935 | ND | 3.12 | ND | 0.415 | 0.793 | 2.16 | 2.06 | 0.337 | 0.073 | ND | 3.28 | 2.26 | 3.13 | 1.47 | 1.93 | 1.07 | 0.871 | 4.31 | 5.24 | 0.752 | 5.18 | 1.5 | 0.046 | 2.53 | 0.323 | 0.207 | ND | 0.45 | 2.51 | 2.83 | 3.37 | 2.82 | 5.28 | 0.23 | ND | ND | 1.21 | 1.5 | 1.51 | ND | ND | 1.79 | ND | 1.53 | ND | 0.471 | 1.2 | 2.39 | 0.049 | 1.74 | 0.924
B |  | L | 1.39 | 4.92 | 1.23 | 0.74 | 1.52 | 4.51 | 1.07 | 1.76 | 1.6 | ND | ND | 3.82 | 2.72 | ND | 1.01 | 1.37 | ND | 1.94 | 3.61 | 3.52 | 3.38 | 2.58 | ND | 1.72 | ND | 0.985 | 4.16 | 5.03 | 0.974 | 1.99 | 2.83 | 4.62 | 1.87 | 1.37 | 1.57 | 0.934 | 0.604 | 1.12 | 0.297 | 0.193 | 0.591 | 0.613 | 0.226 | ND | 0.696 | ND | ND | ND | ND | ND | 1.14 | ND | 0.187 | 0.971 | 1.34 | 0.963 | 0.829 | 1.02 | 1.53 | 3.12 | 3.72 | ND
| +4 FT 6 IN | C | ND | 1.18 | 0.692 | ND | 1.87 | ND | 0.811 | ND | ND | 0.474 | 0.311 | 0.358 | 1.78 | 0.676 | 1.48 | 3.09 | 1.73 | 1.39 | 0.301 | 2.01 | 1.3 | 3.7 | 0.477 | ND | 2.97 | ND | 7.28 | ND | 0.272 | 6.64 | 0.226 | 5.72 | 1.98 | 0.532 | 1.09 | 2.51 | 1.12 | 0.359 | 0.792 | 1.71 | 3.11 | 2.28 | ND | 3.72 | 2.25 | ND | 1.65 | 0.643 | ND | ND | ND | 1.04 | 0.113 | 1.82 | 0.551 | 1.53 | 1.82 | 1.23 | 0.714 | 0.397 | 3.54 | 2.13
|  | R | ND | ND | ND | ND | 1.41 | 1 | ND | ND | 0.663 | 0.523 | 0.605 | ND | ND | 0.17 | 0.604 | 1.35 | ND | 1.57 | 2.24 | 0.108 | 2.87 | 3.96 | 2.24 | ND | 2.29 | 3.12 | 3.81 | 0.75 | 2.94 | 6.76 | 1.82 | 9.29 | 2.85 | 1.16 | 4.47 | 0.798 | 3.28 | 2.72 | 1.49 | 0.026 | 1.62 | 0.498 | 2.67 | ND | ND | ND | 2.26 | 0.974 | ND | 2.33 | ND | 1.57 | 1.87 | 1.38 | 1.67 | 1.49 | 1.45 | 0.072 | 0.534 | 0.825 | 2.11 | 2.75
B |  | L | ND | ND | 3.98 | 3.16 | 2.3 | ND | ND | ND | 0.269 | ND | 1.04 | 0.325 | ND | 0.419 | 0.64 | 3.88 | 1.71 | 0.502 | 1.87 | 1.57 | 0.61 | 0.426 | 2.47 | 1.69 | 0.055 | ND | ND | 0.951 | 2.12 | 3.04 | ND | 1.59 | 5.25 | 0.849 | 0.415 | 5.95 | ND | ND | 3.48 | 2.85 | 4.06 | 2.44 | 1.49 | 3.26 | 1.34 | 2.18 | 1.23 | 0.636 | 1.19 | 2.47 | 2 | 1.48 | 0.202 | 8.1 | 0.692 | 2.5 | ND | ND | 1.41 | 0.571 | 1.98 | ND
| +3 FT | C | 3.76 | 2.3 | ND | ND | 0.541 | 0.441 | ND | 1.12 | 3.42 | ND | ND | ND | 0.661 | ND | 0.489 | ND | 0.374 | ND | 1.51 | 0.161 | ND | ND | ND | 0.333 | ND | 0.642 | ND | ND | ND | 5.54 | ND | 1.22 | 0.954 | ND | ND | 0.31 | ND | 2.24 | 2.86 | ND | ND | 4.17 | 0.324 | ND | 0.212 | ND | 1.55 | 4.65 | ND | 2.76 | 0.578 | 1.11 | 0.839 | 8.68 | 0.198 | 3.72 | 0.751 | 1.16 | 0.053 | 0.296 | 3.17 | 4.37
|  | R | ND | ND | 0.786 | ND | 0.673 | ND | 2.07 | ND | 1.06 | ND | ND | ND | ND | 0.059 | ND | ND | ND | 0.349 | ND | ND | ND | ND | 0.466 | ND | ND | ND | ND | ND | ND | 0.956 | ND | ND | 5.47 | ND | ND | 5.38 | 3.41 | 4.58 | 2.5 | ND | ND | 2.26 | ND | 1.13 | 0.572 | 2.54 | 0.298 | 1.5 | 1.7 | 3.02 | 0.766 | 1.15 | 4.44 | 5.52 | 0.052 | 0.261 | 0.864 | 1.01 | 0.411 | 0.969 | 3.48 | 4.03
B |  | L | ND | 0.697 | 1.93 | ND | ND | 1.48 | 1.53 | 1.15 | ND | ND | ND | ND | ND | 1.68 | 0.393 | 1.88 | ND | 0.529 | ND | 0.138 | ND | ND | 1.25 | 0.233 | 1.56 | 0.119 | 0.399 | ND | 4.85 | ND | ND | 8.61 | ND | ND | ND | ND | 2.09 | ND | ND | ND | 3.16 | ND | ND | 2.31 | 2.45 | 2.08 | ND | ND | ND | 0.89 | 0.143 | ND | ND | 0.843 | 0.325 | 1.67 | 0.037 | 2.78 | ND | ND | ND | ND
| +1 FT 6 IN | C | 2.15 | 4.18 | ND | 0.519 | 0.126 | 0.614 | 0.339 | ND | 0.087 | 2.21 | 1.99 | 1.33 | ND | 1.35 | ND | ND | 2.65 | ND | ND | ND | ND | ND | ND | ND | 1.53 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.51 | 0.965 | ND | 0.787 | 1.08 | ND | 0.022 | ND | ND | ND | ND | ND | 0.804 | 1.32 | 0.763 | 3.47 | 2.58 | 5.11 | 0.76 | 2.23 | 0.75 | 0.272 | 0.964 | 0.601 | 1.82 | ND
|  | R | ND | ND | ND | 1.07 | ND | 1.72 | 0.999 | 0.089 | ND | 1.59 | ND | ND | ND | ND | ND | ND | 2.9 | 1.82 | ND | ND | 0.743 | ND | ND | ND | ND | 1.74 | ND | ND | ND | ND | 3.95 | ND | ND | 0.484 | 0.022 | ND | ND | ND | 0.314 | ND | 0.325 | 3.13 | 3.58 | 1.18 | 9.05 | 3.85 | 5.33 | 8.46 | 5.68 | 5.62 | 1.74 | 3.84 | 2.53 | ND | 5.08 | 5.55 | 1.88 | 0.948 | ND | ND | ND | ND
B |  | L | ND | ND | 0.085 | ND | 1.13 | ND | 3.58 | 1.37 | 0.895 | 0.568 | 0.108 | 2.5 | 0.876 | 1.75 | 0.24 | 1.7 | 2.54 | 1.66 | ND | ND | ND | ND | 2.28 | 0.814 | 0.78 | ND | 0.49 | ND | 1.74 | ND | 0.317 | ND | 0.006 | ND | 1.45 | 0.972 | ND | 0.428 | 0.362 | ND | 0.349 | 0.76 | ND | ND | ND | 1.45 | ND | 0.044 | ND | 0.989 | 1.75 | 3.09 | 3.01 | 5.25 | 0.02 | ND | 5.43 | 2.69 | 1.95 | 4.74 | 0.982 | ND
| 0 REFERENCE | C | ND | ND | ND | 0.3 | 1.7 | 1.25 | 0.757 | 0.048 | 1.48 | ND | ND | 1.63 | 1.34 | 0.809 | 0.778 | 1.04 | 0.95 | ND | 1.6 | 0.36 | ND | 0.364 | ND | ND | 2.06 | ND | ND | ND | 1.49 | ND | 1.74 | ND | ND | ND | ND | ND | ND | 1.95 | 3.06 | 2.22 | ND | ND | ND | ND | 4.77 | ND | 1.71 | 2.62 | 4.79 | ND | 4.43 | ND | 3.16 | ND | 4.1 | 9.5 | 1.17 | 4.9 | 1.75 | 3.27 | 0.652 | 0.289
|  | R | ND | ND | ND | 2.29 | 1.73 | 1.68 | 1.7 | 1.99 | 1.75 | 1.99 | 1.19 | ND | ND | 2.28 | ND | 0.785 | 1.32 | 2.05 | 1.87 | ND | ND | 0.327 | ND | 2.9 | 1.46 | ND | ND | 0.179 | 4.11 | ND | 1.57 | ND | 2.18 | ND | ND | ND | ND | 0.622 | 0.285 | ND | 6.94 | ND | 7.21 | 4.73 | ND | 7.38 | ND | ND | ND | ND | 6.9 | 4.46 | 8.29 | 8.37 | 7.9 | 12.6 | 6.72 | 4.53 | ND | 1.47 | ND | 11.1
B | POSITION 'A' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.406 | ND | 2.88 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.24 | 1.03 | 3.95 | 1.4 | 0.499 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| SECONDARIES | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4.5 | 4.11 | ND | ND | ND | 0.295 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B | POSITION 'B' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.01 | ND | 0.238 | 1.16 | 1.9 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2 | ND | 1.8 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| SECONDARIES | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.31 | 4.35 | 3.04 | 6.3 | 4.1 | 2.68 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B |  | L | ND | 8.02 | 2.07 | 1.11 | 2.89 | 1.27 | 0.789 | 0.955 | 0.121 | 2.11 | 1.45 | 0.259 | 2.38 | 0.773 | 1.57 | 1.94 | 0.345 | 1.69 | 0.059 | 0.46 | 1.81 | ND | ND | 0.131 | ND | 0.286 | 0.631 | 0.469 | 1.63 | ND | 1.34 | 0.701 | ND | 1.82 | ND | ND | ND | 0.964 | ND | 2.51 | 3.22 | 2.72 | 0.183 | 3.39 | 3.58 | 2.73 | ND | ND | 0.104 | 0.499 | ND | 0.793 | ND | ND | 1.16 | 3.98 | 0.702 | 0.187 | ND | ND | 1.23 | 2.06
| -9 IN | C | 3.11 | 0.646 | 0.592 | ND | 1.63 | 1.04 | 1.33 | 0.522 | ND | 2.33 | 1.39 | 2.03 | ND | 2.95 | 0.44 | 0.918 | 1.78 | 2.54 | 3.19 | 2.25 | 4.24 | 1.69 | 1.1 | 1.72 | 3.81 | 2.92 | 1.35 | ND | 2.01 | 0.232 | ND | 0.21 | 0.243 | 8.78 | 1.89 | 5.64 | 2.46 | ND | ND | 5.76 | 2.31 | 0.495 | ND | 2.04 | 0.923 | 0.666 | ND | ND | 0.032 | 3.55 | 1.01 | 4.46 | 1.29 | ND | 3.69 | 4.89 | ND | 0.974 | 3.47 | 2.2 | ND | 0.042
|  | R | ND | 0.283 | 4.45 | 1.27 | 0.165 | 2.4 | ND | 1.49 | 2.93 | 1.68 | 1.66 | 0.818 | 0.749 | 0.251 | 0.112 | 0.187 | 0.523 | ND | 2.11 | 1.41 | 3.2 | ND | ND | 0.607 | ND | 1.21 | 0.512 | ND | ND | ND | ND | 1.56 | 0.219 | ND | 4.37 | ND | ND | ND | ND | ND | ND | ND | ND | 2.54 | 2.2 | ND | 2.01 | ND | ND | 0.475 | ND | 3.17 | 5.8 | ND | 6.46 | 5.14 | 1.48 | 3.01 | ND | ND | 16.7 | 1.4
B | POSITION 'C' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.78 | 3.58 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.42 | 1.76 | 0.831 | 1.15 | 2.31 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| SECONDARIES | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.28 | 1.21 | 0.36 | 5.38 | 6.07 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
B |  | L | ND | 0.122 | 2.42 | 1.55 | 4.05 | 0.635 | 1.65 | 0.449 | 1.54 | 0.208 | 0.749 | ND | 1.71 | 0.888 | 1.69 | 1.89 | 2.26 | 0.63 | 3.36 | 1.62 | 0.203 | 1.41 | ND | 0.999 | 1.57 | 0.788 | ND | 0.505 | 1.99 | 1.42 | 0.62 | ND | 2.6 | 0.176 | 1.93 | ND | 0.478 | 0.206 | 0.947 | ND | ND | ND | ND | 0.505 | 0.492 | ND | ND | ND | 0.435 | ND | ND | 0.603 | ND | ND | 2.85 | ND | 0.4 | 1.06 | ND | 1.73 | 2.43 | 0.652
| -18 IN | C | ND | ND | 4.27 | ND | 4.36 | 1.48 | 0.476 | ND | 0.873 | ND | 2.95 | 2.53 | 0.316 | 1.81 | 2.12 | 0.767 | 0.882 | 0.947 | 0.69 | 2.18 | 0.879 | 0.919 | ND | 1.23 | 0.723 | 0.553 | 1.93 | 1.53 | ND | 0.34 | 0.183 | ND | ND | 0.487 | 1.14 | ND | 0.361 | 0.782 | ND | 0.712 | ND | 0.641 | 0.014 | 1.8 | ND | 2.15 | ND | ND | ND | ND | ND | 1.05 | 1.1 | 3.52 | 2.84 | ND | 1 | 1.26 | ND | ND | ND | 0.671
|  | R | ND | 2.01 | 0.296 | 3.31 | 1.62 | ND | ND | ND | ND | ND | ND | 0.563 | ND | ND | 0.101 | ND | 1.13 | 0.417 | 1.46 | 0.057 | 0.908 | 1.38 | ND | 2.43 | ND | 0.135 | 1.34 | 0.254 | ND | 0.091 | 0.16 | ND | 2.12 | ND | 0.976 | ND | ND | ND | 0.076 | ND | ND | ND | 0.468 | ND | ND | 1.71 | ND | 2.33 | 3.21 | 3.19 | ND | 2.67 | 3.12 | 5.18 | 3.56 | ND | 1.55 | 3.18 | ND | 2.64 | ND | ND
B |  | L | ND | 5.54 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| -27 IN | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.68 | 0.039 | ND | ND | ND | ND
|  | R | 52.8 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.879 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.1 | ND | ND | ND | 1.75 | ND | ND
A |  | L | ND | ND | 1.07 | ND | 2.27 | 0.355 | ND | 0.205 | ND | 1.52 | ND | ND | 0.668 | 0.843 | 2.74 | 0.17 | ND | 0.532 | ND | 2.55 | 3.95 | 0.128 | 2.48 | ND | 1.37 | ND | 1.4 | 0.456 | 0.621 | 1.66 | 0.934 | ND | 0.678 | 1.05 | 0.555 | 1.11 | 2.1 | 0.942 | 0.389 | ND | 0.269 | 0.61 | ND | ND | ND | ND | ND | 1.52 | 0.761 | 0.979 | 0.497 | 2.15 | 0.071 | 3.01 | 1.38 | 1.58 | ND | ND | ND | 0.609 | 0.849 | ND
| -36 IN | C | ND | ND | 1.71 | ND | ND | 0.39 | ND | 2.61 | 2.65 | 1.06 | ND | ND | ND | 0.671 | 0.933 | 0.434 | ND | 2.48 | ND | ND | 1.48 | ND | 3.49 | 3.58 | 2.42 | 1.11 | ND | 2.18 | 2 | ND | 0.926 | 0.109 | 1.36 | 0.021 | ND | ND | ND | ND | 0.028 | ND | 1.91 | ND | ND | ND | ND | ND | 1.64 | 1.14 | ND | 0.303 | 0.903 | 0.129 | 2.4 | 1.5 | ND | 1.33 | ND | 0.349 | 3.48 | ND | 2.31 | 6.63
|  | R | ND | ND | 1.25 | 30.5 | ND | 1.2 | 1.5 | 3.63 | 1.21 | 0.321 | 0.067 | ND | ND | ND | 0.116 | 3.13 | ND | ND | 0.099 | 1.25 | 0.81 | ND | ND | ND | ND | 0.123 | 0.311 | ND | 1.01 | ND | ND | ND | ND | 0.774 | 1.05 | ND | ND | ND | 0.613 | ND | 1.01 | 0.87 | ND | ND | ND | ND | ND | ND | 0.888 | 4.71 | ND | 1.39 | 0.705 | 1.45 | 0.782 | 2.6 | 0.063 | 0.851 | 0.95 | ND | ND | 22
A |  | L | ND | ND | ND | ND | 3.02 | ND | 0.018 | ND | ND | 0.349 | ND | 1.7 | 3.83 | ND | 0.13 | 0.213 | 0.437 | 1.88 | ND | ND | ND | 0.219 | 1.27 | 0.969 | ND | 0.233 | ND | ND | ND | 3.25 | 0.057 | 0.66 | 2.96 | ND | 0.129 | ND | 1.85 | ND | ND | ND | 0.419 | ND | 3.42 | ND | ND | ND | 1.54 | ND | 0.633 | 0.801 | ND | 0.607 | 1.41 | 0.955 | ND | ND | 0.503 | ND | ND | ND | 1.16 | 2.41
| -45 IN | C | 0.077 | ND | 0.559 | ND | ND | 0.173 | ND | ND | ND | ND | ND | 0.275 | ND | ND | ND | ND | ND | 0.027 | ND | ND | ND | ND | ND | ND | ND | 2.49 | ND | ND | ND | 4.31 | ND | 2.65 | ND | ND | 0.942 | ND | 1.59 | 0.989 | 0.649 | ND | 1.13 | 2.67 | ND | ND | 0.448 | 0.886 | ND | 2.03 | ND | ND | 0.595 | 1.04 | 2.39 | 0.197 | 1.23 | 0.832 | 8.75 | ND | 1.46 | 3.26 | 0.111 | ND
|  | R | ND | ND | ND | ND | ND | ND | ND | ND | 1.3 | ND | 0.631 | 0.442 | ND | ND | ND | ND | ND | 1.83 | 0.977 | 1.16 | ND | 0.83 | ND | ND | ND | ND | 0.258 | ND | ND | 0.944 | ND | 2.47 | ND | ND | ND | 0.811 | ND | 1.39 | 1.21 | ND | 0.601 | ND | ND | ND | ND | ND | 0.113 | 0.376 | 2.46 | 1.03 | ND | 0.877 | ND | ND | 1.01 | 0.342 | 2.75 | 1.02 | ND | 0.298 | ND | ND
A |  | L | 1.28 | 3.48 | 2.14 | 4.56 | 7.92 | 5.89 | ND | 4.59 | 6.31 | 1.12 | 1.18 | 3.72 | 0.936 | 6.72 | 3.91 | 1.66 | 1.14 | ND | 0.498 | 1.51 | 5.66 | 1.02 | 13.3 | 6.64 | 4.56 | 2.29 | 2.92 | 5.61 | ND | 3.11 | 4.37 | 1.15 | 3.86 | ND | ND | 1.31 | 6.54 | ND | 5.09 | 4.72 | 1.35 | 1.94 | 1.99 | ND | 3.63 | 2.52 | 3.3 | 1.09 | 1.91 | 4.08 | ND | 4.99 | 3.89 | 3.43 | 1.89 | 2.5 | 2.25 | 1.24 | ND | 3.2 | 8.28 | 9.87
| -54 IN | C | 1.65 | 2.61 | 1.6 | 1.61 | 5.95 | 8.19 | ND | ND | ND | 3.11 | 2.05 | 2.82 | 0.413 | 4.58 | 1.66 | ND | ND | ND | ND | 3.05 | ND | 0.786 | 6.37 | ND | 2.87 | 0.642 | ND | ND | ND | ND | 0.966 | 0.571 | 2.42 | ND | ND | 1.89 | ND | ND | ND | 4.45 | ND | 1.45 | ND | 2.15 | ND | ND | ND | ND | 0.491 | ND | ND | 4.16 | ND | 1.33 | 2.64 | 0.991 | ND | 0.843 | ND | 5.15 | 4.4 | 3.3
|  | R | 0.874 | 2.85 | ND | 2.28 | 4.17 | ND | 0.981 | 0.429 | 5.36 | 6.13 | 2.58 | 0.027 | 4.71 | 4.75 | 0.295 | ND | ND | 0.455 | ND | 3.08 | ND | 4.62 | 5.83 | 2.24 | 1.77 | 1.49 | 4.4 | 3.31 | 0.863 | 2.67 | 1.15 | 0.493 | 3.56 | 0.212 | 2.02 | 4.25 | 2.3 | ND | 2.85 | 6.81 | 2.25 | 2.18 | 2.94 | 5.27 | ND | 3.16 | 2.19 | ND | 2.24 | ND | ND | ND | ND | 7.38 | 0.618 | 0.571 | ND | ND | ND | 6.56 | 5.77 | 2.5
A |  | L | 0.163 | 5.73 | 8.23 | 0.893 | 4.44 | 3.3 | 0.606 | 4.08 | 8.12 | ND | 4.71 | 1.71 | 0.772 | 0.751 | 0.207 | 0.583 | 0.524 | 1.1 | 3.6 | 5.31 | ND | 2.7 | 4.36 | 2.04 | 2.24 | ND | 2.54 | ND | ND | 0.353 | ND | ND | ND | ND | 3.26 | 0.677 | 0.305 | 1.69 | ND | 1.29 | ND | ND | ND | 0.535 | ND | 0.516 | 4.29 | 3.36 | 0.245 | 3.72 | ND | 5.03 | 2.21 | 6.81 | ND | ND | ND | ND | ND | 3.55 | 2.76 | 3.36
| -63 IN | C | 1.74 | 6.42 | 2.68 | ND | 2.66 | ND | 2.95 | 3.11 | 4.84 | 2.85 | 5.92 | ND | 0.959 | 1.84 | 0.955 | ND | ND | 0.332 | ND | ND | ND | 1.95 | ND | ND | ND | 0.578 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.34 | ND | ND | 1.02 | ND | ND | 5.9 | 3.76 | ND | 1.81 | 1.96 | 1.76 | 1.37 | 0.151 | 2.93 | ND | ND | 5.61 | ND | ND | ND | 5.47 | 2.1 | 1.48 | ND | 3.19
|  | R | ND | 1.96 | 1.67 | 2.45 | 2.33 | 4.45 | 1.85 | 1.47 | ND | 0.282 | 0.194 | 3.33 | 1.96 | ND | ND | ND | 1.59 | ND | ND | 3.68 | 2.75 | 2.87 | ND | ND | ND | 1.95 | 0.319 | ND | ND | ND | ND | ND | ND | 0.331 | ND | 3.82 | 2.85 | ND | 5.7 | 2.93 | 5.53 | 2.23 | 5.27 | 4.25 | 1.07 | 3.12 | 1.27 | 2.28 | 1.45 | 4.24 | ND | ND | 1.43 | 7.18 | ND | 1.2 | 7.76 | 3.11 | 2.42 | ND | 6.61 | 0.492
A | POSITION 'A' | L | ND | ND | 0.589 | 0.879 | ND | ND | ND | ND | ND | 4.15 | ND | 0.859 | 3.15 | ND | ND | 2.12 | ND | 2.14 | ND | ND | ND | 2.25 | ND | ND | 1.08 | ND | ND | 1.1 | 0.788 | ND | ND | 2.27 | ND | ND | 2.37 | ND | ND | ND | ND | ND | ND | 1.34 | ND | ND | 0.096 | ND | ND | ND | ND | ND | ND | ND | 2 | 1.76 | ND | ND | ND | ND | ND | 0.501 | ND | ND
| OF THE | C | ND | ND | ND | 0.118 | ND | ND | ND | ND | 4.48 | 2.77 | ND | 3.37 | ND | ND | 0.944 | 1.51 | ND | 2.11 | 6.14 | ND | 0.04 | 1.92 | ND | 1.69 | 3.36 | ND | ND | 2.36 | 1.24 | ND | ND | 2.1 | ND | 3.7 | 4.54 | ND | ND | ND | 0.281 | ND | ND | 2.73 | ND | 0.128 | 0.393 | ND | 2.69 | 3.01 | ND | ND | 1.58 | ND | 3.69 | 2.46 | ND | ND | ND | ND | 0.322 | ND | ND | ND
| PRIMARIES | R | ND | ND | 2.47 | ND | ND | 0.915 | 2.3 | ND | 2.3 | ND | ND | ND | ND | ND | 1.35 | 1.49 | ND | 3.14 | ND | ND | 0.432 | 3.81 | ND | 1.77 | 2.79 | ND | ND | 3.77 | 6.36 | ND | 2.19 | 2.08 | ND | 3.41 | 2.92 | ND | ND | ND | ND | ND | 0.073 | 2.84 | ND | 1.51 | ND | ND | ND | 2.94 | ND | ND | ND | ND | 2.38 | 2.61 | ND | ND | ND | ND | ND | 0.358 | ND | ND
A | POSITION 'B' | L | ND | ND | 4.18 | ND | ND | 3.89 | 0.65 | ND | 2.28 | 5.97 | ND | 2.83 | 1.73 | ND | 1.65 | 1.99 | ND | 1.05 | 1.76 | ND | 1.35 | 0.786 | ND | 2.65 | 3.69 | ND | ND | ND | 2 | ND | 0.45 | 0.096 | ND | 1.42 | 2.18 | ND | ND | ND | 1.73 | ND | 0.953 | ND | ND | 2.96 | ND | ND | 2.53 | 1.55 | ND | 0.308 | 3.58 | ND | ND | 4.44 | ND | 0.343 | ND | ND | ND | 2.64 | ND | ND
| OF THE | C | ND | ND | 4.78 | 1.27 | ND | 4.3 | 3.23 | ND | ND | 2.85 | ND | 4.55 | 0.111 | ND | ND | 2.35 | ND | 3.22 | 1.27 | ND | 3.15 | 3.9 | ND | 5.17 | 3.51 | ND | ND | 3.69 | 1.71 | ND | 1.36 | 0.375 | ND | 3.16 | 1.17 | ND | ND | ND | 0.6 | ND | 1.17 | 1.85 | ND | 1.14 | ND | ND | 4.13 | 4.43 | ND | 5.1 | 2.78 | ND | 1.09 | 4.38 | ND | 4.29 | ND | ND | ND | 3.02 | ND | ND
| PRIMARIES | R | ND | ND | 1.72 | 4.08 | ND | 1.19 | 1.02 | ND | 1.98 | 4.56 | ND | 2.73 | 3.17 | ND | 2.18 | 2.21 | ND | 1.47 | 0.647 | ND | 0.791 | 1.72 | ND | 4.53 | 4.72 | ND | ND | 3.82 | ND | ND | 2.38 | 4.28 | ND | 5.49 | 2.47 | ND | ND | ND | 2.01 | ND | 2.12 | 2.77 | ND | ND | 0.472 | ND | 1.43 | 4.62 | ND | 3.88 | ND | ND | ND | 2.01 | ND | 5.45 | 0.813 | ND | ND | 2.2 | ND | ND
A | POSITION 'C' | L | ND | ND | 6.67 | 1.5 | ND | 3.17 | 6.09 | ND | 1.92 | 2.45 | ND | 3.9 | 1.63 | ND | 1.27 | 1.4 | ND | 6.95 | ND | ND | 5.3 | 2.6 | ND | 6.15 | 5.53 | ND | ND | 4.17 | ND | ND | 0.375 | 3.14 | ND | 0.122 | 2.67 | ND | ND | ND | 0.036 | ND | 2.47 | 0.686 | ND | 0.654 | 1.7 | ND | 1.62 | 2.12 | ND | 0.622 | ND | ND | 6.07 | 4 | ND | 4.64 | ND | ND | 2.29 | ND | ND | ND
| OF THE | C | ND | ND | 4.64 | 1.72 | ND | 1.13 | 6.52 | ND | 1.44 | 2.31 | ND | 2.71 | 1.72 | ND | 3.61 | 4.42 | ND | 3.61 | 4.47 | ND | 3.43 | 4.77 | ND | 3.96 | 2.16 | ND | ND | 5.32 | 2.29 | ND | 1.42 | 1.18 | ND | 3.24 | 3.17 | ND | ND | ND | ND | ND | 6.34 | 3.07 | ND | 3.03 | 2.46 | ND | 5.48 | 1.55 | ND | 6.44 | 0.247 | ND | 4.52 | 1.85 | ND | 3.43 | ND | ND | 1 | ND | ND | ND
| PRIMARIES | R | ND | ND | 2.35 | 1.55 | ND | 2.34 | 5.12 | ND | 2.89 | 1.39 | ND | 4.68 | 4.09 | ND | 2.63 | 3.23 | ND | 3.07 | 2.26 | ND | 3.37 | 2.65 | ND | 2.1 | 7.15 | ND | ND | 2.68 | 0.414 | ND | 1.57 | 3.26 | ND | 3.11 | 0.544 | ND | ND | 2.25 | 0.381 | ND | ND | 3.47 | ND | 2.1 | 3.74 | ND | 3.16 | 3.34 | ND | 5.03 | 1.34 | ND | 6.67 | ND | ND | 1.56 | ND | ND | 3.79 | ND | ND | ND
A |  | L | ND | 3.01 | ND | 2.86 | 3.22 | ND | 6.29 | 1.46 | 5.5 | 5.76 | 0.862 | 6.98 | 2.42 | 2.34 | 4.13 | 5.75 | 1.6 | 1.09 | 1.23 | 2.16 | 0.987 | 0.258 | 2.46 | 10.4 | 10.7 | 10.9 | 3.27 | 4.77 | ND | 5.33 | 0.806 | 5.38 | 4.78 | 2.3 | 3.98 | 1.35 | 1.84 | ND | 0.078 | 1.44 | 1.64 | 8.86 | 3.2 | 4.49 | 3.8 | 5.41 | 1.17 | 4.77 | 7.93 | 1.83 | 3.16 | 8.59 | 7.87 | 1.82 | ND | ND | ND | 5.41 | ND | ND | ND | 2.64
| -72 IN | C | ND | 0.468 | ND | ND | 1.83 | 2.24 | 6.43 | 4.08 | 5.19 | 6.52 | ND | 6.19 | 0.324 | ND | 4.2 | 5.99 | 4.84 | 9.44 | 7.1 | 1.9 | 0.263 | 1.9 | ND | 11.1 | 6.03 | 5.02 | 8.43 | 10.5 | ND | 3.43 | 4.92 | 5.44 | 3.65 | 7.07 | 0.425 | 1.52 | 1.91 | ND | 3.25 | 6.5 | 2.98 | 1.32 | 2.55 | 4.33 | 3.11 | 6.42 | 5.22 | 4.75 | 5.74 | 2.18 | 6.04 | 4.19 | 7.34 | 4.12 | 0.801 | ND | 3.13 | 5.23 | ND | ND | 0.291 | 3.18
|  | R | ND | 1.32 | ND | 0.792 | 1.75 | ND | 3.61 | 3.35 | 4.84 | 5.27 | 0.437 | 3.11 | 2.07 | 3.22 | 3.55 | 2.76 | 0.192 | 5.98 | 4.65 | 3.68 | 3.88 | 1.29 | 0.588 | 10.2 | 7.12 | 6.17 | 5.27 | 3.83 | ND | 1.3 | ND | 2.91 | 6.08 | ND | 0.447 | 3.99 | 7.73 | 5.51 | 0.622 | 6.4 | 9.25 | 0.546 | 4.33 | 2.21 | 5.4 | 6.7 | 2.2 | 4.73 | 2.27 | 3.93 | 1.6 | 7.47 | ND | 5.27 | 1.53 | 2.07 | ND | 4.76 | ND | ND | 1.21 | ND
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | AVG | MAX
| CORROSION RATE (mpy): |  | 10: NOTE: CORROSION RATES ARE BASED ON COMPARISON OF; 30: TEST RESULTS |  |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | < 0 mpy (LOSS) or no data |  | 30: OVERALL CORROSION RATE (mils per year):
| 0-10 mpy (LOSS) |  | 10: 2020, 2022, 2023, 2024, 2025 |  |  |  | CALCULATED CORROSION RATE
| 10-20 mpy (LOSS) |  | 10: INSPECTION DATA; 30: 2.476
| > 20 mpy (LOSS) |  | 10: ND; 15: NO COMPARISON DATA
CORROSION
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Projection
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. PROJECTED THICKNESS MEASUREMENTS ARE IN INCHES. | [66 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | AVG | MIN
C | POSITION 'A' | L | 6: 0.179; 7: 0.187; 8: 0.188; 9: 0.164; 10: 0.116; 11: 0.175; 29: 0.185; 30: 0.204; 31: 0.182; 32: 0.177; 33: 0.118; 34: 0.173; 51: 0.168; 52: 0.177; 53: 0.176; 54: 0.16; 55: 0.133
0.099 | OF THE | C | 6: 0.174; 7: 0.18; 8: 0.177; 9: 0.178; 10: 0.16; 11: 0.18; 29: 0.183; 30: 0.102; 31: 0.172; 32: 0.175; 33: 0.105; 34: 0.18; 51: 0.182; 52: 0.174; 53: 0.181; 54: 0.173; 55: 0.177; 56: 0.18
| TERTIARIES | R | 6: 0.176; 7: 0.184; 8: 0.177; 9: 0.177; 10: 0.098; 11: 0.182; 29: 0.175; 30: 0.092; 31: 0.17; 32: 0.176; 33: 0.121; 34: 0.176; 51: 0.178; 52: 0.176; 53: 0.182; 54: 0.163; 55: 0.179; 56: 0.182
C | POSITION 'B' | L | 6: 0.177; 7: 0.176; 8: 0.172; 9: 0.178; 10: RT; 11: 0.17; 29: 0.178; 30: RT; 31: 0.183; 32: 0.181; 33: RT; 34: 0.188; 51: 0.194; 52: 0.165; 53: 0.167; 54: RT; 55: 0.177; 56: 0.18
0.099 | OF THE | C | 6: 0.173; 7: 0.177; 8: 0.169; 9: 0.184; 10: RT; 11: 0.18; 29: 0.176; 30: RT; 31: 0.178; 32: 0.18; 33: RT; 34: 0.181; 51: 0.169; 52: 0.171; 53: 0.18; 54: RT; 55: 0.175; 56: 0.185
| TERTIARIES | R | 6: 0.18; 7: 0.179; 8: 0.177; 9: 0.176; 10: RT; 11: 0.178; 29: 0.177; 30: RT; 31: 0.176; 32: 0.175; 33: RT; 34: 0.184; 51: 0.176; 52: 0.179; 53: 0.181; 54: RT; 55: 0.177; 56: 0.18
C | POSITION 'C' | L | 6: 0.169; 7: 0.182; 8: 0.176; 9: 0.178; 10: 0.145; 11: 0.175; 29: 0.179; 30: 0.117; 31: 0.185; 32: 0.182; 33: 0.114; 34: 0.189; 51: 0.181; 52: 0.173; 53: 0.177; 54: 0.17; 55: 0.183; 56: 0.179
0.099 | OF THE | C | 6: 0.171; 7: 0.175; 8: 0.183; 9: 0.183; 10: 0.114; 11: 0.174; 29: 0.177; 30: 0.107; 31: 0.18; 32: 0.18; 33: 0.13; 34: 0.182; 51: 0.181; 52: 0.178; 53: 0.181; 54: 0.169; 55: 0.176; 56: 0.178
| TERTIARIES | R | 6: 0.177; 7: 0.179; 8: 0.172; 9: 0.183; 10: 0.15; 11: 0.172; 29: 0.174; 30: 0.114; 31: 0.168; 32: 0.184; 33: 0.131; 34: 0.185; 51: 0.174; 52: 0.177; 53: 0.183; 54: 0.177; 55: 0.181; 56: 0.178
B |  | L | 0.212 | 0.194 | 0.2 | 0.214 | 0.218 | 0.218 | 0.219 | 0.185 | 0.212 | 0.221 | 0.212 | 0.209 | 0.218 | 0.199 | 0.202 | 0.197 | 0.206 | 0.227 | 0.207 | 0.21 | 0.225 | 0.206 | 0.214 | 0.21 | 0.211 | 0.226 | 0.223 | 0.194 | 0.235 | 0.208 | 0.222 | 0.23 | 0.22 | 0.236 | 0.212 | 0.231 | 0.241 | 0.241 | 0.209 | 0.213 | 0.22 | 0.224 | 0.211 | 0.231 | 0.236 | 0.215 | 0.222 | 0.23 | 0.229 | 0.217 | 0.224 | 0.211 | 0.23 | 0.215 | 0.221 | 0.206 | 0.219 | 0.236 | 0.207 | 0.22 | 0.171 | 0.161
0.083 | +16 FT 6 IN | C | 0.205 | 0.204 | 0.212 | 0.207 | 0.207 | 0.209 | 0.212 | 0.189 | 0.195 | 0.213 | 0.211 | 0.223 | 0.214 | 0.208 | 0.197 | 0.202 | 0.213 | 0.208 | 0.218 | 0.21 | 0.215 | 0.209 | 0.166 | 0.205 | 0.219 | 0.231 | 0.216 | 0.217 | 0.223 | 0.241 | 0.241 | 0.235 | 0.227 | 0.218 | 0.225 | 0.229 | 0.224 | 0.173 | 0.229 | 0.229 | 0.217 | 0.233 | 0.238 | 0.228 | 0.23 | 0.231 | 0.217 | 0.224 | 0.221 | 0.219 | 0.213 | 0.208 | 0.217 | 0.218 | 0.207 | 0.22 | 0.225 | 0.202 | 0.215 | 0.211 | 0.214 | 0.25
|  | R | 0.216 | 0.228 | 0.194 | 0.215 | 0.209 | 0.219 | 0.209 | 0.217 | 0.196 | 0.206 | 0.214 | 0.214 | 0.216 | 0.226 | 0.196 | 0.204 | 0.212 | 0.196 | 0.209 | 0.204 | 0.206 | 0.217 | 0.225 | 0.22 | 0.221 | 0.232 | 0.226 | 0.239 | 0.219 | 0.233 | 0.217 | 0.234 | 0.233 | 0.237 | 0.226 | 0.233 | 0.226 | 0.201 | 0.216 | 0.23 | 0.221 | 0.234 | 0.233 | 0.229 | 0.216 | 0.228 | 0.217 | 0.242 | 0.238 | 0.221 | 0.226 | 0.198 | 0.209 | 0.219 | 0.211 | 0.217 | 0.219 | 0.242 | 0.217 | RF | 0.217 | RF
B |  | L | 0.218 | 0.196 | 0.185 | 0.176 | 0.196 | 0.207 | 0.203 | 0.199 | 0.202 | 0.192 | 0.196 | 0.208 | 0.193 | 0.213 | 0.202 | 0.216 | 0.21 | 0.202 | 0.209 | 0.185 | 0.19 | 0.212 | 0.183 | 0.203 | 0.193 | 0.202 | 0.197 | 0.22 | 0.204 | 0.203 | 0.22 | 0.213 | 0.223 | 0.224 | 0.196 | 0.209 | 0.206 | 0.185 | 0.192 | 0.182 | 0.204 | 0.206 | 0.201 | 0.177 | 0.208 | 0.203 | 0.192 | 0.204 | 0.205 | 0.209 | 0.203 | 0.225 | 0.196 | 0.203 | 0.208 | 0.199 | 0.202 | 0.16 | 0.187 | 0.211 | 0.193 | 0.22
0.083 | +15 FT | C | 0.221 | 0.211 | 0.214 | 0.197 | 0.212 | 0.207 | 0.214 | 0.202 | 0.211 | 0.189 | 0.186 | 0.203 | 0.225 | 0.21 | 0.197 | 0.204 | 0.216 | 0.202 | 0.212 | 0.193 | 0.205 | 0.208 | 0.205 | 0.205 | 0.204 | 0.219 | 0.222 | 0.22 | 0.202 | 0.213 | 0.175 | 0.218 | 0.214 | 0.217 | 0.213 | 0.219 | 0.205 | 0.206 | 0.219 | 0.202 | 0.212 | 0.19 | 0.205 | 0.178 | 0.21 | 0.213 | 0.197 | 0.203 | 0.208 | 0.193 | 0.213 | 0.224 | 0.218 | 0.223 | 0.222 | 0.192 | 0.196 | 0.185 | 0.198 | 0.2 | 0.21 | 0.218
|  | R | 0.168 | 0.191 | 0.201 | 0.167 | 0.192 | 0.195 | 0.19 | 0.185 | 0.197 | 0.186 | 0.194 | 0.208 | 0.208 | 0.191 | 0.191 | 0.213 | 0.204 | 0.201 | 0.21 | 0.212 | 0.206 | 0.208 | 0.204 | 0.212 | 0.217 | 0.223 | 0.216 | 0.209 | 0.218 | 0.21 | 0.215 | 0.216 | 0.207 | 0.182 | 0.205 | 0.202 | 0.19 | 0.221 | 0.167 | 0.196 | 0.208 | 0.224 | 0.203 | 0.206 | 0.21 | 0.21 | 0.217 | 0.211 | 0.204 | 0.212 | 0.215 | 0.21 | 0.212 | 0.204 | 0.218 | 0.221 | 0.209 | 0.197 | 0.198 | 0.21 | 0.213 | 0.21
B |  | L | 0.207 | 0.202 | 0.198 | 0.177 | 0.17 | 0.16 | 0.175 | 0.19 | 0.175 | 0.195 | 0.156 | 0.184 | 0.144 | 0.126 | 0.205 | 0.144 | 0.186 | 0.194 | 0.178 | 0.217 | 0.215 | 0.191 | 0.142 | 0.212 | 0.219 | 0.199 | 0.213 | 0.164 | 0.195 | 0.218 | 0.214 | 0.206 | 0.194 | 0.207 | 0.215 | 0.186 | 0.18 | 0.192 | 0.195 | 0.179 | 0.193 | 0.178 | 0.176 | 0.181 | 0.174 | 0.222 | 0.214 | 0.189 | 0.216 | 0.181 | 0.192 | 0.18 | 0.213 | 0.196 | 0.198 | 0.187 | 0.2 | 0.199 | 0.186 | 0.192 | 0.192 | 0.179
0.083 | +13 FT 6 IN | C | 0.184 | 0.204 | 0.195 | 0.157 | 0.207 | 0.185 | 0.207 | 0.183 | 0.167 | 0.198 | 0.202 | 0.178 | 0.187 | 0.14 | 0.178 | 0.194 | 0.189 | 0.206 | 0.194 | 0.196 | 0.196 | 0.205 | 0.208 | 0.204 | 0.209 | 0.205 | 0.208 | 0.189 | 0.213 | 0.185 | 0.196 | 0.21 | 0.206 | 0.21 | 0.215 | 0.199 | 0.218 | 0.195 | 0.19 | 0.182 | 0.161 | 0.188 | 0.18 | 0.19 | 0.192 | 0.199 | 0.22 | 0.206 | 0.205 | 0.184 | 0.171 | 0.2 | 0.203 | 0.215 | 0.186 | 0.193 | 0.206 | 0.189 | 0.203 | 0.167 | 0.193 | 0.199
|  | R | 0.181 | 0.218 | 0.215 | 0.206 | 0.208 | 0.196 | 0.206 | 0.198 | 0.16 | 0.208 | 0.206 | 0.162 | 0.201 | 0.2 | 0.198 | 0.205 | 0.161 | 0.185 | 0.212 | 0.226 | 0.231 | 0.194 | 0.219 | 0.207 | 0.203 | 0.218 | 0.2 | 0.205 | 0.215 | 0.181 | 0.197 | 0.223 | 0.212 | 0.179 | 0.194 | 0.197 | 0.209 | 0.191 | 0.196 | 0.188 | 0.197 | 0.211 | 0.198 | 0.189 | 0.224 | 0.192 | 0.207 | 0.206 | 0.201 | 0.196 | 0.197 | 0.196 | 0.207 | 0.194 | 0.192 | 0.203 | 0.21 | 0.213 | 0.212 | 0.194 | 0.2 | 0.185
B |  | L | 0.165 | 0.191 | 0.216 | 0.204 | 0.206 | 0.207 | 0.213 | 0.179 | 0.194 | 0.181 | 0.192 | 0.169 | 0.167 | 0.186 | 0.164 | 0.201 | 0.173 | 0.206 | 0.194 | 0.216 | 0.193 | 0.204 | 0.195 | 0.202 | 0.217 | 0.201 | 0.21 | 0.172 | 0.221 | 0.201 | 0.202 | 0.204 | 0.193 | 0.202 | 0.206 | 0.202 | 0.207 | 0.213 | 0.204 | 0.177 | 0.188 | 0.193 | 0.204 | 0.19 | 0.187 | 0.181 | 0.19 | 0.2 | 0.185 | 0.197 | 0.181 | 0.19 | 0.211 | 0.199 | 0.197 | 0.201 | 0.203 | 0.182 | 0.222 | 0.204 | 0.213 | 0.177
0.083 | +12 FT | C | 0.191 | 0.216 | 0.187 | 0.207 | 0.194 | 0.209 | 0.205 | 0.179 | 0.204 | 0.19 | 0.191 | 0.178 | 0.184 | 0.197 | 0.184 | 0.202 | 0.194 | 0.2 | 0.196 | 0.21 | 0.212 | 0.207 | 0.183 | 0.205 | 0.199 | 0.208 | 0.207 | 0.201 | 0.21 | 0.216 | 0.205 | 0.216 | 0.194 | 0.206 | 0.211 | 0.193 | 0.205 | 0.181 | 0.192 | 0.211 | 0.204 | 0.196 | 0.171 | 0.182 | 0.189 | 0.202 | 0.208 | 0.189 | 0.184 | 0.171 | 0.191 | 0.189 | 0.202 | 0.208 | 0.182 | 0.208 | 0.204 | 0.192 | 0.224 | 0.201 | 0.206 | 0.188
|  | R | 0.191 | 0.217 | 0.21 | 0.202 | 0.201 | 0.175 | 0.194 | 0.198 | 0.212 | 0.178 | 0.197 | 0.139 | 0.171 | 0.188 | 0.165 | 0.184 | 0.185 | 0.193 | 0.202 | 0.21 | 0.193 | 0.202 | 0.167 | 0.214 | 0.208 | 0.213 | 0.211 | 0.206 | 0.216 | 0.212 | 0.21 | 0.199 | 0.191 | 0.209 | 0.206 | 0.209 | 0.187 | 0.199 | 0.222 | 0.212 | 0.193 | 0.205 | 0.183 | 0.21 | 0.21 | 0.207 | 0.211 | 0.185 | 0.187 | 0.198 | 0.205 | 0.178 | 0.184 | 0.206 | 0.144 | 0.207 | 0.207 | 0.191 | 0.191 | 0.221 | 0.214 | 0.196
B | POSITION 'A' | L | 2: 0.232; 3: 0.236; 4: 0.239; 5: 0.203; 58: 0.209; 59: 0.217; 60: 0.234; 61: 0.216
0.083 | OF THE | C | 2: 0.215; 3: 0.233; 4: 0.233; 5: 0.211; 58: 0.191; 59: 0.215; 60: 0.223; 61: 0.203
| OB PORTS | R | 2: 0.226; 3: 0.213; 4: 0.223; 5: 0.199; 58: 0.204; 59: 0.22; 60: 0.227; 61: 0.211
B | POSITION 'B' | L | 2: 0.212; 3: 0.227; 4: 0.208; 5: 0.205; 58: 0.214; 59: 0.243; 60: 0.195; 61: 0.207
0.083 | OF THE | C | 2: 0.217; 3: 0.225; 4: 0.221; 5: 0.222; 58: 0.199; 59: 0.198; 60: 0.22; 61: 0.217
| OB PORTS | R | 2: 0.217; 3: 0.219; 4: 0.222; 5: 0.223; 58: 0.218; 59: 0.218; 60: 0.208; 61: 0.216
B | POSITION 'C' | L | 2: 0.21; 3: 0.23; 4: 0.223; 5: 0.202; 58: 0.204; 59: 0.233; 60: 0.233; 61: 0.21
0.083 | OF THE | C | 2: 0.21; 3: 0.228; 4: 0.219; 5: 0.213; 58: 0.215; 59: 0.208; 60: 0.229; 61: 0.204
| OB PORTS | R | 2: 0.194; 3: 0.228; 4: 0.218; 5: 0.206; 58: 0.211; 59: 0.223; 60: 0.21; 61: 0.176
B |  | L | 0.2 | 0.195 | 0.209 | 0.22 | 0.196 | 0.2 | 0.224 | 0.183 | 0.21 | 0.194 | 0.176 | 0.173 | 0.183 | 0.179 | 0.164 | 0.177 | 0.159 | 0.197 | 0.177 | 0.188 | 0.137 | 0.196 | 0.198 | 0.214 | 0.188 | 0.213 | 0.207 | 0.211 | 0.151 | 0.203 | 0.221 | 0.212 | 0.215 | 0.22 | 0.196 | 0.194 | 0.198 | 0.21 | 0.186 | 0.175 | 0.187 | 0.176 | 0.154 | 0.177 | 0.194 | 0.185 | 0.199 | 0.192 | 0.198 | 0.175 | 0.182 | 0.2 | 0.194 | 0.18 | 0.193 | 0.209 | 0.186 | 0.196 | 0.2 | 0.199 | 0.211 | 0.199
0.083 | +10 FT 6 IN | C | 0.183 | 0.191 | 0.221 | 0.222 | 0.192 | 0.203 | 0.194 | 0.189 | 0.202 | 0.188 | 0.207 | 0.181 | 0.173 | 0.166 | 0.191 | 0.185 | 0.168 | 0.21 | 0.186 | 0.179 | 0.187 | 0.205 | 0.212 | 0.202 | 0.183 | 0.221 | 0.209 | 0.22 | 0.209 | 0.187 | 0.218 | 0.209 | 0.205 | 0.221 | 0.194 | 0.185 | 0.186 | 0.201 | 0.173 | 0.169 | 0.198 | 0.192 | 0.198 | 0.193 | 0.174 | 0.205 | 0.194 | 0.18 | 0.177 | 0.189 | 0.18 | 0.192 | 0.199 | 0.166 | 0.192 | 0.2 | 0.21 | 0.218 | 0.201 | 0.213 | 0.202 | 0.215
|  | R | 0.199 | 0.195 | 0.226 | 0.22 | 0.202 | 0.202 | 0.199 | 0.172 | 0.161 | 0.183 | 0.161 | 0.178 | 0.168 | 0.164 | 0.186 | 0.185 | 0.174 | 0.17 | 0.18 | 0.208 | 0.19 | 0.195 | 0.202 | 0.191 | 0.195 | 0.202 | 0.212 | 0.204 | 0.204 | 0.191 | 0.211 | 0.229 | 0.21 | 0.219 | 0.212 | 0.216 | 0.188 | 0.201 | 0.194 | 0.187 | 0.19 | 0.199 | 0.203 | 0.191 | 0.173 | 0.204 | 0.185 | 0.215 | 0.162 | 0.19 | 0.209 | 0.185 | 0.211 | 0.201 | 0.193 | 0.194 | 0.192 | 0.214 | 0.201 | 0.207 | 0.225 | 0.223
B |  | L | 0.226 | 0.21 | 0.243 | 0.219 | 0.21 | 0.205 | 0.176 | 0.216 | 0.187 | 0.207 | 0.165 | 0.197 | 0.159 | 0.152 | 0.203 | 0.195 | 0.161 | 0.226 | 0.225 | 0.203 | 0.213 | 0.198 | 0.242 | 0.204 | 0.208 | 0.199 | 0.207 | 0.231 | 0.184 | 0.177 | 0.093 | 0.224 | 0.221 | 0.213 | 0.199 | 0.176 | 0.191 | 0.181 | 0.191 | 0.185 | 0.194 | 0.17 | 0.214 | 0.172 | 0.191 | 0.219 | 0.195 | 0.205 | 0.181 | 0.211 | 0.222 | 0.208 | 0.203 | 0.196 | 0.215 | 0.205 | 0.194 | 0.194 | 0.214 | 0.221 | 0.196 | 0.221
0.083 | +9 FT | C | 0.212 | 0.197 | 0.234 | 0.233 | 0.228 | 0.205 | 0.192 | 0.188 | 0.201 | 0.198 | 0.184 | 0.19 | 0.169 | 0.204 | 0.203 | 0.205 | 0.172 | 0.224 | 0.222 | 0.2 | 0.197 | 0.19 | 0.193 | 0.195 | 0.218 | 0.19 | 0.221 | 0.211 | 0.216 | 0.152 | 0.107 | 0.242 | 0.184 | 0.24 | 0.237 | 0.171 | 0.199 | 0.209 | 0.189 | 0.185 | 0.236 | 0.2 | 0.226 | 0.166 | 0.155 | 0.17 | 0.177 | 0.208 | 0.197 | 0.203 | 0.221 | 0.209 | 0.206 | 0.196 | 0.217 | 0.206 | 0.223 | 0.217 | 0.213 | 0.21 | 0.2 | 0.217
|  | R | 0.225 | 0.216 | 0.236 | 0.209 | 0.211 | 0.21 | 0.184 | 0.203 | 0.19 | 0.193 | 0.214 | 0.2 | 0.168 | 0.208 | 0.191 | 0.192 | 0.187 | 0.219 | 0.209 | 0.186 | 0.211 | 0.206 | 0.164 | 0.229 | 0.196 | 0.228 | 0.177 | 0.211 | 0.194 | 0.196 | 0.214 | 0.149 | 0.229 | 0.186 | 0.205 | 0.18 | 0.186 | 0.189 | 0.2 | 0.22 | 0.203 | 0.175 | 0.23 | 0.191 | 0.181 | 0.199 | 0.177 | 0.16 | 0.148 | 0.19 | 0.187 | 0.213 | 0.201 | RF | 0.224 | 0.206 | 0.229 | 0.211 | 0.233 | 0.227 | 0.224 | 0.204
B | POSITION 'A' | L | 29: 0.215; 30: 0.226; 31: 0.229; 32: 0.225; 33: 0.222; 34: 0.202
0.083 | OF THE | C | 29: 0.216; 30: 0.236; 31: 0.23; 32: 0.214; 33: 0.214; 34: 0.212
| OSCILLATOR | R | 29: 0.228; 30: 0.224; 31: 0.221; 32: 0.215; 33: 0.222; 34: 0.224
B | POSITION 'B' | L | 29: 0.221; 30: 0.23; 31: 0.211; 32: 0.217; 33: 0.195; 34: 0.212
0.083 | OF THE | C | 29: 0.217; 30: 0.224; 31: 0.226; 32: 0.215; 33: 0.224; 34: 0.227
| OSCILLATOR | R | 29: 0.232; 30: 0.223; 31: 0.218; 32: 0.229; 33: 0.215; 34: 0.195
B | POSITION 'C' | L | 29: 0.219; 30: 0.22; 31: 0.227; 32: 0.238; 33: 0.207; 34: 0.227
0.083 | OF THE | C | 29: 0.214; 30: 0.226; 31: 0.205; 32: 0.22; 33: 0.219; 34: 0.227
| OSCILLATOR | R | 29: 0.218; 30: 0.225; 31: 0.222; 32: 0.233; 33: 0.224; 34: 0.215
B | POSITION 'D' | L | 29: 0.219; 30: 0.203; 31: 0.227; 32: 0.244; 33: 0.231; 34: 0.214
0.083 | OF THE | C | 29: 0.216; 30: 0.226; 31: 0.225; 32: 0.244; 33: 0.211; 34: 0.211
| OSCILLATOR | R | 29: 0.226; 30: 0.207; 31: 0.233; 32: 0.235; 33: 0.207; 34: 0.201
B | POSITION 'E' | L | 29: 0.211; 30: 0.223; 31: 0.216; 32: 0.234; 33: 0.226; 34: 0.185
0.083 | OF THE | C | 29: 0.217; 30: 0.197; 31: 0.222; 32: 0.228; 33: 0.212; 34: 0.19
| OSCILLATOR | R | 29: 0.237; 30: 0.201; 31: 0.232; 32: 0.241; 33: 0.202; 34: 0.215
B |  | L | 0.22 | 0.135 | 0.211 | 0.216 | 0.223 | 0.213 | 0.209 | 0.212 | 0.221 | 0.209 | 0.191 | 0.213 | 0.161 | 0.196 | 0.204 | 0.16 | 0.194 | 0.192 | 0.197 | 0.183 | 0.2 | 0.188 | 0.199 | 0.2 | 0.209 | 0.222 | 0.175 | 0.224 | 0.175 | 0.201 | 0.216 | 0.228 | 0.197 | 0.217 | 0.185 | 0.139 | 0.197 | 0.191 | 0.161 | 0.204 | 0.219 | 0.206 | 0.207 | 0.196 | 0.167 | 0.209 | 0.216 | 0.191 | 0.208 | 0.218 | 0.22 | 0.189 | 0.19 | 0.178 | 0.226 | 0.194 | 0.225 | 0.224 | 0.197 | 0.243 | 0.194 | 0.172
0.083 | +7 FT 6 IN | C | 0.23 | 0.176 | 0.22 | 0.208 | 0.196 | 0.214 | 0.208 | 0.221 | 0.204 | 0.21 | 0.213 | 0.221 | RF | 0.225 | 0.215 | 0.194 | 0.212 | 0.184 | 0.197 | 0.183 | 0.206 | 0.201 | 0.195 | 0.214 | 0.212 | 0.227 | 0.183 | 0.181 | 0.204 | 0.229 | 0.204 | 0.207 | 0.215 | 0.167 | 0.193 | 0.197 | 0.189 | 0.187 | 0.194 | 0.196 | 0.197 | 0.194 | 0.193 | 0.2 | 0.179 | 0.199 | 0.201 | 0.201 | 0.217 | 0.193 | 0.2 | 0.229 | 0.201 | RF | 0.187 | 0.204 | 0.195 | 0.224 | 0.211 | 0.22 | 0.207 | 0.221
|  | R | 0.232 | 0.186 | 0.196 | 0.203 | 0.227 | 0.225 | 0.217 | 0.216 | 0.211 | 0.187 | 0.203 | 0.223 | 0.192 | 0.21 | 0.212 | 0.189 | 0.205 | 0.18 | 0.218 | 0.194 | 0.218 | 0.193 | 0.198 | 0.196 | 0.221 | 0.205 | 0.176 | 0.194 | 0.197 | 0.195 | 0.211 | 0.198 | 0.205 | 0.223 | 0.186 | 0.154 | 0.196 | 0.205 | 0.191 | 0.184 | 0.184 | 0.21 | 0.211 | 0.198 | 0.173 | 0.193 | 0.195 | 0.214 | 0.2 | 0.201 | 0.19 | 0.193 | 0.196 | 0.197 | 0.19 | 0.205 | 0.205 | 0.198 | 0.2 | 0.224 | 0.21 | 0.239
B |  | L | 0.173 | 0.181 | 0.215 | 0.212 | 0.203 | 0.2 | 0.231 | 0.213 | 0.225 | 0.202 | 0.205 | 0.187 | RF | 0.191 | 0.22 | 0.22 | 0.215 | 0.189 | 0.212 | 0.173 | 0.168 | 0.169 | 0.185 | 0.169 | 0.193 | 0.177 | 0.191 | 0.201 | 0.175 | 0.212 | 0.195 | 0.184 | 0.186 | 0.184 | 0.185 | 0.196 | 0.192 | 0.197 | 0.174 | 0.199 | 0.183 | 0.183 | 0.195 | 0.2 | 0.173 | 0.185 | 0.184 | 0.201 | 0.19 | 0.202 | 0.204 | 0.19 | 0.199 | 0.211 | 0.218 | 0.215 | 0.218 | 0.209 | 0.194 | 0.203 | 0.215 | 0.188
0.083 | +6 FT | C | 0.204 | 0.17 | 0.21 | 0.226 | 0.222 | 0.215 | 0.219 | 0.201 | 0.227 | 0.199 | 0.209 | 0.215 | 0.196 | 0.208 | 0.197 | 0.183 | 0.185 | 0.193 | 0.181 | 0.17 | 0.178 | 0.169 | 0.154 | 0.158 | 0.192 | 0.186 | 0.192 | 0.213 | 0.151 | 0.15 | 0.219 | 0.173 | 0.178 | 0.199 | 0.191 | 0.196 | 0.209 | 0.212 | 0.158 | 0.208 | 0.189 | 0.206 | 0.209 | 0.153 | 0.2 | 0.179 | 0.191 | 0.189 | 0.201 | 0.188 | 0.201 | 0.181 | 0.185 | 0.22 | 0.197 | 0.214 | 0.2 | 0.211 | 0.213 | 0.222 | 0.214 | 0.199
|  | R | 0.191 | 0.164 | 0.211 | 0.217 | 0.197 | 0.221 | 0.207 | 0.224 | 0.214 | 0.209 | 0.196 | 0.214 | 0.179 | 0.217 | 0.2 | 0.192 | 0.178 | 0.184 | 0.195 | 0.202 | 0.209 | 0.177 | 0.181 | 0.177 | 0.188 | 0.182 | 0.194 | 0.192 | 0.172 | 0.162 | 0.197 | 0.168 | 0.192 | 0.202 | 0.178 | 0.191 | 0.199 | 0.206 | 0.194 | 0.173 | 0.184 | 0.172 | 0.183 | 0.158 | 0.197 | 0.205 | 0.214 | 0.193 | 0.189 | 0.196 | 0.206 | 0.218 | 0.192 | 0.22 | 0.198 | 0.225 | 0.203 | 0.206 | 0.202 | 0.218 | 0.199 | 0.203
B |  | L | 0.2 | 0.166 | 0.202 | 0.214 | 0.199 | 0.178 | 0.205 | 0.195 | 0.194 | 0.212 | 0.215 | 0.175 | 0.184 | 0.207 | 0.203 | 0.194 | 0.207 | 0.195 | 0.175 | 0.176 | 0.179 | 0.185 | 0.211 | 0.183 | 0.205 | 0.194 | 0.174 | 0.162 | 0.192 | 0.19 | 0.188 | 0.168 | 0.19 | 0.192 | 0.189 | 0.194 | 0.188 | 0.193 | 0.196 | 0.198 | 0.194 | 0.196 | 0.196 | 0.212 | 0.183 | 0.205 | 0.225 | 0.21 | 0.205 | 0.208 | 0.197 | 0.209 | 0.198 | 0.201 | 0.194 | 0.202 | 0.199 | 0.205 | 0.201 | 0.19 | 0.19 | 0.223
0.083 | +4 FT 6 IN | C | 0.217 | 0.192 | 0.206 | 0.218 | 0.202 | 0.216 | 0.207 | 0.219 | 0.212 | 0.198 | 0.207 | 0.203 | 0.193 | 0.199 | 0.193 | 0.175 | 0.182 | 0.196 | 0.194 | 0.172 | 0.188 | 0.165 | 0.188 | 0.2 | 0.169 | 0.208 | 0.141 | 0.204 | 0.186 | 0.15 | 0.195 | 0.158 | 0.18 | 0.192 | 0.186 | 0.169 | 0.18 | 0.196 | 0.194 | 0.189 | 0.177 | 0.176 | 0.205 | 0.161 | 0.181 | 0.22 | 0.189 | 0.195 | 0.21 | 0.213 | 0.216 | 0.187 | 0.198 | 0.19 | 0.198 | 0.194 | 0.193 | 0.201 | 0.209 | 0.208 | 0.188 | 0.199
|  | R | RF | RF | 0.216 | 0.213 | 0.206 | 0.201 | 0.214 | 0.208 | 0.199 | 0.192 | 0.2 | 0.213 | 0.206 | 0.199 | 0.196 | 0.187 | 0.205 | 0.189 | 0.177 | 0.193 | 0.173 | 0.163 | 0.178 | 0.218 | 0.173 | 0.167 | 0.167 | 0.192 | 0.165 | 0.142 | 0.175 | 0.128 | 0.178 | 0.191 | 0.161 | 0.186 | 0.174 | 0.174 | 0.183 | 0.197 | 0.184 | 0.189 | 0.165 | 0.215 | 0.206 | 0.211 | 0.171 | 0.196 | 0.214 | 0.186 | 0.215 | 0.188 | 0.187 | 0.194 | 0.188 | 0.194 | 0.195 | 0.208 | 0.212 | 0.21 | 0.204 | 0.191
B |  | L | 0.237 | 0.255 | 0.181 | 0.187 | 0.194 | 0.23 | 0.23 | 0.224 | 0.213 | 0.211 | 0.204 | 0.203 | 0.235 | 0.204 | 0.214 | 0.177 | 0.194 | 0.203 | 0.196 | 0.19 | 0.2 | 0.205 | 0.186 | 0.196 | 0.201 | 0.198 | 0.219 | 0.203 | 0.193 | 0.189 | 0.201 | 0.194 | 0.165 | 0.205 | 0.209 | 0.16 | 0.212 | RF | 0.18 | 0.186 | 0.174 | 0.185 | 0.191 | 0.181 | 0.181 | 0.183 | 0.192 | 0.193 | 0.191 | 0.182 | 0.185 | 0.186 | 0.201 | 0.139 | 0.198 | 0.184 | 0.205 | 0.217 | 0.193 | 0.207 | 0.202 | 0.231
0.083 | +3 FT | C | 0.185 | 0.177 | 0.204 | 0.231 | 0.206 | 0.206 | 0.232 | 0.208 | 0.189 | 0.209 | 0.211 | 0.21 | 0.203 | 0.212 | 0.206 | 0.213 | 0.198 | 0.207 | 0.186 | 0.19 | 0.197 | 0.22 | 0.196 | 0.195 | 0.205 | 0.187 | 0.217 | 0.214 | 0.196 | 0.139 | 0.185 | 0.187 | 0.189 | 0.179 | 0.213 | 0.189 | 0.216 | 0.184 | 0.176 | 0.214 | 0.213 | 0.16 | 0.191 | 0.214 | 0.182 | 0.192 | 0.184 | 0.161 | 0.214 | 0.182 | 0.193 | 0.188 | 0.194 | 0.137 | 0.204 | 0.174 | 0.199 | 0.204 | 0.211 | 0.214 | 0.191 | 0.181
|  | R | RF | 0.191 | 0.193 | 0.21 | 0.203 | 0.206 | 0.199 | 0.217 | 0.202 | 0.22 | 0.224 | 0.206 | 0.214 | 0.192 | 0.209 | 0.199 | 0.186 | 0.193 | 0.189 | 0.197 | 0.208 | 0.202 | 0.19 | 0.198 | 0.198 | 0.2 | 0.211 | 0.218 | 0.213 | 0.187 | 0.205 | 0.217 | 0.153 | 0.204 | 0.2 | 0.151 | 0.173 | 0.163 | 0.171 | 0.198 | 0.201 | 0.169 | 0.203 | 0.182 | 0.18 | 0.182 | 0.2 | 0.192 | 0.186 | 0.181 | 0.19 | 0.19 | 0.171 | 0.164 | 0.206 | 0.205 | 0.203 | 0.204 | 0.208 | 0.206 | 0.19 | 0.182
B |  | L | 0.246 | 0.203 | 0.193 | 0.232 | 0.214 | 0.207 | 0.193 | 0.196 | 0.228 | 0.216 | 0.222 | 0.231 | RF | 0.193 | 0.209 | 0.187 | 0.217 | 0.207 | 0.214 | 0.206 | 0.223 | 0.209 | 0.2 | 0.211 | 0.2 | 0.21 | 0.211 | 0.218 | 0.181 | 0.222 | 0.234 | 0.135 | 0.223 | 0.218 | 0.244 | 0.22 | 0.203 | 0.245 | RF | 0.23 | 0.186 | 0.21 | 0.214 | 0.19 | 0.193 | 0.195 | 0.212 | 0.209 | 0.219 | 0.2 | 0.208 | 0.213 | 0.214 | 0.185 | 0.2 | 0.188 | 0.205 | 0.186 | 0.217 | 0.217 | 0.232 | 0.234
0.083 | +1 FT 6 IN | C | 0.195 | 0.171 | 0.215 | 0.216 | 0.208 | 0.211 | 0.204 | 0.223 | 0.211 | 0.197 | 0.194 | 0.194 | RF | 0.195 | 0.208 | 0.206 | 0.181 | 0.209 | 0.2 | 0.216 | 0.213 | 0.203 | 0.208 | 0.204 | 0.195 | 0.22 | 0.218 | 0.21 | 0.202 | 0.205 | 0.224 | 0.228 | 0.204 | 0.243 | 0.222 | 0.207 | 0.201 | 0.199 | 0.222 | 0.194 | 0.19 | 0.211 | 0.207 | 0.201 | 0.228 | 0.208 | 0.217 | 0.22 | 0.199 | 0.192 | 0.19 | 0.176 | 0.18 | 0.161 | 0.193 | 0.185 | 0.206 | 0.205 | 0.202 | 0.213 | 0.205 | RF
|  | R | 0.21 | 0.239 | 0.22 | 0.201 | 0.215 | 0.196 | 0.2 | 0.203 | 0.225 | 0.198 | 0.208 | 0.214 | RF | 0.199 | 0.207 | 0.207 | 0.174 | 0.187 | 0.208 | 0.204 | 0.199 | 0.202 | 0.211 | 0.201 | 0.208 | 0.187 | 0.21 | 0.205 | 0.231 | 0.233 | 0.168 | 0.207 | 0.213 | 0.184 | 0.191 | 0.21 | 0.204 | RF | 0.198 | 0.217 | 0.182 | 0.168 | 0.167 | 0.176 | 0.117 | 0.159 | 0.159 | 0.128 | 0.148 | 0.147 | 0.176 | 0.166 | 0.178 | 0.217 | 0.164 | 0.162 | 0.183 | 0.206 | 0.215 | 0.224 | 0.235 | RF
B |  | L | 0.213 | 0.248 | 0.213 | 0.212 | 0.199 | 0.209 | 0.176 | 0.192 | 0.197 | 0.2 | 0.203 | 0.187 | 0.192 | 0.195 | 0.204 | 0.192 | 0.18 | 0.196 | 0.206 | 0.208 | 0.219 | 0.206 | 0.195 | 0.205 | 0.206 | 0.214 | 0.215 | 0.217 | 0.202 | 0.215 | 0.211 | 0.212 | 0.216 | 0.242 | 0.198 | 0.206 | 0.237 | 0.211 | 0.209 | 0.211 | 0.211 | 0.211 | 0.216 | 0.217 | 0.212 | 0.202 | 0.213 | 0.208 | 0.213 | 0.205 | 0.193 | 0.178 | 0.18 | 0.162 | 0.196 | 0.231 | 0.152 | 0.173 | 0.182 | 0.156 | 0.194 | 0.2
0.083 | 0 REFERENCE | C | 0.212 | RF | 0.217 | 0.211 | 0.197 | 0.2 | 0.199 | 0.203 | 0.197 | 0.202 | 0.203 | 0.193 | 0.194 | 0.201 | 0.202 | 0.196 | 0.192 | 0.209 | 0.197 | 0.2 | 0.205 | 0.203 | 0.209 | 0.206 | 0.193 | 0.214 | 0.245 | 0.21 | 0.204 | 0.244 | 0.2 | RF | RF | 0.247 | 0.199 | 0.236 | 0.214 | 0.194 | 0.178 | 0.184 | 0.222 | 0.218 | 0.243 | 0.21 | 0.155 | 0.203 | 0.193 | 0.186 | 0.162 | 0.212 | 0.16 | 0.214 | 0.165 | 0.228 | 0.169 | 0.1 | 0.182 | 0.156 | 0.183 | 0.171 | 0.2 | 0.211
|  | R | RF | 0.217 | 0.215 | 0.197 | 0.195 | 0.191 | 0.187 | 0.189 | 0.19 | 0.182 | 0.187 | 0.193 | 0.225 | 0.179 | 0.23 | 0.19 | 0.185 | 0.183 | 0.184 | 0.19 | 0.214 | 0.195 | 0.235 | 0.178 | 0.191 | 0.206 | 0.207 | 0.206 | 0.175 | 0.206 | 0.193 | 0.213 | 0.191 | 0.237 | 0.193 | 0.212 | 0.194 | 0.197 | 0.194 | 0.213 | 0.139 | 0.225 | 0.129 | 0.156 | 0.203 | 0.127 | 0.2 | 0.218 | 0.175 | 0.175 | 0.128 | 0.146 | 0.116 | 0.117 | 0.114 | 0.086 | 0.131 | 0.151 | 0.243 | 0.181 | 0.214 | 0.11
B | POSITION 'A' | L | 30: 0.211; 31: 0.212; 32: 0.234; 33: 0.198; 34: 0.217; 35: 0.22
0.083 | OF THE | C | 30: 0.208; 31: 0.191; 32: 0.205; 33: 0.187; 34: 0.205; 35: 0.202
| SECONDARIES | R | 30: 0.175; 31: 0.177; 32: 0.232; 33: 0.232; 34: 0.221; 35: 0.193
B | POSITION 'B' | L | 30: 0.211; 31: 0.221; 32: 0.217; 33: 0.21; 34: 0.203; 35: 0.213
0.083 | OF THE | C | 30: 0.196; 31: 0.206; 32: 0.203; 33: 0.255; 34: 0.233; 35: 0.203
| SECONDARIES | R | 30: 0.199; 31: 0.178; 32: 0.192; 33: 0.161; 34: 0.17; 35: 0.172
B |  | L | RF | 0.165 | 0.2 | 0.203 | 0.193 | 0.2 | 0.2 | 0.205 | 0.205 | 0.184 | 0.198 | 0.205 | 0.188 | 0.205 | 0.201 | 0.194 | 0.206 | 0.2 | 0.217 | 0.204 | 0.199 | 0.212 | 0.214 | 0.214 | 0.209 | 0.211 | 0.208 | 0.208 | 0.203 | 0.206 | 0.205 | 0.214 | 0.209 | 0.213 | 0.224 | 0.21 | 0.216 | 0.204 | 0.219 | 0.205 | 0.181 | 0.186 | 0.206 | 0.18 | 0.171 | 0.181 | 0.201 | 0.213 | 0.199 | 0.2 | 0.218 | 0.192 | 0.221 | 0.197 | 0.193 | 0.171 | 0.186 | 0.184 | 0.242 | 0.211 | 0.193 | 0.205
0.083 | -9 IN | C | 0.202 | 0.209 | 0.212 | 0.225 | 0.201 | 0.202 | 0.202 | 0.203 | 0.2 | 0.189 | 0.196 | 0.19 | 0.208 | 0.185 | 0.212 | 0.199 | 0.191 | 0.194 | 0.187 | 0.191 | 0.183 | 0.196 | 0.204 | 0.194 | 0.184 | 0.188 | 0.198 | 0.204 | 0.201 | 0.199 | 0.21 | 0.215 | 0.209 | 0.131 | 0.19 | 0.162 | 0.188 | 0.212 | 0.211 | 0.173 | 0.188 | 0.199 | 0.198 | 0.188 | 0.197 | 0.181 | 0.188 | 0.19 | 0.182 | 0.172 | 0.183 | 0.161 | 0.189 | 0.191 | 0.169 | 0.152 | 0.191 | 0.179 | 0.161 | 0.174 | 0.219 | 0.221
|  | R | RF | 0.214 | 0.189 | 0.205 | 0.204 | 0.192 | 0.209 | 0.192 | 0.185 | 0.191 | 0.192 | 0.194 | 0.195 | 0.199 | 0.204 | 0.198 | 0.197 | 0.218 | 0.189 | 0.191 | 0.188 | 0.205 | 0.208 | 0.199 | 0.201 | 0.19 | 0.203 | 0.204 | 0.213 | 0.217 | 0.221 | 0.197 | 0.213 | 0.207 | 0.157 | 0.207 | 0.218 | 0.219 | 0.207 | 0.197 | 0.192 | 0.201 | 0.196 | 0.177 | 0.173 | 0.197 | 0.172 | 0.187 | 0.187 | 0.176 | 0.184 | 0.154 | 0.143 | 0.213 | 0.138 | 0.148 | 0.162 | 0.159 | 0.239 | 0.216 | 0.059 | 0.215
B | POSITION 'C' | L | 30: 0.202; 31: 0.197; 32: 0.224; 33: 0.224; 34: 0.225; 35: 0.214
0.083 | OF THE | C | 30: 0.196; 31: 0.21; 32: 0.207; 33: 0.208; 34: 0.205; 35: 0.224
| SECONDARIES | R | 30: 0.217; 31: 0.2; 32: 0.206; 33: 0.218; 34: 0.164; 35: 0.16
B |  | L | 0.23 | 0.212 | 0.202 | 0.206 | 0.185 | 0.203 | 0.199 | 0.208 | 0.199 | 0.204 | 0.203 | 0.203 | 0.194 | 0.206 | 0.201 | 0.198 | 0.191 | 0.201 | 0.186 | 0.195 | 0.21 | 0.206 | 0.206 | 0.205 | 0.198 | 0.207 | 0.216 | 0.211 | 0.201 | 0.205 | 0.212 | 0.221 | 0.207 | 0.215 | 0.205 | 0.222 | 0.212 | 0.209 | 0.209 | 0.204 | 0.212 | 0.201 | 0.204 | 0.197 | 0.188 | 0.2 | 0.19 | 0.212 | 0.203 | 0.203 | 0.203 | 0.197 | 0.196 | 0.21 | 0.175 | 0.202 | 0.194 | 0.188 | 0.235 | 0.186 | 0.187 | 0.216
0.083 | -18 IN | C | 0.228 | 0.208 | 0.191 | 0.213 | 0.185 | 0.196 | 0.213 | 0.211 | 0.205 | 0.207 | 0.19 | 0.189 | 0.208 | 0.199 | 0.198 | 0.196 | 0.206 | 0.206 | 0.202 | 0.192 | 0.204 | 0.206 | 0.209 | 0.206 | 0.205 | 0.207 | 0.193 | 0.203 | 0.221 | 0.214 | 0.204 | 0.208 | 0.226 | 0.213 | 0.208 | 0.22 | 0.204 | 0.193 | 0.203 | 0.194 | 0.22 | 0.188 | 0.192 | 0.182 | 0.189 | 0.175 | 0.19 | 0.203 | 0.194 | 0.196 | 0.184 | 0.194 | 0.192 | 0.174 | 0.175 | 0.198 | 0.191 | 0.183 | 0.239 | 0.207 | 0.217 | 0.217
|  | R | 0.231 | 0.2 | 0.216 | 0.195 | 0.196 | 0.201 | 0.202 | 0.209 | 0.212 | 0.213 | 0.205 | 0.198 | 0.209 | 0.21 | 0.208 | 0.202 | 0.196 | 0.202 | 0.192 | 0.204 | 0.201 | 0.201 | 0.22 | 0.189 | 0.212 | 0.195 | 0.194 | 0.206 | 0.216 | 0.214 | 0.206 | 0.216 | 0.191 | 0.232 | 0.196 | 0.214 | 0.222 | 0.201 | 0.182 | 0.198 | 0.199 | 0.176 | 0.187 | 0.194 | 0.193 | 0.173 | 0.191 | 0.167 | 0.16 | 0.169 | 0.184 | 0.168 | 0.174 | 0.153 | 0.157 | 0.191 | 0.185 | 0.171 | 0.24 | 0.182 | 0.216 | 0.221
B |  | L | 0.329 | 0.185 | 0.325 | 0.332 | 0.314 | 0.323 | 0.32 | 0.329 | 0.317 | 0.307 | 0.31 | 0.318 | 0.31 | 0.315 | 0.331 | 0.328 | 0.322 | 0.307 | 0.321 | 0.313 | 0.315 | 0.334 | 0.323 | 0.327 | 0.332 | 0.319 | 0.322 | 0.325 | 0.327 | 0.32 | 0.324 | 0.316 | 0.317 | 0.323 | 0.323 | 0.313 | 0.316 | 0.326 | 0.323 | 0.314 | 0.316 | 0.316 | 0.314 | 0.314 | 0.319 | 0.306 | 0.306 | 0.313 | 0.307 | 0.304 | 0.307 | 0.299 | 0.306 | 0.321 | 0.321 | 0.321 | 0.323 | 0.317 | 0.32 | 0.326 | 0.323 | RF
0.083 | -27 IN | C | 0.329 | 0.319 | 0.314 | 0.321 | 0.316 | 0.324 | 0.333 | 0.319 | 0.316 | 0.302 | 0.303 | 0.307 | 0.317 | 0.321 | 0.325 | 0.317 | 0.33 | 0.31 | 0.318 | 0.316 | 0.309 | 0.322 | 0.319 | 0.331 | 0.325 | 0.321 | 0.325 | RF | 0.311 | 0.329 | 0.323 | 0.317 | 0.307 | 0.309 | 0.311 | 0.299 | 0.296 | 0.309 | 0.313 | 0.307 | 0.309 | 0.305 | 0.306 | 0.304 | 0.306 | 0.292 | 0.308 | 0.296 | 0.294 | 0.305 | 0.303 | 0.293 | 0.304 | 0.304 | 0.32 | 0.321 | 0.187 | 0.199 | 0.326 | 0.333 | 0.316 | 0.321
|  | R | 0.001 | 0.319 | 0.325 | 0.323 | 0.327 | 0.323 | 0.328 | 0.324 | 0.321 | 0.31 | 0.201 | 0.311 | 0.327 | 0.324 | 0.332 | 0.326 | 0.337 | 0.318 | 0.342 | 0.317 | 0.309 | 0.309 | 0.32 | 0.333 | 0.314 | 0.316 | 0.311 | 0.326 | 0.325 | 0.327 | 0.314 | 0.311 | 0.306 | 0.306 | 0.316 | 0.31 | 0.3 | 0.306 | 0.319 | 0.284 | 0.308 | 0.308 | 0.314 | 0.306 | 0.314 | 0.305 | 0.314 | 0.3 | 0.308 | 0.31 | 0.311 | 0.297 | 0.321 | 0.323 | RF | 0.169 | RF | 0.329 | RF | 0.191 | 0.32 | 0.33
A |  | L | 0.341 | RF | 0.321 | 0.33 | 0.307 | 0.33 | 0.32 | 0.327 | 0.331 | 0.296 | 0.316 | 0.317 | 0.305 | 0.317 | 0.312 | 0.319 | 0.327 | 0.312 | 0.313 | 0.3 | 0.296 | 0.328 | 0.304 | 0.324 | 0.32 | 0.32 | 0.308 | 0.315 | 0.324 | 0.317 | 0.324 | 0.318 | 0.308 | 0.31 | 0.319 | 0.311 | 0.306 | 0.317 | 0.32 | 0.317 | 0.318 | 0.315 | 0.311 | 0.315 | 0.32 | 0.316 | 0.312 | 0.309 | 0.315 | 0.309 | 0.312 | 0.297 | 0.316 | 0.279 | 0.315 | 0.321 | 0.335 | 0.328 | RF | 0.319 | 0.333 | RF
0.083 | -36 IN | C | RF | RF | 0.315 | RF | RF | 0.335 | RF | 0.312 | 0.296 | 0.303 | 0.308 | 0.324 | RF | 0.321 | 0.321 | 0.318 | 0.335 | 0.295 | 0.316 | 0.313 | 0.313 | 0.334 | 0.293 | 0.306 | 0.311 | 0.307 | 0.319 | 0.303 | 0.31 | 0.315 | 0.321 | 0.317 | 0.304 | 0.31 | 0.328 | 0.319 | 0.315 | 0.322 | 0.326 | 0.295 | 0.305 | 0.314 | 0.31 | 0.307 | 0.321 | 0.298 | 0.294 | 0.306 | 0.324 | 0.312 | 0.311 | 0.305 | 0.303 | 0.308 | 0.33 | 0.324 | 0.324 | 0.325 | 0.305 | 0.324 | 0.309 | 0.288
|  | R | RF | RF | 0.313 | 0.134 | RF | 0.324 | 0.317 | 0.301 | 0.304 | 0.316 | 0.319 | 0.309 | 0.326 | 0.329 | 0.32 | 0.298 | 0.331 | 0.32 | 0.317 | 0.315 | 0.319 | 0.329 | 0.321 | 0.324 | 0.327 | 0.321 | 0.315 | 0.313 | 0.314 | 0.319 | 0.321 | 0.323 | 0.308 | 0.305 | 0.323 | 0.321 | 0.311 | 0.313 | 0.323 | 0.307 | 0.31 | 0.312 | 0.331 | 0.322 | 0.322 | 0.323 | 0.308 | 0.319 | 0.306 | 0.289 | 0.325 | 0.303 | 0.318 | 0.308 | 0.319 | 0.311 | 0.323 | 0.324 | 0.317 | 0.331 | RF | 0.197
A |  | L | 0.331 | RF | RF | 0.345 | 0.284 | 0.321 | 0.327 | 0.324 | 0.327 | 0.312 | 0.324 | 0.303 | 0.29 | 0.356 | 0.315 | 0.327 | 0.32 | 0.302 | 0.346 | 0.313 | 0.343 | 0.324 | 0.326 | 0.314 | 0.346 | 0.324 | 0.324 | 0.328 | 0.33 | 0.293 | 0.323 | 0.323 | 0.301 | 0.324 | 0.328 | 0.311 | 0.301 | 0.319 | 0.323 | 0.341 | 0.32 | 0.329 | 0.291 | 0.303 | 0.317 | 0.31 | 0.296 | 0.35 | 0.31 | 0.307 | 0.324 | 0.309 | 0.303 | 0.312 | 0.319 | 0.31 | 0.319 | 0.322 | 0.317 | 0.32 | 0.317 | 0.317
0.083 | -45 IN | C | 0.331 | RF | 0.312 | RF | 0.317 | 0.324 | 0.326 | 0.326 | 0.325 | 0.315 | 0.305 | 0.319 | 0.328 | RF | 0.344 | 0.327 | 0.326 | 0.313 | 0.345 | 0.317 | 0.323 | 0.341 | 0.329 | 0.326 | 0.332 | 0.304 | 0.332 | 0.332 | 0.337 | 0.29 | 0.322 | 0.306 | 0.337 | 0.328 | 0.318 | 0.306 | 0.298 | 0.318 | 0.32 | 0.301 | 0.311 | 0.3 | 0.319 | 0.32 | 0.322 | 0.289 | 0.308 | 0.297 | 0.336 | 0.313 | 0.308 | 0.287 | 0.298 | 0.31 | 0.306 | 0.314 | 0.276 | 0.342 | 0.304 | 0.288 | 0.319 | 0.331
|  | R | 0.332 | RF | 0.369 | RF | 0.32 | 0.327 | 0.386 | 0.342 | 0.314 | 0.336 | 0.303 | 0.317 | 0.318 | 0.313 | 0.331 | 0.335 | 0.35 | 0.308 | 0.318 | 0.294 | 0.339 | 0.323 | 0.325 | 0.332 | 0.322 | 0.327 | 0.323 | 0.359 | 0.338 | 0.321 | 0.328 | 0.301 | 0.316 | 0.365 | 0.325 | 0.304 | 0.311 | 0.309 | 0.32 | 0.304 | 0.32 | 0.351 | 0.312 | 0.321 | 0.32 | 0.313 | 0.316 | 0.305 | 0.296 | 0.31 | 0.327 | 0.296 | 0.322 | 0.317 | 0.306 | 0.322 | 0.303 | 0.306 | 0.329 | 0.318 | 0.338 | 0.334
A |  | L | 0.318 | 0.303 | 0.312 | 0.298 | 0.269 | 0.284 | RF | 0.294 | 0.277 | 0.314 | 0.306 | 0.29 | 0.321 | 0.274 | 0.292 | 0.309 | 0.311 | RF | 0.321 | 0.294 | 0.271 | 0.319 | 0.223 | 0.27 | 0.294 | 0.286 | 0.291 | 0.289 | RF | 0.297 | 0.296 | 0.321 | 0.289 | RF | RF | 0.301 | 0.265 | 0.306 | 0.292 | 0.285 | 0.309 | 0.311 | 0.296 | RF | 0.296 | 0.291 | 0.282 | 0.314 | 0.298 | 0.284 | RF | 0.269 | 0.285 | 0.295 | 0.303 | 0.303 | 0.303 | 0.301 | RF | 0.296 | 0.263 | 0.254
0.083 | -54 IN | C | 0.312 | 0.293 | 0.307 | 0.322 | 0.286 | 0.272 | RF | RF | 0.322 | 0.302 | 0.289 | 0.296 | 0.299 | 0.279 | 0.307 | RF | RF | 0.304 | 0.305 | 0.274 | 0.307 | 0.307 | 0.249 | RF | 0.307 | 0.299 | 0.301 | RF | RF | RF | 0.316 | 0.321 | 0.292 | RF | 0.316 | 0.288 | 0.296 | RF | 0.311 | 0.267 | RF | 0.303 | RF | 0.292 | RF | RF | RF | 0.307 | 0.3 | RF | RF | 0.263 | RF | 0.3 | 0.297 | 0.315 | RF | 0.302 | RF | 0.284 | 0.295 | 0.302
|  | R | 0.319 | 0.304 | RF | 0.31 | 0.288 | RF | 0.308 | 0.328 | 0.286 | 0.28 | 0.291 | 0.315 | 0.285 | 0.278 | 0.31 | RF | RF | 0.323 | RF | 0.292 | 0.324 | 0.292 | 0.273 | 0.304 | 0.295 | 0.29 | 0.286 | 0.304 | 0.301 | 0.296 | 0.323 | 0.314 | 0.289 | 0.31 | 0.309 | 0.271 | 0.285 | RF | 0.279 | 0.263 | 0.306 | 0.304 | 0.291 | 0.27 | RF | 0.286 | 0.3 | RF | 0.291 | RF | RF | RF | RF | 0.26 | 0.307 | 0.327 | RF | RF | RF | 0.273 | 0.281 | 0.311
A |  | L | 0.329 | 0.285 | 0.276 | 0.317 | 0.295 | 0.301 | 0.318 | 0.304 | 0.262 | 0.313 | 0.276 | 0.296 | 0.301 | 0.299 | 0.316 | 0.307 | 0.308 | 0.299 | 0.277 | 0.269 | 0.324 | 0.294 | 0.269 | 0.291 | 0.304 | 0.318 | 0.305 | 0.337 | 0.325 | 0.323 | 0.35 | 0.329 | 0.323 | 0.315 | 0.298 | 0.309 | 0.31 | 0.315 | 0.319 | 0.297 | 0.326 | 0.332 | 0.325 | 0.307 | 0.331 | 0.311 | 0.28 | 0.301 | 0.306 | 0.29 | 0.308 | 0.28 | 0.301 | 0.27 | 0.321 | 0.324 | 0.342 | 0.316 | 0.373 | 0.29 | 0.302 | 0.306
0.083 | -63 IN | C | 0.315 | 0.277 | 0.301 | 0.321 | 0.301 | 0.327 | 0.299 | 0.307 | 0.29 | 0.294 | 0.264 | 0.335 | 0.294 | 0.29 | 0.307 | 0.338 | 0.323 | 0.309 | 0.298 | 0.318 | 0.321 | 0.295 | 0.324 | 0.321 | 0.341 | 0.303 | 0.333 | 0.323 | 0.313 | 0.319 | 0.322 | 0.319 | 0.317 | 0.315 | 0.316 | 0.313 | 0.29 | 0.303 | 0.303 | 0.285 | 0.323 | 0.307 | 0.265 | 0.279 | 0.329 | 0.287 | 0.293 | 0.299 | 0.295 | 0.295 | 0.273 | 0.309 | 0.3 | 0.262 | 0.32 | 0.327 | 0.318 | 0.28 | 0.305 | 0.316 | RF | 0.311
|  | R | 0.32 | 0.315 | 0.315 | 0.309 | 0.313 | 0.298 | 0.312 | 0.318 | 0.329 | 0.319 | 0.311 | 0.299 | 0.3 | 0.315 | 0.323 | 0.335 | 0.301 | 0.337 | 0.336 | 0.288 | 0.298 | 0.296 | 0.307 | 0.335 | 0.311 | 0.294 | 0.32 | 0.349 | 0.324 | 0.337 | 0.329 | 0.326 | 0.345 | 0.321 | 0.327 | 0.288 | 0.294 | 0.318 | 0.277 | 0.304 | 0.283 | 0.296 | 0.267 | 0.289 | 0.293 | 0.275 | 0.297 | 0.281 | 0.301 | 0.291 | 0.308 | 0.311 | 0.29 | 0.24 | 0.301 | 0.316 | 0.272 | 0.295 | 0.307 | RF | 0.291 | 0.321
A | POSITION 'A' | L |  |  | 0.328 | 0.323 |  | 0.336 | 0.325 |  | 0.32 | 0.283 |  | 0.305 | 0.293 |  | 0.33 | 0.31 |  | 0.305 | 0.319 |  | 0.326 | 0.315 |  | 0.323 | 0.323 |  |  | 0.309 | 0.321 |  | 0.328 | 0.311 |  | 0.32 | 0.308 |  |  | 0.326 | 0.327 |  | 0.321 | 0.317 |  | 0.316 | 0.314 |  | 0.316 | 0.331 |  | 0.328 | 0.315 |  | 0.308 | 0.309 |  | 0.338 | 0.322 |  | 0.327 | 0.315
0.083 | OF THE | C |  |  | 0.33 | 0.323 |  | 0.325 | 0.326 |  | 0.288 | 0.303 |  | 0.292 | 0.304 |  | 0.317 | 0.31 |  | 0.3 | 0.278 |  | 0.317 | 0.324 |  | 0.313 | 0.307 |  |  | 0.3 | 0.318 |  | 0.329 | 0.309 |  | 0.282 | 0.29 |  |  | 0.321 | 0.319 |  | 0.322 | 0.305 |  | 0.309 | 0.319 |  | 0.29 | 0.297 |  | 0.315 | 0.311 |  | 0.3 | 0.3 |  | 0.337 | 0.319 |  | 0.318 | 0.327
| PRIMARIES | R |  |  | 0.305 | 0.333 |  | 0.326 | 0.308 |  | 0.302 | 0.329 |  | 0.335 | 0.318 |  | 0.319 | 0.311 |  | 0.295 | 0.326 |  | 0.318 | 0.297 |  | 0.305 | 0.311 |  |  | 0.295 | 0.276 |  | 0.31 | 0.305 |  | 0.286 | 0.307 |  |  | 0.317 | 0.331 |  | 0.311 | 0.303 |  | 0.299 | 0.332 |  | 0.319 | 0.294 |  | 0.324 | 0.317 |  | 0.311 | 0.302 |  | 0.326 | 0.328 |  | 0.321 | 0.32
A | POSITION 'B' | L |  |  | 0.287 | 0.322 |  | 0.293 | 0.324 |  | 0.305 | 0.281 |  | 0.29 | 0.304 |  | 0.318 | 0.313 |  | 0.312 | 0.305 |  | 0.303 | 0.328 |  | 0.302 | 0.305 |  |  | 0.322 | 0.315 |  | 0.329 | 0.329 |  | 0.313 | 0.314 |  |  | 0.308 | 0.306 |  | 0.313 | 0.33 |  | 0.285 | 0.325 |  | 0.287 | 0.314 |  | 0.314 | 0.294 |  | 0.308 | 0.298 |  | 0.309 | 0.311 |  | 0.314 | 0.302
0.083 | OF THE | C |  |  | 0.285 | 0.313 |  | 0.295 | 0.301 |  | 0.331 | 0.296 |  | 0.288 | 0.309 |  | 0.335 | 0.31 |  | 0.295 | 0.308 |  | 0.294 | 0.3 |  | 0.285 | 0.301 |  |  | 0.288 | 0.315 |  | 0.315 | 0.326 |  | 0.304 | 0.322 |  |  | 0.329 | 0.318 |  | 0.316 | 0.313 |  | 0.306 | 0.323 |  | 0.282 | 0.282 |  | 0.275 | 0.291 |  | 0.31 | 0.284 |  | 0.287 | 0.357 |  | 0.358 | 0.294
| PRIMARIES | R |  |  | 0.315 | 0.293 |  | 0.322 | 0.317 |  | 0.308 | 0.29 |  | 0.301 | 0.29 |  | 0.303 | 0.307 |  | 0.309 | 0.315 |  | 0.306 | 0.315 |  | 0.287 | 0.284 |  |  | 0.29 | 0.331 |  | 0.3 | 0.292 |  | 0.278 | 0.309 |  |  | 0.322 | 0.307 |  | 0.298 | 0.301 |  | 0.32 | 0.312 |  | 0.3 | 0.277 |  | 0.29 | 0.317 |  | 0.319 | 0.308 |  | 0.284 | 0.317 |  | 0.359 | 0.298
A | POSITION 'C' | L |  |  | 0.272 | 0.316 |  | 0.306 | 0.284 |  | 0.308 | 0.3 |  | 0.296 | 0.309 |  | 0.312 | 0.318 |  | 0.269 | 0.323 |  | 0.278 | 0.311 |  | 0.277 | 0.298 |  |  | 0.291 | 0.327 |  | 0.325 | 0.307 |  | 0.324 | 0.311 |  |  | 0.33 | 0.322 |  | 0.306 | 0.316 |  | 0.322 | 0.315 |  | 0.302 | 0.31 |  | 0.323 | 0.339 |  | 0.268 | 0.295 |  | 0.287 | 0.33 |  | 0.294 | 0.322
0.083 | OF THE | C |  |  | 0.289 | 0.31 |  | 0.322 | 0.275 |  | 0.314 | 0.302 |  | 0.304 | 0.305 |  | 0.296 | 0.287 |  | 0.287 | 0.294 |  | 0.287 | 0.289 |  | 0.298 | 0.312 |  |  | 0.29 | 0.306 |  | 0.32 | 0.32 |  | 0.301 | 0.304 |  |  | 0.346 | 0.323 |  | 0.279 | 0.297 |  | 0.309 | 0.31 |  | 0.279 | 0.316 |  | 0.28 | 0.311 |  | 0.288 | 0.304 |  | 0.307 | 0.317 |  | 0.318 | 0.318
| PRIMARIES | R |  |  | 0.304 | 0.31 |  | 0.321 | 0.283 |  | 0.305 | 0.311 |  | 0.301 | 0.283 |  | 0.311 | 0.291 |  | 0.299 | 0.308 |  | 0.301 | 0.3 |  | 0.309 | 0.26 |  |  | 0.311 | 0.324 |  | 0.324 | 0.295 |  | 0.302 | 0.325 |  |  | 0.311 | 0.323 |  | 0.334 | 0.29 |  | 0.313 | 0.289 |  | 0.294 | 0.287 |  | 0.288 | 0.301 |  | 0.275 | 0.304 |  | 0.323 | 0.325 |  | 0.3 | 0.322
A |  | L | 0.357 | 0.313 | 0.335 | 0.329 | 0.307 | 0.343 | 0.29 | 0.327 | 0.287 | 0.285 | 0.32 | 0.281 | 0.305 | 0.311 | 0.292 | 0.287 | 0.324 | 0.321 | 0.322 | 0.312 | 0.322 | 0.324 | 0.305 | 0.243 | 0.246 | 0.239 | 0.31 | 0.297 | 0.352 | 0.296 | 0.321 | 0.297 | 0.305 | 0.314 | 0.303 | 0.326 | 0.308 | 0.36 | 0.326 | 0.315 | 0.325 | 0.267 | 0.316 | 0.302 | 0.31 | 0.28 | 0.317 | 0.292 | 0.264 | 0.312 | 0.305 | 0.27 | 0.285 | 0.312 | 0.348 | 0.334 | 0.355 | 0.306 | 0.338 | 0.359 | 0.353 | 0.328
0.083 | -72 IN | C | 0.354 | 0.323 | 0.336 | 0.387 | 0.326 | 0.318 | 0.288 | 0.303 | 0.285 | 0.284 | 0.346 | 0.278 | 0.321 | 0.36 | 0.296 | 0.289 | 0.3 | 0.26 | 0.273 | 0.311 | 0.328 | 0.311 | 0.352 | 0.231 | 0.278 | 0.292 | 0.271 | 0.246 | 0.348 | 0.312 | 0.289 | 0.277 | 0.31 | 0.278 | 0.332 | 0.315 | 0.306 | 0.356 | 0.306 | 0.267 | 0.308 | 0.306 | 0.298 | 0.282 | 0.306 | 0.274 | 0.276 | 0.287 | 0.276 | 0.308 | 0.276 | 0.295 | 0.269 | 0.285 | 0.324 | 0.346 | 0.31 | 0.312 | 0.343 | 0.339 | 0.338 | 0.33
|  | R | 0.355 | 0.321 | 0.347 | 0.339 | 0.316 | 0.339 | 0.312 | 0.31 | 0.297 | 0.297 | 0.32 | 0.301 | 0.305 | 0.306 | 0.299 | 0.305 | 0.335 | 0.295 | 0.298 | 0.298 | 0.304 | 0.322 | 0.324 | 0.241 | 0.271 | 0.269 | 0.294 | 0.302 | 0.351 | 0.322 | 0.338 | 0.295 | 0.282 | 0.352 | 0.326 | 0.299 | 0.246 | 0.285 | 0.327 | 0.276 | 0.261 | 0.317 | 0.287 | 0.299 | 0.289 | 0.273 | 0.302 | 0.282 | 0.308 | 0.299 | 0.31 | 0.272 | 0.317 | 0.279 | 0.321 | 0.327 | 0.343 | 0.303 | 0.359 | 0.353 | 0.337 | 0.359
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | AVG | MIN
C | 0.001-0.099 | 0.141-0.150 | 10: OUTSIDE DIAMETER:; 23: 2.969; 30: FUTURE PROJECTION
LEGEND | 0.100-0.110 | 0.151-0.160 | 10: TUBE MATERIAL:; 23: SA-178A; 35: MAX. THICKNESS
| 0.111-0.120 | 0.161-0.170 | 10: NOMINAL WALL:; 23: 0.18; 35: AVG. THICKNESS
| 0.121-0.130 | 0.171-0.180 | 10: ASME MIN:; 23: 0.099; 35: MIN. THICKNESS
| 0.131-0.140 | 0.181-0.999 | 10: MILL FLAG:; 23: 0.11; 35: STD DEV.
B | 0.001-0.083 | 0.124-0.133 | 10: OUTSIDE DIAMETER:; 23: 3; 30: FUTURE PROJECTION
LEGEND | 0.084-0.093 | 0.134-0.143 | 10: TUBE MATERIAL:; 23: SA210A1; 35: MAX. THICKNESS
| 0.094-0.103 | 0.144-0.153 | 10: NOMINAL WALL:; 23: 0.203; 35: AVG. THICKNESS
| 0.104-0.113 | 0.154-0.163 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS
| 0.114-0.123 | 0.164-0.999 | 10: MILL FLAG:; 23: 0.1; 35: STD DEV.
A | 0.001-0.083 | 0.140-0.149 | 10: OUTSIDE DIAMETER:; 23: 3; 30: FUTURE PROJECTION |  |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | 0.100-0.109 | 0.150-0.159 | 10: TUBE MATERIAL:; 23: SA-210A1; 35: MAX. THICKNESS
| 0.110-0.119 | 0.160-0.169 | 10: NOMINAL WALL:; 23: 0.3; 35: AVG. THICKNESS |  |  |  | PROJECTED TUBE WALL THICKNESS - 5 YEARS
| 0.120-0.129 | 0.170-0.179 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS
| 0.130-0.139 | 0.180-0.999 | 10: MILL FLAG:; 23: 0.2; 35: STD DEV.
PROJECTION
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Retirement
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. | [64 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62
C | POSITION 'A' | Year | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | Apr 2030 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Nov 2029 | May 2055 | May 2055 | Nov 2030 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | ND | ND | May 2055 | May 2034 | ND | ND | ND | ND | ND | ND | ND
OF THE
TERTIARIES
C | POSITION 'B' | Year | ND | ND | ND | ND | ND | May 2055 | ND | May 2055 | ND | ND | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
TERTIARIES
C | POSITION 'C' | Year | ND | ND | ND | ND | ND | May 2055 | ND | ND | May 2055 | Dec 2031 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | Feb 2031 | May 2055 | May 2055 | Sep 2031 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | ND | May 2055 | ND | ND | ND | ND | ND | ND
OF THE
TERTIARIES
B |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jan 2052 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Aug 2039 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | ND | Apr 2045 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2046 | Feb 2042
+16 FT 6 IN
B |  | Year | Feb 2041 | May 2055 | Jun 2052 | Sep 2041 | Jun 2054 | May 2055 | May 2055 | Feb 2050 | May 2055 | Aug 2054 | May 2055 | May 2055 | Oct 2053 | Mar 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2051 | Jul 2049 | May 2055 | Jul 2048 | May 2055 | Feb 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Dec 2043 | May 2055 | May 2055 | May 2049 | May 2055 | May 2055 | May 2055 | May 2048 | Dec 2040 | Dec 2050 | May 2055 | Dec 2054 | May 2055 | Dec 2045 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jan 2040 | Nov 2054 | May 2055 | May 2055 | May 2055
+15 FT
B |  | Year | May 2044 | May 2055 | May 2055 | Feb 2038 | Jan 2041 | Nov 2038 | Oct 2046 | Oct 2053 | Jun 2038 | May 2055 | Aug 2038 | Jun 2041 | Nov 2035 | Jun 2033 | Jan 2046 | Jun 2035 | Jun 2039 | Feb 2049 | Apr 2044 | May 2055 | May 2055 | May 2055 | Feb 2035 | May 2055 | May 2055 | May 2055 | May 2055 | Jan 2039 | May 2055 | May 2046 | May 2055 | May 2055 | May 2055 | Nov 2044 | Apr 2055 | May 2051 | Jul 2047 | May 2055 | May 2055 | Nov 2048 | Nov 2040 | Nov 2049 | Aug 2048 | Jan 2049 | May 2044 | May 2055 | May 2055 | Jan 2054 | May 2055 | Mar 2049 | Jun 2043 | Aug 2047 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2053 | Feb 2042 | May 2055 | Oct 2047
+13 FT 6 IN
B |  | Year | Mar 2041 | Apr 2052 | May 2055 | May 2055 | May 2055 | Apr 2046 | May 2055 | Jul 2051 | May 2055 | Feb 2054 | May 2055 | Dec 2035 | Jul 2047 | May 2055 | Jan 2044 | May 2055 | Apr 2047 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2040 | May 2055 | May 2055 | May 2055 | May 2055 | May 2042 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2050 | May 2055 | May 2055 | Jul 2047 | Oct 2052 | Jan 2055 | Sep 2052 | May 2055 | May 2055 | Jan 2053 | Jun 2045 | Sep 2052 | Apr 2047 | Aug 2050 | May 2055 | Feb 2036 | May 2055 | May 2055 | Sep 2049 | May 2055 | May 2055 | May 2055 | May 2045
+12 FT
B | POSITION 'A' | Year | ND | May 2055 | May 2055 | ND | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Oct 2052 | May 2055 | May 2055 | May 2055 | ND
OF THE
OB PORTS
B | POSITION 'B' | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND
OF THE
OB PORTS
B | POSITION 'C' | Year | ND | May 2055 | ND | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | Aug 2047 | ND
OF THE
OB PORTS
B |  | Year | Oct 2050 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2045 | Jul 2044 | May 2055 | Jan 2042 | May 2055 | Mar 2051 | Apr 2043 | Oct 2044 | Feb 2051 | Jan 2044 | Oct 2045 | Jun 2053 | Jan 2052 | Jan 2035 | May 2055 | May 2055 | May 2055 | Mar 2049 | May 2055 | May 2055 | May 2055 | Sep 2037 | Mar 2053 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2052 | May 2055 | Feb 2045 | Aug 2044 | May 2055 | Feb 2046 | Mar 2039 | Jan 2054 | Jan 2048 | Apr 2052 | Oct 2054 | Dec 2051 | Jan 2041 | Sep 2047 | Sep 2050 | May 2055 | May 2055 | Jan 2042 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055
+10 FT 6 IN
B |  | Year | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2049 | May 2055 | May 2055 | May 2055 | Jun 2043 | May 2055 | Aug 2044 | May 2040 | May 2055 | May 2055 | Jan 2045 | ND | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2042 | May 2055 | May 2055 | May 2055 | Apr 2047 | May 2055 | Oct 2054 | Jul 2039 | Feb 2031 | Sep 2039 | Jan 2049 | Jan 2054 | May 2055 | Jul 2047 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2050 | ND | Feb 2043 | Sep 2041 | Nov 2049 | Aug 2048 | Apr 2043 | Apr 2039 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055
+9 FT
B | POSITION 'A' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
B | POSITION 'B' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Sep 2050 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
B | POSITION 'C' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
B | POSITION 'D' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
B | POSITION 'E' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Sep 2051 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
B |  | Year | May 2055 | Jul 2035 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | Apr 2043 | May 2055 | May 2055 | Apr 2043 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Jan 2050 | May 2054 | Nov 2048 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2046 | May 2055 | Oct 2037 | May 2055 | May 2055 | Sep 2043 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jan 2045 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jan 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2043
+7 FT 6 IN
B |  | Year | Aug 2047 | Oct 2045 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2049 | May 2047 | Feb 2042 | Oct 2044 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2040 | Dec 2039 | May 2055 | Sep 2046 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2045 | May 2055 | May 2055 | May 2055 | May 2055 | Mar 2043 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055
+6 FT
B |  | Year | May 2055 | Apr 2047 | May 2055 | May 2055 | May 2055 | Jun 2051 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Aug 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jun 2050 | May 2055 | May 2055 | May 2055 | May 2055 | May 2038 | Mar 2046 | May 2055 | Feb 2039 | May 2055 | Mar 2035 | May 2055 | May 2055 | Oct 2047 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jun 2051 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055
+4 FT 6 IN
B |  | Year | May 2055 | May 2055 | Dec 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | Jul 2040 | ND | May 2055 | Apr 2043 | May 2055 | May 2055 | Feb 2043 | May 2055 | Nov 2047 | May 2055 | May 2055 | Oct 2052 | Jan 2049 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2047 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2050 | Aug 2036 | May 2055 | Oct 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2052
+3 FT
B |  | Year | May 2055 | Jul 2051 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | Jul 2050 | ND | Feb 2052 | May 2036 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2053 | May 2055 | Feb 2034 | Jan 2050 | Aug 2044 | Sep 2035 | Oct 2041 | Nov 2041 | May 2055 | Feb 2052 | May 2055 | Aug 2045 | May 2046 | Aug 2044 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND
+1 FT 6 IN
B |  | Year | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | Sep 2052 | ND | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Jul 2038 | May 2055 | Oct 2036 | Oct 2045 | Jul 2045 | May 2036 | May 2055 | May 2055 | Oct 2046 | May 2055 | Dec 2036 | Aug 2044 | Apr 2034 | Jun 2034 | Apr 2034 | Aug 2030 | Jul 2037 | Mar 2045 | May 2055 | Nov 2045 | May 2055 | Nov 2032
0 REFERENCE
B | POSITION 'A' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Oct 2050 | Mar 2053 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
SECONDARIES
B | POSITION 'B' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | Mar 2052 | May 2055 | Oct 2042 | Jul 2051 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
SECONDARIES
B |  | Year | May 2055 | Aug 2040 | Feb 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Dec 2053 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2035 | Apr 2047 | May 2044 | May 2055 | May 2055 | ND | Feb 2046 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Nov 2047 | Oct 2040 | ND | Dec 2038 | Jan 2043 | May 2055 | May 2055 | Dec 2052 | May 2055 | Dec 2028 | May 2055
-9 IN
B | POSITION 'C' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2045 | Jan 2043 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
SECONDARIES
B |  | Year | ND | May 2055 | May 2055 | May 2055 | Oct 2053 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Jun 2054 | May 2055 | ND | May 2055 | May 2055 | Nov 2043 | Mar 2051 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055
-18 IN
B |  | Year | May 2026 | Nov 2048 | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | ND
-27 IN
A |  | Year | ND | ND | May 2055 | Jan 2032 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2035
-36 IN
A |  | Year | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jun 2052 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055
-45 IN
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | Nov 2053 | May 2053 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Nov 2040 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | Jun 2054 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Jan 2052 | Sep 2047
-54 IN
A |  | Year | May 2055 | May 2055 | Oct 2053 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jun 2052 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Mar 2052 | ND | May 2055 | Oct 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055
-63 IN
A | POSITION 'A' | Year | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | ND | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | ND | May 2055 | May 2055 | ND | ND | ND | ND | May 2055 | May 2055 | ND | ND
OF THE
PRIMARIES
A | POSITION 'B' | Year | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | ND | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | ND | ND
OF THE
PRIMARIES
A | POSITION 'C' | Year | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | Jan 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | ND | ND | May 2055 | ND | ND | ND
OF THE
PRIMARIES
A |  | Year | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2049 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Aug 2043 | Jul 2045 | Jul 2044 | Sep 2052 | Nov 2045 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jun 2051 | May 2055 | May 2055 | May 2055 | Aug 2049 | Mar 2051 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Mar 2053 | May 2055 | May 2055 | Mar 2052 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055
-72 IN
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62
| PROJECTED TO REACH TMIN: |  | 10: NOTE: CORROSION RATE IS BASED ON COMPARISON OF; 30: EARLIEST DATE OF PROJECTED RETIREMENT: | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | + 5 YEARS (or no data)
| WITHIN 5 YEARS |  | 10: 2020, 2022, 2023, 2024, 2025 |  | PROJECTED TUBE RETIREMENT DATE
| WITHIN 3 YEARS |  | 10: INSPECTION DATA; 30: May 2026
| WITHIN 1 YEAR |  | 10: ND; 15: NO COMPARISON DATA
RETIREMENT
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Low (hidden)
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. LOW THICKNESS MEASUREMENTS ARE IN INCHES. | [66 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | AVG | MIN
C | POSITION 'A' | LOWEST
0.099 | OF THE
TERTIARIES
C | POSITION 'B' | LOWEST | bar: 10; 30; 33; 54
0.099 | OF THE
TERTIARIES
C | POSITION 'C' | LOWEST
0.099 | OF THE
TERTIARIES
B |  | LOWEST
0.083 | +16 FT 6 IN
B |  | LOWEST
0.083 | +15 FT
B |  | LOWEST
0.083 | +13 FT 6 IN
B |  | LOWEST
0.083 | +12 FT
B | POSITION 'A' | LOWEST
0.083 | OF THE
OB PORTS
B | POSITION 'B' | LOWEST
0.083 | OF THE
OB PORTS
B | POSITION 'C' | LOWEST
0.083 | OF THE
OB PORTS
B |  | LOWEST
0.083 | +10 FT 6 IN
B |  | LOWEST | bar: 13; 30; 54
0.083 | +9 FT
B | POSITION 'A' | LOWEST
0.083 | OF THE
OSCILLATOR
B | POSITION 'B' | LOWEST
0.083 | OF THE
OSCILLATOR
B | POSITION 'C' | LOWEST
0.083 | OF THE
OSCILLATOR
B | POSITION 'D' | LOWEST
0.083 | OF THE
OSCILLATOR
B | POSITION 'E' | LOWEST
0.083 | OF THE
OSCILLATOR
B |  | LOWEST | bar: 13; 54
0.083 | +7 FT 6 IN
B |  | LOWEST | bar: 13; 39
0.083 | +6 FT
B |  | LOWEST | bar: 2
0.083 | +4 FT 6 IN
B |  | LOWEST | bar: 54; 61
0.083 | +3 FT
B |  | LOWEST | bar: 13
0.083 | +1 FT 6 IN
B |  | LOWEST
0.083 | 0 REFERENCE
B | POSITION 'A' | LOWEST
0.083 | OF THE
SECONDARIES
B | POSITION 'B' | LOWEST
0.083 | OF THE
SECONDARIES
B |  | LOWEST
0.083 | -9 IN
B | POSITION 'C' | LOWEST
0.083 | OF THE
SECONDARIES
B |  | LOWEST
0.083 | -18 IN
B |  | LOWEST
0.083 | -27 IN
A |  | LOWEST | bar: 2; 5; 61
0.083 | -36 IN
A |  | LOWEST | bar: 2
0.083 | -45 IN
A |  | LOWEST | bar: 51; 59
0.083 | -54 IN
A |  | LOWEST | bar: 60 to 61
0.083 | -63 IN
A | POSITION 'A' | LOWEST
0.083 | OF THE
PRIMARIES
A | POSITION 'B' | LOWEST
0.083 | OF THE
PRIMARIES
A | POSITION 'C' | LOWEST
0.083 | OF THE
PRIMARIES
A |  | LOWEST | bar: 2; 24 to 25
0.083 | -72 IN
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | AVG | MIN
C | 0.001-0.099 | 0.141-0.150 | 10: OUTSIDE DIAMETER:; 23: 2.969; 30: INSPECTION RESULTS
LEGEND | 0.100-0.110 | 0.151-0.160 | 10: TUBE MATERIAL:; 23: SA-178A; 35: MAX. THICKNESS
| 0.111-0.120 | 0.161-0.170 | 10: NOMINAL WALL:; 23: 0.18; 35: AVG. THICKNESS
| 0.121-0.130 | 0.171-0.180 | 10: ASME MIN:; 23: 0.099; 35: MIN. THICKNESS
| 0.131-0.140 | 0.181-0.999 | 10: MILL FLAG:; 23: 0.11; 35: STD DEV.
B | 0.001-0.083 | 0.124-0.133 | 10: OUTSIDE DIAMETER:; 23: 3; 30: INSPECTION RESULTS
LEGEND | 0.084-0.093 | 0.134-0.143 | 10: TUBE MATERIAL:; 23: SA210A1; 35: MAX. THICKNESS
| 0.094-0.103 | 0.144-0.153 | 10: NOMINAL WALL:; 23: 0.203; 35: AVG. THICKNESS
| 0.104-0.113 | 0.154-0.163 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS
| 0.114-0.123 | 0.164-0.999 | 10: MILL FLAG:; 23: 0.1; 35: STD DEV.
A | 0.001-0.083 | 0.140-0.149 | 10: OUTSIDE DIAMETER:; 23: 3; 30: INSPECTION RESULTS |  |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | 0.100-0.109 | 0.150-0.159 | 10: TUBE MATERIAL:; 23: SA-210A1; 35: MAX. THICKNESS
| 0.110-0.119 | 0.160-0.169 | 10: NOMINAL WALL:; 23: 0.3; 35: AVG. THICKNESS |  |  |  | TUBE WALL THICKNESS SURVEY (LOW VALUE)
| 0.120-0.129 | 0.170-0.179 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS
| 0.130-0.139 | 0.180-0.999 | 10: MILL FLAG:; 23: 0.2; 35: STD DEV.
LOW THICKNESS
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com