## Thickness
2025 |  | RF - REFRACTORY; ST - STRUCTURAL INTERFERENCE; | [72 empty] | OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. THICKNESS MEASUREMENTS ARE IN INCHES. | [72 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MIN
A |  | L | RF | 0.232 | 0.234 | 0.225 | 0.228 | 0.231 | 0.23 | 0.228 | 0.222 | 0.233 | 0.225 | 0.221 | 0.334 | 0.222 | 0.222 | 0.223 | 0.219 | 0.222 | 0.216 | 0.216 | 0.222 | 0.224 | 0.211 | 0.222 | 0.209 | 0.217 | 0.213 | 0.214 | 0.209 | 0.215 | 0.217 | 0.215 | 0.212 | 0.219 | 0.212 | 0.223 | 0.222 | 0.222 | 0.209 | 0.218 | 0.211 | 0.208 | 0.215 | 0.225 | 0.22 | 0.225 | 0.213 | 0.32 | 0.324 | 0.221 | 0.218 | 0.217 | 0.219 | 0.216 | 0.216 | 0.218 | 0.224 | 0.22 | 0.201 | 0.221 | 0.22 | 0.227 | 0.214 | 0.233 | 0.26 | 0.275 | 0.24 | 0.21 | RF
0.083 | +16 FT 6 IN | C | RF | 0.228 | 0.234 | 0.233 | 0.235 | 0.23 | 0.23 | 0.239 | 0.225 | 0.24 | 0.233 | 0.221 | 0.333 | 0.224 | 0.221 | 0.226 | 0.227 | 0.221 | 0.217 | 0.225 | 0.228 | 0.227 | 0.218 | 0.214 | 0.225 | 0.226 | 0.217 | 0.219 | 0.207 | 0.226 | 0.216 | 0.21 | 0.213 | 0.216 | 0.224 | 0.231 | 0.215 | 0.227 | 0.22 | 0.218 | 0.217 | 0.219 | 0.219 | 0.219 | 0.23 | 0.22 | 0.22 | 0.328 | 0.319 | 0.222 | 0.217 | 0.221 | 0.216 | 0.225 | 0.22 | 0.22 | 0.217 | 0.221 | 0.211 | 0.226 | 0.219 | 0.224 | 0.216 | 0.234 | 0.27 | 0.267 | 0.221 | 0.211 | RF
|  | R | RF | 0.239 | 0.239 | 0.225 | 0.227 | 0.232 | 0.228 | 0.222 | 0.23 | 0.233 | 0.227 | 0.218 | 0.335 | 0.219 | 0.213 | 0.219 | 0.225 | 0.217 | 0.218 | 0.217 | 0.228 | 0.214 | 0.226 | 0.22 | 0.222 | 0.225 | 0.215 | 0.219 | 0.214 | 0.214 | 0.215 | 0.212 | 0.211 | 0.211 | 0.216 | 0.223 | 0.218 | 0.228 | 0.216 | 0.215 | 0.22 | 0.214 | 0.217 | 0.215 | 0.214 | 0.222 | 0.223 | 0.32 | 0.322 | 0.223 | 0.213 | 0.227 | 0.225 | 0.22 | 0.226 | 0.222 | 0.216 | 0.215 | 0.21 | 0.22 | 0.225 | 0.223 | 0.221 | 0.224 | 0.264 | 0.267 | 0.229 | 0.208 | RF
A |  | L | 0.287 | 0.229 | 0.224 | 0.233 | 0.224 | 0.236 | 0.238 | 0.229 | 0.229 | 0.232 | 0.229 | 0.221 | 0.337 | 0.22 | 0.223 | 0.208 | 0.215 | 0.213 | 0.221 | 0.205 | 0.212 | 0.225 | 0.203 | 0.2 | 0.212 | 0.216 | 0.215 | 0.21 | 0.203 | 0.207 | 0.194 | 0.207 | 0.219 | 0.213 | 0.221 | 0.221 | 0.208 | 0.216 | 0.211 | 0.211 | 0.209 | 0.219 | 0.216 | 0.205 | 0.219 | 0.218 | 0.208 | 0.308 | 0.311 | 0.217 | 0.205 | 0.206 | 0.216 | 0.211 | 0.217 | 0.214 | 0.226 | 0.211 | 0.217 | 0.201 | 0.213 | 0.213 | 0.219 | 0.215 | 0.261 | 0.267 | 0.231 | 0.206 | RF
0.083 | +15 FT | C | 0.287 | 0.233 | 0.224 | 0.23 | 0.223 | 0.234 | 0.229 | 0.225 | 0.23 | 0.232 | 0.224 | 0.224 | 0.33 | 0.225 | 0.225 | 0.214 | 0.214 | 0.212 | 0.21 | 0.203 | 0.212 | 0.223 | 0.193 | 0.205 | 0.214 | 0.215 | 0.218 | 0.212 | 0.21 | 0.208 | 0.203 | 0.201 | 0.227 | 0.212 | 0.22 | 0.221 | 0.21 | 0.213 | 0.203 | 0.207 | 0.215 | 0.217 | 0.217 | 0.214 | 0.214 | 0.207 | 0.211 | 0.309 | 0.308 | 0.228 | 0.209 | 0.206 | 0.22 | 0.215 | 0.222 | 0.214 | 0.232 | 0.217 | 0.221 | 0.207 | 0.215 | 0.214 | 0.221 | 0.225 | 0.264 | 0.272 | 0.224 | 0.206 | RF
|  | R | 0.269 | 0.235 | 0.227 | 0.235 | 0.222 | 0.233 | 0.232 | 0.221 | 0.233 | 0.232 | 0.229 | 0.226 | 0.329 | 0.222 | 0.219 | 0.215 | 0.217 | 0.216 | 0.214 | 0.213 | 0.211 | 0.22 | 0.211 | 0.201 | 0.209 | 0.217 | 0.216 | 0.211 | 0.217 | 0.201 | 0.211 | 0.211 | 0.218 | 0.214 | 0.216 | 0.225 | 0.209 | 0.217 | 0.21 | 0.207 | 0.211 | 0.208 | 0.214 | 0.208 | 0.213 | 0.2 | 0.204 | 0.304 | 0.309 | 0.222 | 0.213 | 0.207 | 0.221 | 0.216 | 0.208 | 0.211 | 0.231 | 0.216 | 0.22 | 0.211 | 0.219 | 0.216 | 0.214 | 0.22 | 0.258 | 0.264 | 0.218 | 0.209 | RF
A |  | L | 0.236 | 0.234 | 0.216 | 0.225 | 0.236 | 0.233 | 0.228 | 0.227 | 0.229 | 0.215 | 0.219 | 0.224 | 0.335 | 0.232 | 0.217 | 0.213 | 0.221 | 0.214 | 0.239 | 0.22 | 0.213 | 0.215 | 0.208 | 0.213 | 0.221 | 0.216 | 0.207 | 0.209 | 0.214 | 0.206 | 0.208 | 0.211 | 0.215 | 0.216 | 0.206 | 0.217 | 0.217 | 0.217 | 0.219 | 0.213 | 0.219 | 0.223 | 0.215 | 0.219 | 0.225 | 0.206 | 0.219 | 0.3 | 0.311 | 0.202 | 0.211 | 0.205 | 0.205 | 0.187 | 0.192 | 0.189 | 0.197 | 0.197 | 0.207 | 0.203 | 0.208 | 0.21 | 0.212 | 0.219 | 0.26 | 0.263 | 0.228 | 0.213 | 0.261
0.083 | +13 FT 6 IN | C | 0.245 | 0.227 | 0.227 | 0.226 | 0.233 | 0.234 | 0.234 | 0.223 | 0.232 | 0.227 | 0.214 | 0.219 | 0.335 | 0.22 | 0.225 | 0.21 | 0.216 | 0.208 | 0.233 | 0.221 | 0.218 | 0.218 | 0.21 | 0.205 | 0.215 | 0.217 | 0.213 | 0.202 | 0.203 | 0.206 | 0.208 | 0.21 | 0.212 | 0.217 | 0.212 | 0.216 | 0.22 | 0.213 | 0.212 | 0.201 | 0.195 | 0.207 | 0.207 | 0.197 | 0.208 | 0.204 | 0.204 | 0.306 | 0.301 | 0.207 | 0.204 | 0.211 | 0.214 | 0.202 | 0.21 | 0.215 | 0.205 | 0.218 | 0.221 | 0.213 | 0.211 | 0.221 | 0.213 | 0.219 | 0.26 | 0.279 | 0.229 | 0.205 | 0.268
|  | R | 0.231 | 0.226 | 0.231 | 0.229 | 0.232 | 0.226 | 0.224 | 0.222 | 0.23 | 0.232 | 0.225 | 0.232 | 0.329 | 0.221 | 0.217 | 0.212 | 0.219 | 0.214 | 0.237 | 0.225 | 0.222 | 0.217 | 0.203 | 0.208 | 0.217 | 0.216 | 0.213 | 0.21 | 0.205 | 0.207 | 0.209 | 0.203 | 0.213 | 0.215 | 0.209 | 0.215 | 0.22 | 0.211 | 0.193 | 0.197 | 0.218 | 0.196 | 0.2 | 0.214 | 0.202 | 0.197 | 0.216 | 0.304 | 0.304 | 0.202 | 0.204 | 0.208 | 0.204 | 0.203 | 0.214 | 0.204 | 0.212 | 0.214 | 0.216 | 0.218 | 0.215 | 0.214 | 0.217 | 0.218 | 0.271 | 0.279 | 0.224 | 0.222 | 0.255
A |  | L | 0.234 | 0.221 | 0.236 | 0.232 | 0.23 | 0.231 | 0.229 | 0.238 | 0.222 | 0.235 | 0.216 | 0.225 | 0.327 | 0.223 | 0.22 | 0.207 | 0.203 | 0.204 | 0.214 | 0.203 | 0.218 | 0.201 | 0.207 | 0.203 | 0.206 | 0.198 | 0.21 | 0.205 | 0.208 | 0.21 | 0.2 | 0.219 | 0.196 | 0.22 | 0.22 | 0.224 | 0.201 | 0.2 | 0.195 | 0.211 | 0.185 | 0.223 | 0.193 | 0.171 | 0.196 | 0.199 | 0.186 | 0.277 | 0.286 | 0.208 | 0.22 | 0.184 | 0.18 | 0.209 | 0.194 | 0.214 | 0.205 | 0.212 | 0.201 | 0.215 | 0.217 | 0.229 | 0.217 | 0.226 | 0.266 | 0.281 | 0.218 | 0.225 | 0.259
0.083 | +12 FT | C | 0.224 | 0.222 | 0.236 | 0.227 | 0.225 | 0.239 | 0.234 | 0.235 | 0.228 | 0.231 | 0.223 | 0.218 | 0.332 | 0.224 | 0.223 | 0.218 | 0.205 | 0.209 | 0.202 | 0.203 | 0.209 | 0.208 | 0.199 | 0.211 | 0.203 | 0.192 | 0.203 | 0.194 | 0.212 | 0.191 | 0.193 | 0.197 | 0.214 | 0.218 | 0.221 | 0.217 | 0.22 | 0.217 | 0.207 | 0.186 | 0.198 | 0.171 | 0.202 | 0.175 | 0.184 | 0.188 | 0.182 | 0.285 | 0.282 | 0.213 | 0.22 | 0.191 | 0.196 | 0.191 | 0.197 | 0.197 | 0.201 | 0.208 | 0.213 | 0.221 | 0.216 | 0.222 | 0.212 | 0.223 | 0.26 | 0.264 | 0.225 | 0.221 | 0.26
|  | R | 0.223 | 0.227 | 0.233 | 0.232 | 0.221 | 0.227 | 0.231 | 0.225 | 0.226 | 0.237 | 0.218 | 0.228 | 0.331 | 0.219 | 0.22 | 0.217 | 0.214 | 0.213 | 0.206 | 0.209 | 0.21 | 0.203 | 0.201 | 0.204 | 0.203 | 0.213 | 0.199 | 0.198 | 0.215 | 0.205 | 0.208 | 0.204 | 0.217 | 0.221 | 0.224 | 0.214 | 0.211 | 0.207 | 0.192 | 0.21 | 0.218 | 0.195 | 0.189 | 0.181 | 0.194 | 0.187 | 0.182 | 0.291 | 0.293 | 0.2 | 0.183 | 0.192 | 0.203 | 0.201 | 0.198 | 0.206 | 0.226 | 0.21 | 0.212 | 0.225 | 0.213 | 0.225 | 0.215 | 0.23 | 0.264 | 0.257 | 0.223 | 0.219 | 0.241
A | POSITION 'A' | L | 2: 0.219; 3: 0.225; 4: 0.226; 5: 0.216; 65: 0.254; 66: 0.271; 67: 0.227; 68: 0.211
0.083 | OF THE | C | 2: 0.212; 3: 0.228; 4: 0.224; 5: 0.218; 65: 0.256; 66: 0.275; 67: 0.229; 68: 0.209
| OB PORTS | R | 2: 0.217; 3: 0.227; 4: 0.229; 5: 0.217; 65: 0.255; 66: 0.275; 67: 0.22; 68: 0.219
A | POSITION 'B' | L | 2: 0.213; 3: 0.229; 4: 0.222; 5: 0.225; 65: 0.256; 66: 0.263; 67: 0.223; 68: 0.217
0.083 | OF THE | C | 2: 0.21; 3: 0.223; 4: 0.215; 5: 0.227; 65: 0.256; 66: 0.266; 67: 0.219; 68: 0.203
| OB PORTS | R | 2: 0.215; 3: 0.227; 4: 0.225; 5: 0.217; 65: 0.262; 66: 0.27; 67: 0.217; 68: 0.212
A | POSITION 'C' | L | 2: 0.226; 3: 0.235; 4: 0.223; 5: 0.224; 65: 0.254; 66: 0.254; 67: 0.229; 68: 0.213
0.083 | OF THE | C | 2: 0.214; 3: 0.222; 4: 0.23; 5: 0.23; 65: 0.264; 66: 0.27; 67: 0.222; 68: 0.214
| OB PORTS | R | 2: 0.216; 3: 0.224; 4: 0.233; 5: 0.23; 65: 0.261; 66: 0.277; 67: 0.216; 68: 0.216
A |  | L | 0.233 | 0.218 | 0.216 | 0.225 | 0.232 | 0.221 | 0.227 | 0.221 | 0.225 | 0.218 | 0.218 | 0.227 | 0.32 | 0.21 | 0.216 | 0.195 | 0.197 | 0.217 | 0.2 | 0.205 | 0.202 | 0.196 | 0.188 | 0.189 | 0.223 | 0.205 | 0.205 | 0.199 | 0.186 | 0.204 | 0.194 | 0.206 | 0.212 | 0.215 | 0.22 | 0.231 | 0.209 | 0.194 | 0.198 | 0.206 |  | 0.192 | 0.176 | 0.249 | 0.174 | 0.2 | 0.187 | 0.306 | 0.256 | 0.18 | 0.225 | 0.206 | 0.182 | 0.204 | 0.201 | 0.206 | 0.228 | 0.206 | 0.206 | 0.208 | 0.212 | 0.208 | 0.213 | 0.225 | 0.27 | 0.267 | 0.214 | 0.218 | 0.265
0.083 | +10 FT 6 IN | C | 0.225 | 0.221 | 0.222 | 0.233 | 0.222 | 0.22 | 0.225 | 0.217 | 0.221 | 0.222 | 0.221 | 0.22 | 0.319 | 0.212 | 0.21 | 0.205 | 0.196 | 0.23 | 0.201 | 0.194 | 0.207 | 0.203 | 0.197 | 0.199 | 0.19 | 0.201 | 0.21 | 0.195 | 0.198 | 0.194 | 0.2 | 0.208 | 0.211 | 0.218 | 0.217 | 0.236 | 0.205 | 0.195 | 0.182 | 0.181 | 0.174 | 0.186 | 0.18 | 0.246 | 0.186 | 0.179 | 0.174 | 0.295 | 0.243 | 0.193 | 0.193 | 0.192 | 0.198 | 0.197 | 0.229 | 0.22 | 0.217 | 0.209 | 0.205 | 0.214 | 0.215 | 0.208 | 0.221 | 0.216 | 0.265 | 0.28 | 0.214 | 0.214 | 0.253
|  | R | 0.225 | 0.223 | 0.217 | 0.231 | 0.22 | 0.224 | 0.23 | 0.221 | 0.216 | 0.223 | 0.221 | 0.222 | 0.318 | 0.213 | 0.237 | 0.202 | 0.193 | 0.203 | 0.203 | 0.225 | 0.201 | 0.205 | 0.198 | 0.205 | 0.188 | 0.203 | 0.19 | 0.199 | 0.191 | 0.204 | 0.213 | 0.189 | 0.217 | 0.206 | 0.224 | 0.236 | 0.199 | 0.198 | 0.167 | 0.191 | 0.187 | 0.176 | 0.246 | 0.241 | 0.192 | 0.186 | 0.201 | 0.291 | 0.24 | 0.19 | 0.189 | 0.201 | 0.198 | 0.196 | 0.201 | 0.207 | 0.205 | 0.212 | 0.201 | 0.213 | 0.216 | 0.214 | 0.214 | 0.219 | 0.273 | 0.262 | 0.216 | 0.214 | 0.265
A |  | L | 0.208 | 0.208 | 0.218 | 0.227 | 0.227 | 0.23 | 0.222 | 0.218 | 0.227 | 0.213 | 0.219 | 0.204 | 0.325 | 0.208 | 0.195 | 0.211 | 0.212 | 0.205 | 0.206 | 0.189 | 0.214 | 0.181 | 0.221 | 0.201 | 0.206 | 0.217 | 0.191 | 0.199 | 0.205 | 0.197 | 0.202 | 0.21 | 0.207 | 0.239 | 0.222 | 0.214 | 0.184 | 0.18 | 0.182 | 0.188 | 0.179 | 0.191 | 0.192 | 0.197 | 0.206 | 0.19 | 0.208 | 0.288 | 0.226 | 0.18 | 0.18 | 0.17 | 0.196 | 0.194 | 0.197 | 0.218 | 0.215 | 0.211 | 0.206 | 0.213 | 0.217 | 0.225 | 0.226 | 0.23 | 0.254 | 0.276 | 0.226 | 0.216 | 0.277
0.083 | +9 FT | C | 0.219 | 0.208 | 0.217 | 0.229 | 0.218 | 0.227 | 0.222 | 0.216 | 0.22 | 0.215 | 0.216 | 0.206 | 0.33 | 0.201 | 0.197 | 0.215 | 0.211 | 0.218 | 0.206 | 0.19 | 0.202 | 0.18 | 0.228 | 0.201 | 0.206 | 0.209 | 0.19 | 0.201 | 0.202 | 0.198 | 0.199 | 0.211 | 0.208 | 0.195 | 0.225 | 0.214 | 0.185 | 0.183 | 0.182 | 0.182 | 0.179 | 0.201 | 0.18 | 0.257 | 0.24 | 0.193 | 0.186 | 0.285 | 0.223 | 0.179 | 0.188 | 0.194 | 0.195 | 0.191 | 0.197 | 0.211 | 0.212 | 0.208 | 0.203 | 0.218 | 0.214 | 0.229 | 0.226 | 0.217 | 0.253 | 0.265 | 0.233 | 0.217 | 0.275
|  | R | 0.218 | 0.211 | 0.215 | 0.228 | 0.238 | 0.225 | 0.222 | 0.214 | 0.223 | 0.213 | 0.218 | 0.205 | 0.321 | 0.206 | 0.201 | 0.214 | 0.206 | 0.215 | 0.213 | 0.191 | 0.204 | 0.181 | 0.187 | 0.196 | 0.196 | 0.211 | 0.196 | 0.201 | 0.204 | 0.201 | 0.207 | 0.215 | 0.203 | 0.195 | 0.227 | 0.213 | 0.184 | 0.181 | 0.185 | 0.183 | 0.178 | 0.203 | 0.171 | 0.202 | 0.207 | 0.194 | 0.18 | 0.292 | 0.221 | 0.188 | 0.181 | 0.186 | 0.197 | 0.191 | 0.196 | 0.212 | 0.215 | 0.205 | 0.203 | 0.211 | 0.217 | 0.21 | 0.224 | 0.213 | 0.26 | 0.278 | 0.237 | 0.216 | 0.27
A | POSITION 'A' | L | 33: 0.214; 34: 0.243; 35: 0.228; 36: 0.209; 37: 0.219; 38: 0.193
0.083 | OF THE | C | 33: 0.212; 34: 0.214; 35: 0.218; 36: 0.219; 37: 0.209; 38: 0.202
| OSCILLATOR | R | 33: 0.207; 34: 0.213; 35: 0.213; 36: 0.213; 37: 0.206; 38: 0.186
A | POSITION 'B' | L | 33: 0.207; 34: 0.217; 35: 0.224; 36: 0.24; 37: 0.22; 38: 0.199
0.083 | OF THE | C | 33: 0.212; 34: 0.221; 35: 0.222; 36: 0.23; 37: 0.208; 38: 0.197
| OSCILLATOR | R | 33: 0.212; 34: 0.215; 35: 0.218; 36: 0.204; 37: 0.208; 38: 0.2
A | POSITION 'C' | L | 33: 0.207; 34: 0.21; 35: 0.216; 36: 0.232; 37: 0.208; 38: 0.193
0.083 | OF THE | C | 33: 0.214; 34: 0.217; 35: 0.222; 36: 0.228; 37: 0.205; 38: 0.187
| OSCILLATOR | R | 33: 0.213; 34: 0.215; 35: 0.225; 36: 0.229; 37: 0.211; 38: 0.211
A | POSITION 'D' | L | 33: 0.194; 34: 0.215; 35: 0.224; 36: 0.227; 37: 0.223; 38: 0.199
0.083 | OF THE | C | 33: 0.194; 34: 0.204; 35: 0.215; 36: 0.236; 37: 0.216; 38: 0.189
| OSCILLATOR | R | 33: 0.226; 34: 0.225; 35: 0.219; 36: 0.222; 37: 0.216; 38: 0.178
A | POSITION 'E' | L | 33: 0.191; 34: 0.22; 35: 0.231; 36: 0.22; 37: 0.22; 38: 0.204
0.083 | OF THE | C | 33: 0.198; 34: 0.198; 35: 0.226; 36: 0.216; 37: 0.22; 38: 0.205
| OSCILLATOR | R | 33: 0.208; 34: 0.231; 35: 0.228; 36: 0.215; 37: 0.212; 38: 0.217
A |  | L | 0.234 | 0.208 | 0.22 | 0.229 | 0.226 | 0.228 | 0.223 | 0.224 | 0.222 | 0.205 | 0.209 | 0.207 | 0.316 | 0.199 | 0.195 | 0.196 | 0.215 | 0.211 | 0.201 | 0.199 | 0.191 | 0.185 | 0.216 | 0.203 | 0.209 | 0.182 | 0.189 | 0.196 | 0.206 | 0.206 | 0.215 | 0.197 | 0.2 | 0.2 | 0.207 | 0.196 | 0.197 | 0.182 | 0.197 | 0.189 | 0.195 | 0.181 | 0.201 | 0.2 | 0.198 | 0.186 | 0.179 | 0.296 | 0.294 | 0.19 | 0.198 | 0.207 | 0.192 | 0.204 | 0.204 | 0.214 | 0.213 | 0.253 | 0.206 | 0.208 | 0.214 | 0.213 | 0.209 | 0.242 | 0.252 | 0.252 | 0.21 | 0.208 | 0.279
0.083 | +7 FT 6 IN | C | 0.211 | 0.217 | 0.224 | 0.237 | 0.218 | 0.228 | 0.223 | 0.231 | 0.217 | 0.21 | 0.214 | 0.209 | 0.323 | 0.211 | 0.206 | 0.197 | 0.197 | 0.195 | 0.206 | 0.206 | 0.191 | 0.176 | 0.199 | 0.171 | 0.183 | 0.183 | 0.198 | 0.226 | 0.206 | 0.187 | 0.203 | 0.175 | 0.182 | 0.203 | 0.202 | 0.194 | 0.199 | 0.183 | 0.191 | 0.191 | 0.181 | 0.184 | 0.189 | 0.182 | 0.182 | 0.193 | 0.196 | 0.296 | 0.3 | 0.196 | 0.199 | 0.233 | 0.197 | 0.209 | 0.214 | 0.209 | 0.219 | 0.221 | 0.206 | 0.21 | 0.212 | 0.214 | 0.214 | 0.206 | 0.254 | 0.25 | 0.211 | 0.214 | 0.244
|  | R | 0.229 | 0.212 | 0.22 | 0.233 | 0.223 | 0.217 | 0.218 | 0.232 | 0.218 | 0.208 | 0.219 | 0.202 | 0.315 | 0.195 | 0.204 | 0.193 | 0.189 | 0.206 | 0.181 | 0.187 | 0.178 | 0.184 | 0.209 | 0.203 | 0.184 | 0.218 | 0.221 | 0.213 | 0.206 | 0.228 | 0.193 | 0.174 | 0.18 | 0.199 | 0.211 | 0.192 | 0.195 | 0.184 | 0.203 | 0.199 | 0.194 | 0.186 | 0.194 | 0.186 | 0.192 | 0.191 | 0.2 | 0.29 | 0.309 | 0.194 | 0.194 | 0.197 | 0.2 | 0.205 | 0.213 | 0.213 | 0.217 | 0.211 | 0.23 | 0.216 | 0.207 | 0.21 | 0.21 | 0.209 | 0.254 | 0.251 | 0.205 | 0.205 | 0.233
A |  | L | 0.214 | 0.223 | 0.217 | 0.226 | 0.223 | 0.216 | 0.217 | 0.211 | 0.215 | 0.206 | 0.208 | 0.202 | 0.314 | 0.203 | 0.197 | 0.186 | 0.192 | 0.178 | 0.193 | 0.18 | 0.175 | 0.194 | 0.212 | 0.172 | 0.186 | 0.197 | 0.209 | 0.22 | 0.228 | 0.217 | 0.207 | 0.216 | 0.186 | 0.204 | 0.199 | 0.209 | 0.18 | 0.194 | 0.202 | 0.204 | 0.197 | 0.192 | 0.196 | 0.205 | 0.201 | 0.206 | 0.205 | 0.307 | 0.31 | 0.209 | 0.212 | 0.204 | 0.214 | 0.194 | 0.21 | 0.22 | 0.226 | 0.21 | 0.211 | 0.213 | 0.218 | 0.213 | 0.221 | 0.215 | 0.258 | 0.259 | 0.219 | 0.224 | 0.25
0.083 | +6 FT | C | 0.223 | 0.217 | 0.221 | 0.219 | 0.222 | 0.218 | 0.212 | 0.221 | 0.208 | 0.208 | 0.202 | 0.195 | 0.317 | 0.206 | 0.192 | 0.18 | 0.193 | 0.19 | 0.19 | 0.172 | 0.186 | 0.189 | 0.198 | 0.177 | 0.195 | 0.2 | 0.211 | 0.227 | 0.224 | 0.222 | 0.218 | 0.196 | 0.182 | 0.194 | 0.196 | 0.199 | 0.192 | 0.201 | 0.208 | 0.207 | 0.216 | 0.196 | 0.195 | 0.207 | 0.207 | 0.21 | 0.209 | 0.303 | 0.304 | 0.207 | 0.212 | 0.218 | 0.216 | 0.203 | 0.213 | 0.213 | 0.217 | 0.209 | 0.216 | 0.211 | 0.211 | 0.22 | 0.218 | 0.213 | 0.256 | 0.254 | 0.222 | 0.211 | 0.264
|  | R | 0.234 | 0.213 | 0.221 | 0.214 | 0.223 | 0.211 | 0.211 | 0.215 | 0.206 | 0.208 | 0.214 | 0.208 | 0.311 | 0.194 | 0.198 | 0.191 | 0.192 | 0.178 | 0.199 | 0.167 | 0.179 | 0.182 | 0.187 | 0.201 | 0.178 | 0.21 | 0.218 | 0.222 | 0.228 | 0.221 | 0.201 | 0.192 | 0.177 | 0.198 | 0.199 | 0.188 | 0.202 | 0.197 | 0.209 | 0.217 | 0.196 | 0.202 | 0.191 | 0.202 | 0.213 | 0.203 | 0.201 | 0.297 | 0.309 | 0.209 | 0.21 | 0.22 | 0.223 | 0.211 | 0.219 | 0.234 | 0.22 | 0.223 | 0.22 | 0.226 | 0.215 | 0.23 | 0.212 | 0.227 | 0.26 | 0.256 | 0.216 | 0.21 | 0.237
A |  | L | 0.224 | 0.218 | 0.233 | 0.219 | 0.226 | 0.213 | 0.212 | 0.238 | 0.212 | 0.205 | 0.207 | 0.193 | 0.305 | 0.211 | 0.199 | 0.215 | 0.187 | 0.184 | 0.176 | 0.189 | 0.191 | 0.191 | 0.205 | 0.167 | 0.182 | 0.199 | 0.203 | 0.219 | 0.221 | 0.217 | 0.205 | 0.202 | 0.203 | 0.186 | 0.21 | 0.199 | 0.2 | 0.203 | 0.208 | 0.215 | 0.205 | 0.208 | 0.199 | 0.201 | 0.206 | 0.202 | 0.215 | 0.31 | 0.297 | 0.195 | 0.21 | 0.204 | 0.202 | 0.206 | 0.217 | 0.209 | 0.211 | 0.22 | 0.207 | 0.219 | 0.214 | 0.2 | 0.211 | 0.204 | 0.259 | 0.262 | 0.209 | 0.206 | 0.271
0.083 | +4 FT 6 IN | C | 0.226 | 0.216 | 0.22 | 0.219 | 0.218 | 0.21 | 0.211 | 0.209 | 0.209 | 0.21 | 0.207 | 0.208 | 0.308 | 0.21 | 0.196 | 0.194 | 0.191 | 0.189 | 0.178 | 0.198 | 0.201 | 0.183 | 0.184 | 0.182 | 0.172 | 0.201 | 0.22 | 0.217 | 0.219 | 0.214 | 0.209 | 0.197 | 0.202 | 0.205 | 0.206 | 0.209 | 0.207 | 0.203 | 0.207 | 0.207 | 0.202 | 0.206 | 0.202 | 0.198 | 0.204 | 0.203 | 0.203 | 0.284 | 0.279 | 0.192 | 0.203 | 0.225 | 0.206 | 0.21 | 0.211 | 0.217 | 0.214 | 0.212 | 0.209 | 0.206 | 0.212 | 0.21 | 0.209 | 0.203 | 0.248 | 0.251 | 0.226 | 0.212 | 0.247
|  | R | 0.216 | 0.23 | 0.219 | 0.219 | 0.213 | 0.21 | 0.214 | 0.208 | 0.211 | 0.203 | 0.199 | 0.204 | 0.312 | 0.207 | 0.191 | 0.186 | 0.189 | 0.179 | 0.169 | 0.221 | 0.187 | 0.193 | 0.185 | 0.187 | 0.18 | 0.205 | 0.218 | 0.215 | 0.226 | 0.215 | 0.201 | 0.205 | 0.208 | 0.203 | 0.206 | 0.215 | 0.207 | 0.21 | 0.212 | 0.211 | 0.204 | 0.207 | 0.2 | 0.198 | 0.205 | 0.206 | 0.203 | 0.285 | 0.285 | 0.203 | 0.218 | 0.198 | 0.209 | 0.209 | 0.217 | 0.214 | 0.216 | 0.211 | 0.218 | 0.211 | 0.211 | 0.237 | 0.209 | 0.202 | 0.264 | 0.257 | 0.208 | 0.189 | 0.237
A |  | L | 0.22 | 0.221 | 0.226 | 0.229 | 0.22 | 0.22 | 0.21 | 0.216 | 0.223 | 0.213 | 0.208 | 0.198 | 0.317 | 0.223 | 0.21 | 0.22 | 0.185 | 0.193 | 0.206 | 0.192 | 0.19 | 0.196 | 0.186 | 0.194 | 0.191 | 0.213 | 0.197 | 0.213 | 0.196 | 0.222 | 0.213 | 0.192 | 0.203 | 0.208 | 0.212 | 0.211 | 0.208 | 0.211 | 0.222 | 0.214 | 0.211 | 0.229 | 0.201 | 0.214 | 0.207 | 0.202 | 0.206 | 0.296 | 0.284 | 0.209 | 0.208 | 0.208 | 0.224 | 0.233 | 0.22 | 0.234 | 0.212 | 0.212 | 0.212 | 0.204 | 0.212 | 0.23 | 0.209 | 0.2 | 0.256 | 0.26 | 0.223 | 0.228 | 0.279
0.083 | +3 FT | C | 0.224 | 0.219 | 0.222 | 0.227 | 0.214 | 0.218 | 0.212 | 0.229 | 0.218 | 0.215 | 0.2 | 0.21 | 0.317 | 0.22 | 0.214 | 0.209 | 0.193 | 0.198 | 0.183 | 0.189 | 0.197 | 0.207 | 0.196 | 0.193 | 0.206 | 0.197 | 0.21 | 0.22 | 0.202 | 0.213 | 0.205 | 0.206 | 0.209 | 0.211 | 0.211 | 0.207 | 0.216 | 0.21 | 0.217 | 0.214 | 0.205 | 0.207 | 0.2 | 0.191 | 0.198 | 0.201 | 0.197 | 0.271 | 0.26 | 0.199 | 0.199 | 0.203 | 0.216 | 0.218 | 0.217 | 0.215 | 0.205 | 0.21 | 0.212 | 0.208 | 0.216 | 0.214 | 0.215 | 0.202 | 0.263 | 0.265 | 0.219 | 0.213 | 0.25
|  | R | 0.205 | 0.22 | 0.23 | 0.224 | 0.222 | 0.214 | 0.212 | 0.22 | 0.231 | 0.218 | 0.203 | 0.202 | 0.315 | 0.214 | 0.224 | 0.2 | 0.189 | 0.204 | 0.192 | 0.204 | 0.195 | 0.2 | 0.19 | 0.187 | 0.201 | 0.209 | 0.218 | 0.216 | 0.213 | 0.212 | 0.202 | 0.207 | 0.216 | 0.206 | 0.216 | 0.21 | 0.212 | 0.213 | 0.215 | 0.2 | 0.213 | 0.209 | 0.206 | 0.192 | 0.204 | 0.202 | 0.192 | 0.274 | 0.257 | 0.224 | 0.201 | 0.21 | 0.224 | 0.208 | 0.206 | 0.213 | 0.207 | 0.223 | 0.215 | 0.215 | 0.218 | 0.235 | 0.206 | 0.203 | 0.252 | 0.248 | 0.214 | 0.199 | 0.258
A |  | L | 0.219 | 0.229 | 0.222 | 0.227 | 0.222 | 0.237 | 0.231 | 0.238 | 0.219 | 0.211 | 0.204 | 0.219 | 0.324 | 0.236 | 0.209 | 0.203 | 0.206 | 0.203 | 0.212 | 0.219 | 0.215 | 0.225 | 0.215 | 0.211 | 0.207 | 0.204 | 0.209 | 0.209 | 0.204 | 0.2 | 0.205 | 0.219 | 0.213 | 0.216 | 0.206 | 0.205 | 0.208 | 0.215 | 0.213 | 0.208 | 0.204 | 0.196 | 0.195 | 0.211 | 0.199 | 0.2 | 0.198 | 0.295 | 0.29 | 0.197 | 0.207 | 0.201 | 0.204 | 0.206 | 0.199 | 0.2 | 0.203 | 0.202 | 0.212 | 0.215 | 0.212 | 0.214 | 0.206 | 0.241 | 0.219 | 0.223 | 0.229 | 0.227 | 0.256
0.083 | +1 FT 6 IN | C | 0.218 | 0.213 | 0.221 | 0.227 | 0.224 | 0.215 | 0.215 | 0.219 | 0.219 | 0.219 | 0.226 | 0.217 | 0.325 | 0.215 | 0.205 | 0.205 | 0.204 | 0.204 | 0.207 | 0.21 | 0.217 | 0.223 | 0.217 | 0.212 | 0.213 | 0.209 | 0.216 | 0.206 | 0.205 | 0.201 | 0.209 | 0.21 | 0.23 | 0.204 | 0.206 | 0.197 | 0.206 | 0.212 | 0.219 | 0.204 | 0.196 | 0.195 | 0.196 | 0.202 | 0.2 | 0.186 | 0.196 | 0.284 | 0.28 | 0.197 | 0.203 | 0.201 | 0.213 | 0.215 | 0.198 | 0.199 | 0.212 | 0.203 | 0.21 | 0.21 | 0.214 | 0.223 | 0.239 | 0.224 | 0.222 | 0.22 | 0.229 | 0.221 | 0.255
|  | R | 0.224 | 0.213 | 0.223 | 0.225 | 0.213 | 0.224 | 0.217 | 0.231 | 0.228 | 0.223 | 0.216 | 0.216 | 0.317 | 0.209 | 0.209 | 0.209 | 0.206 | 0.205 | 0.211 | 0.209 | 0.205 | 0.221 | 0.216 | 0.219 | 0.208 | 0.211 | 0.216 | 0.205 | 0.203 | 0.205 | 0.209 | 0.206 | 0.218 | 0.201 | 0.2 | 0.195 | 0.202 | 0.22 | 0.2 | 0.201 | 0.196 | 0.186 | 0.192 | 0.197 | 0.18 | 0.184 | 0.183 | 0.273 | 0.288 | 0.195 | 0.215 | 0.203 | 0.21 | 0.214 | 0.201 | 0.21 | 0.218 | 0.207 | 0.214 | 0.224 | 0.216 | 0.22 | 0.2 | 0.221 | 0.23 | 0.233 | 0.203 | 0.237 | 0.239
A |  | L | 0.203 | 0.196 | 0.216 | 0.228 | 0.242 | 0.219 | 0.215 | 0.206 | 0.214 | 0.211 | 0.212 | 0.226 | 0.328 | 0.232 | 0.214 | 0.208 | 0.205 | 0.203 | 0.201 | 0.228 | 0.244 | 0.24 | 0.203 | 0.208 | 0.213 | 0.206 | 0.202 | 0.211 | 0.194 | 0.193 | 0.205 | 0.221 | 0.231 | 0.226 | 0.198 | 0.195 | 0.205 | 0.215 | 0.236 | 0.231 | 0.231 | 0.199 | 0.199 | 0.231 | 0.219 | 0.181 | 0.187 | 0.291 | 0.293 | 0.183 | 0.186 | 0.233 | 0.21 | 0.199 | 0.216 | 0.224 | 0.229 | 0.226 | 0.208 | 0.219 | 0.212 | 0.223 | 0.199 | 0.266 | 0.254 | 0.222 | 0.233 | 0.205 | 0.314
0.083 | 0 REFERENCE | C | 0.206 | 0.196 | 0.216 | 0.242 | 0.234 | 0.221 | 0.221 | 0.214 |  | 0.228 | 0.23 | 0.227 | 0.34 | 0.209 | 0.213 | 0.206 | 0.205 | 0.203 | 0.197 | 0.227 | 0.246 | 0.24 | 0.2 | 0.208 | 0.193 | 0.209 | 0.202 | 0.197 | 0.19 | 0.215 | 0.224 | 0.226 | 0.229 | 0.231 | 0.197 | 0.193 | 0.202 | 0.215 | 0.237 | 0.233 | 0.242 | 0.2 | 0.194 | 0.18 | 0.18 | 0.181 | 0.205 | 0.292 | 0.295 | 0.182 | 0.184 | 0.184 | 0.198 | 0.196 | 0.197 | 0.249 | 0.229 | 0.226 | 0.208 | 0.22 | 0.218 | 0.219 | 0.199 | 0.267 | 0.224 | 0.204 | 0.237 | 0.205 | 0.321
|  | R | 0.217 | 0.197 | 0.231 | 0.235 | 0.217 | 0.213 | 0.207 | 0.212 | 0.215 | 0.211 | 0.228 | 0.231 | 0.314 | 0.207 | 0.21 | 0.206 | 0.205 | 0.203 | 0.2 | 0.227 | 0.244 | 0.237 | 0.204 | 0.202 | 0.204 | 0.201 | 0.189 | 0.19 | 0.193 | 0.209 | 0.218 | 0.224 | 0.236 | 0.231 | 0.196 | 0.197 | 0.206 | 0.216 | 0.234 | 0.235 | 0.222 | 0.199 | 0.195 | 0.18 | 0.207 | 0.181 | 0.213 | 0.311 | 0.295 | 0.182 | 0.186 | 0.207 | 0.206 | 0.209 | 0.222 | 0.234 | 0.229 | 0.225 | 0.206 | 0.223 | 0.222 | 0.2 | 0.199 | 0.267 | 0.227 | 0.2 | 0.234 | 0.204 | 0.27
A | POSITION 'A' | L |  | 0.212 | 0.223 | 0.215 | 0.207 | 0.225 | 0.225 |  |  |  | 0.205 | 0.215 | 0.328 | 0.225 | 0.227 | 0.208 |  |  | 0.202 | 0.209 | 0.223 | 0.212 | 0.22 | 0.202 | [7 empty] | 0.244 | 0.238 | 0.223 | 0.214 |  | 0.212 | 0.215 | 0.212 | 0.214 | 0.215 | 0.213 |  |  |  | 0.216 | 0.211 | 0.299 | 0.308 | 0.192 | 0.196 |  |  | 0.204 | 0.209 | 0.209 | 0.206 | 0.212 | 0.209 |  |  | 0.202 | 0.195 | 0.212 | 0.249 | 0.224 | 0.209
0.083 | OF THE | C |  | 0.207 | 0.215 | 0.217 | 0.203 | 0.224 | 0.217 |  |  |  | 0.204 | 0.209 | 0.307 | 0.214 | 0.205 | 0.204 |  |  | 0.202 | 0.214 | 0.194 | 0.22 | 0.208 | 0.212 | [7 empty] | 0.207 | 0.221 | 0.21 | 0.204 |  | 0.202 | 0.213 | 0.211 | 0.199 | 0.203 | 0.203 |  |  |  | 0.189 | 0.218 | 0.301 | 0.3 | 0.187 | 0.2 |  |  | 0.207 | 0.193 | 0.192 | 0.214 | 0.209 | 0.211 |  |  | 0.216 | 0.196 | 0.205 | 0.191 | 0.227 | 0.207
| SECONDARIES | R |  | 0.208 | 0.215 | 0.216 | 0.222 | 0.216 | 0.218 |  |  |  | 0.205 | 0.21 | 0.309 | 0.221 | 0.207 | 0.225 |  |  | 0.214 | 0.222 | 0.203 | 0.238 | 0.211 | 0.213 | [7 empty] | 0.202 | 0.218 | 0.205 | 0.205 |  | 0.205 | 0.21 | 0.196 | 0.211 | 0.197 | 0.203 |  |  |  | 0.179 | 0.213 | 0.316 | 0.289 | 0.192 | 0.178 |  |  | 0.199 | 0.192 | 0.183 | 0.201 | 0.196 | 0.211 |  |  | 0.233 | 0.221 | 0.202 | 0.23 | 0.231 | 0.214
A | POSITION 'B' | L |  | 0.205 | 0.206 | 0.225 | 0.228 | 0.223 | 0.211 |  |  |  | 0.205 | 0.222 | 0.321 | 0.225 | 0.214 | 0.217 |  |  | 0.214 | 0.224 | 0.241 | 0.242 | 0.218 | 0.207 | [7 empty] | 0.2 | 0.22 | 0.223 | 0.218 |  | 0.196 | 0.218 | 0.229 | 0.235 | 0.219 | 0.217 |  |  |  | 0.197 | 0.201 | 0.288 | 0.318 | 0.209 | 0.21 |  |  | 0.184 | 0.189 | 0.219 | 0.226 | 0.208 | 0.226 |  |  | 0.22 | 0.22 | 0.25 | 0.237 | 0.219 | 0.21
0.083 | OF THE | C |  | 0.192 | 0.206 | 0.227 | 0.226 | 0.222 | 0.209 |  |  |  | 0.212 | 0.219 | 0.343 | 0.229 | 0.198 | 0.216 |  |  | 0.204 | 0.225 | 0.244 | 0.236 | 0.284 | 0.202 | [7 empty] | 0.209 | 0.219 | 0.219 | 0.231 |  | 0.203 | 0.221 | 0.226 | 0.226 | 0.217 | 0.201 |  |  |  | 0.181 | 0.189 | 0.29 | 0.303 | 0.188 | 0.183 |  |  | 0.191 | 0.209 | 0.228 | 0.228 | 0.217 | 0.218 |  |  | 0.207 | 0.225 | 0.24 | 0.246 | 0.213 | 0.209
| SECONDARIES | R |  | 0.201 | 0.207 | 0.236 | 0.233 | 0.211 | 0.209 |  |  |  | 0.219 | 0.215 | 0.336 | 0.229 | 0.208 | 0.209 |  |  | 0.216 | 0.23 | 0.236 | 0.233 | 0.218 | 0.217 | [7 empty] | 0.207 | 0.225 | 0.231 | 0.194 |  | 0.197 | 0.221 | 0.229 | 0.227 | 0.213 | 0.186 |  |  |  | 0.19 | 0.189 | 0.308 | 0.302 | 0.204 | 0.177 |  |  | 0.189 | 0.223 | 0.227 | 0.219 | 0.214 | 0.236 |  |  | 0.216 | 0.309 | 0.246 | 0.241 | 0.245 | 0.213
A |  | L | 0.212 | 0.202 | 0.21 | 0.194 | 0.195 | 0.22 | 0.22 | 0.223 | 0.202 | 0.233 | 0.229 | 0.236 | 0.331 | 0.225 | 0.21 | 0.196 | 0.31 | 0.197 | 0.217 | 0.2 | 0.218 | 0.219 | 0.194 | 0.206 | 0.201 | 0.194 | 0.202 | 0.193 | 0.192 | 0.224 | 0.202 | 0.207 | 0.214 | 0.222 | 0.221 | 0.181 | 0.2 | 0.203 | 0.199 | 0.212 | 0.202 | 0.193 | 0.186 | 0.205 | 0.185 | 0.191 | 0.19 | 0.301 | 0.313 | 0.194 | 0.204 | 0.195 | 0.196 | 0.198 | 0.189 | 0.222 | 0.207 | 0.22 | 0.209 | 0.201 | 0.22 | 0.227 | 0.214 | 0.219 | 0.237 | 0.218 | 0.23 | 0.222 | 0.255
0.083 | -9 IN | C | 0.21 | 0.201 | 0.2 | 0.223 | 0.198 | 0.219 | 0.214 | 0.222 | 0.211 | 0.21 | 0.23 | 0.216 | 0.32 | 0.225 | 0.215 | 0.197 | 0.199 | 0.196 | 0.216 | 0.206 | 0.218 | 0.212 | 0.2 | 0.212 | 0.2 | 0.203 | 0.194 | 0.203 | 0.193 | 0.196 | 0.204 | 0.208 | 0.191 | 0.194 | 0.178 | 0.18 | 0.205 | 0.2 | 0.191 | 0.212 | 0.199 | 0.191 | 0.186 | 0.207 | 0.187 | 0.192 | 0.187 | 0.3 | 0.318 | 0.196 | 0.19 | 0.194 | 0.194 | 0.193 | 0.192 | 0.216 | 0.208 | 0.222 | 0.211 | 0.248 | 0.218 | 0.226 | 0.214 | 0.223 | 0.227 | 0.244 | 0.232 | 0.222 | 0.227
|  | R | 0.21 | 0.2 | 0.207 | 0.221 | 0.221 | 0.221 | 0.216 | 0.222 | 0.209 | 0.214 | 0.229 | 0.214 | 0.323 | 0.223 | 0.206 | 0.198 | 0.323 | 0.2 | 0.214 | 0.199 | 0.191 | 0.232 | 0.206 | 0.202 | 0.206 | 0.204 | 0.198 | 0.191 | 0.192 | 0.213 | 0.204 | 0.193 | 0.19 | 0.218 | 0.179 | 0.192 | 0.205 | 0.199 | 0.192 | 0.209 | 0.199 | 0.193 | 0.187 | 0.206 | 0.183 | 0.192 | 0.187 | 0.31 | 0.313 | 0.202 | 0.183 | 0.193 | 0.19 | 0.194 | 0.191 | 0.219 | 0.212 | 0.224 | 0.209 | 0.244 | 0.217 | 0.233 | 0.214 | 0.222 | 0.221 | 0.203 | 0.222 | 0.221 | 0.252
A | POSITION 'C' | L |  | 0.197 | 0.201 | 0.207 | 0.21 | 0.223 | 0.213 |  |  |  | 0.206 | 0.226 | 0.332 | 0.222 | 0.214 | 0.214 |  |  | 0.212 | 0.215 | 0.214 | 0.215 | 0.219 | 0.213 | [7 empty] | 0.225 | 0.212 | 0.224 | 0.216 |  | 0.215 | 0.218 | 0.209 | 0.209 | 0.221 | 0.204 |  |  |  | 0.21 | 0.199 | 0.307 | 0.311 | 0.215 | 0.208 |  |  | 0.194 | 0.192 | 0.201 | 0.221 | 0.213 | 0.223 |  |  | 0.209 | 0.205 | 0.208 | 0.208 | 0.225 | 0.228
0.083 | OF THE | C |  | 0.194 | 0.194 | 0.204 | 0.205 | 0.218 | 0.213 |  |  |  | 0.216 | 0.215 | 0.301 | 0.222 | 0.216 | 0.204 |  |  | 0.202 | 0.223 | 0.215 | 0.214 | 0.207 | 0.213 | [7 empty] | 0.204 | 0.213 | 0.214 | 0.226 |  | 0.198 | 0.207 | 0.206 | 0.213 | 0.205 | 0.186 |  |  |  | 0.19 | 0.182 | 0.309 | 0.303 | 0.183 | 0.187 |  |  | 0.188 | 0.212 | 0.202 | 0.214 | 0.213 | 0.222 |  |  | 0.224 | 0.224 | 0.226 | 0.194 | 0.223 | 0.219
| SECONDARIES | R |  | 0.202 | 0.213 | 0.215 | 0.214 | 0.214 | 0.218 |  |  |  | 0.215 | 0.214 | 0.339 | 0.209 | 0.213 | 0.208 |  |  | 0.204 | 0.219 | 0.222 | 0.218 | 0.204 | 0.215 | [7 empty] | 0.216 | 0.222 | 0.201 | 0.189 |  | 0.201 | 0.224 | 0.211 | 0.214 | 0.194 | 0.19 |  |  |  | 0.183 | 0.173 | 0.296 | 0.285 | 0.195 | 0.201 |  |  | 0.173 | 0.178 | 0.219 | 0.213 | 0.209 | 0.211 |  |  | 0.224 | 0.215 | 0.228 | 0.239 | 0.229 | 0.214
A |  | L | 0.209 | 0.208 | 0.199 | 0.223 | 0.216 | 0.219 | 0.217 | 0.219 | 0.219 | 0.212 | 0.215 | 0.222 | 0.315 | 0.229 | 0.205 | 0.203 | 0.202 | 0.204 | 0.207 | 0.205 | 0.201 | 0.203 | 0.228 | 0.201 | 0.216 | 0.201 | 0.22 | 0.201 | 0.214 | 0.211 | 0.195 | 0.192 | 0.215 | 0.213 | 0.225 | 0.224 | 0.204 | 0.206 | 0.191 | 0.186 | 0.197 | 0.189 | 0.208 | 0.189 | 0.195 | 0.192 | 0.196 | 0.287 | 0.288 | 0.207 | 0.199 | 0.193 | 0.211 | 0.237 | 0.202 | 0.206 | 0.211 | 0.215 | 0.223 | 0.228 | 0.224 | 0.247 | 0.219 | 0.222 | 0.26 | 0.269 | 0.229 | 0.23 | 0.279
0.083 | -18 IN | C | 0.211 | 0.208 | 0.206 | 0.224 | 0.215 | 0.219 | 0.217 | 0.217 | 0.212 | 0.212 | 0.207 | 0.22 | 0.312 | 0.215 | 0.204 | 0.208 | 0.202 | 0.201 | 0.206 | 0.204 | 0.201 | 0.19 | 0.203 | 0.209 | 0.212 | 0.201 | 0.206 | 0.201 | 0.205 | 0.189 | 0.198 | 0.189 | 0.183 | 0.202 | 0.205 | 0.181 | 0.186 | 0.204 | 0.191 | 0.196 | 0.197 | 0.19 | 0.195 | 0.189 | 0.194 | 0.19 | 0.197 | 0.295 | 0.285 | 0.205 | 0.193 | 0.195 | 0.206 | 0.212 | 0.205 | 0.206 | 0.215 | 0.214 | 0.214 | 0.227 | 0.219 | 0.21 | 0.214 | 0.227 | 0.277 | 0.281 | 0.232 | 0.23 | 0.278
|  | R | 0.21 | 0.208 | 0.206 | 0.223 | 0.217 | 0.22 | 0.215 | 0.22 | 0.215 | 0.212 | 0.206 | 0.221 | 0.311 | 0.212 | 0.231 | 0.205 | 0.2 | 0.202 | 0.206 | 0.2 | 0.2 | 0.199 | 0.205 | 0.2 | 0.219 | 0.201 | 0.201 | 0.222 | 0.199 | 0.197 | 0.193 | 0.178 | 0.208 | 0.225 | 0.185 | 0.187 | 0.211 | 0.204 | 0.188 | 0.186 | 0.199 | 0.191 | 0.199 | 0.193 | 0.191 | 0.193 | 0.19 | 0.273 | 0.284 | 0.201 | 0.213 | 0.192 | 0.207 | 0.21 | 0.198 | 0.21 | 0.219 | 0.215 | 0.214 | 0.227 | 0.22 | 0.209 | 0.222 | 0.218 | 0.268 | 0.229 | 0.23 | 0.258 | 0.245
A |  | L | 0.223 | 0.222 | 0.22 | 0.221 | 0.224 | 0.222 | 0.241 | 0.218 | 0.245 | 0.238 | 0.22 | 0.238 | 0.331 | 0.216 | 0.203 | 0.211 | 0.21 | 0.214 | 0.213 | 0.208 | 0.216 | 0.211 | 0.202 | 0.205 | 0.215 | 0.214 | 0.202 | 0.193 | 0.204 | 0.202 | 0.21 | 0.195 | 0.2 | 0.204 | 0.196 | 0.19 | 0.195 | 0.202 | 0.191 | 0.206 | 0.208 | 0.182 | 0.191 | 0.202 | 0.199 | 0.193 | 0.204 | 0.305 | 0.267 | 0.211 | 0.203 | 0.217 | 0.204 | 0.211 | 0.226 | 0.213 | 0.211 | 0.227 | 0.232 | 0.225 | 0.235 | 0.21 | 0.21 | 0.225 | 0.258 | 0.252 | 0.236 | 0.215 | 0.286
0.083 | -27 IN | C | 0.214 | 0.229 | 0.22 | 0.229 | 0.221 | 0.222 | 0.223 | 0.224 | 0.244 | 0.233 | 0.218 | 0.24 | 0.33 | 0.214 | 0.202 | 0.211 | 0.21 | 0.212 | 0.21 | 0.209 | 0.214 | 0.207 | 0.205 | 0.201 | 0.213 | 0.203 | 0.204 | 0.194 | 0.203 | 0.199 | 0.207 | 0.197 | 0.199 | 0.204 | 0.2 | 0.189 | 0.197 | 0.192 | 0.192 | 0.199 | 0.202 | 0.183 | 0.191 | 0.201 | 0.211 | 0.192 | 0.31 | 0.31 | 0.293 | 0.214 | 0.205 | 0.214 | 0.201 | 0.211 | 0.212 | 0.212 | 0.211 | 0.233 | 0.233 | 0.218 | 0.23 | 0.212 | 0.21 | 0.255 | 0.273 | 0.263 | 0.235 | 0.209 | 0.287
|  | R | 0.221 | 0.214 | 0.256 | 0.23 | 0.221 | 0.225 | 0.226 | 0.218 | 0.24 | 0.231 | 0.234 | 0.202 | 0.327 | 0.215 | 0.201 | 0.209 | 0.215 | 0.21 | 0.212 | 0.21 | 0.216 | 0.213 | 0.201 | 0.205 | 0.215 | 0.201 | 0.204 | 0.204 | 0.201 | 0.195 | 0.209 | 0.193 | 0.2 | 0.216 | 0.204 | 0.189 | 0.195 | 0.205 | 0.19 | 0.198 | 0.201 | 0.184 | 0.191 | 0.201 | 0.21 | 0.192 | 0.214 | 0.289 | 0.269 | 0.217 | 0.203 | 0.215 | 0.202 | 0.209 | 0.225 | 0.226 | 0.211 | 0.221 | 0.221 | 0.221 | 0.235 | 0.211 | 0.214 | 0.25 | 0.281 | 0.264 | 0.236 | 0.214 | 0.286
A |  | L | 0.245 | 0.221 | 0.219 | 0.217 | 0.224 | 0.221 | 0.215 | 0.214 | 0.214 | 0.224 | 0.218 | 0.215 | 0.314 | 0.215 | 0.209 | 0.223 | 0.225 | 0.22 | 0.214 | 0.214 | 0.213 | 0.217 | 0.216 | 0.217 | 0.203 | 0.221 | 0.204 | 0.22 | 0.211 | 0.212 | 0.207 | 0.205 | 0.197 | 0.197 | 0.205 | 0.205 | 0.216 | 0.198 | 0.213 | 0.225 | 0.201 | 0.196 | 0.197 | 0.197 | 0.198 | 0.205 | 0.201 | 0.303 | 0.312 | 0.205 | 0.199 | 0.211 | 0.2 | 0.207 | 0.22 | 0.208 | 0.224 | 0.239 | 0.209 | 0.204 | 0.24 | 0.215 | 0.222 | 0.219 | 0.265 | 0.252 | 0.235 | 0.199 | 0.278
0.083 | -36 IN | C | 0.232 | 0.221 | 0.222 | 0.225 | 0.217 | 0.221 | 0.218 | 0.214 | 0.221 | 0.218 | 0.216 | 0.215 | 0.324 | 0.206 | 0.22 | 0.228 | 0.227 | 0.216 | 0.209 | 0.206 | 0.215 | 0.214 | 0.217 | 0.208 | 0.222 | 0.22 | 0.215 | 0.211 | 0.219 | 0.213 | 0.207 | 0.203 | 0.197 | 0.206 | 0.214 | 0.224 | 0.196 | 0.227 | 0.213 | 0.209 | 0.206 | 0.2 | 0.209 | 0.197 | 0.204 | 0.204 | 0.198 | 0.305 | 0.29 | 0.204 | 0.201 | 0.21 | 0.198 | 0.207 | 0.225 | 0.207 | 0.23 | 0.243 | 0.212 | 0.205 | 0.24 | 0.22 | 0.219 | 0.215 | 0.26 | 0.281 | 0.231 | 0.197 | 0.312
|  | R | 0.223 | 0.224 | 0.219 | 0.22 | 0.228 | 0.215 | 0.215 | 0.214 | 0.219 | 0.219 | 0.216 | 0.226 | 0.299 | 0.209 | 0.231 | 0.229 | 0.216 | 0.214 | 0.216 | 0.236 | 0.215 | 0.215 | 0.226 | 0.206 | 0.223 | 0.211 | 0.213 | 0.214 | 0.213 | 0.198 | 0.22 | 0.205 | 0.194 | 0.205 | 0.213 | 0.2 | 0.212 | 0.213 | 0.218 | 0.208 | 0.199 | 0.197 | 0.199 | 0.197 | 0.204 | 0.202 | 0.197 | 0.297 | 0.286 | 0.207 | 0.201 | 0.213 | 0.199 | 0.206 | 0.223 | 0.217 | 0.228 | 0.25 | 0.209 | 0.205 | 0.241 | 0.221 | 0.214 | 0.215 | 0.26 | 0.275 | 0.241 | 0.196 | 0.289
A |  | L | 0.226 | 0.214 | 0.203 | 0.209 | 0.229 | 0.205 | 0.215 | 0.214 | 0.208 | 0.217 | 0.212 | 0.212 | 0.32 | 0.206 | 0.209 | 0.208 | 0.205 | 0.212 | 0.229 | 0.219 | 0.219 | 0.217 | 0.234 | 0.202 | 0.228 | 0.21 | 0.213 | 0.2 | 0.192 | 0.21 | 0.207 | 0.205 | 0.21 | 0.215 | 0.201 | 0.21 | 0.217 | 0.215 | 0.217 | 0.229 | 0.216 | 0.209 | 0.222 | 0.196 | 0.221 | 0.216 | 0.237 | 0.288 | 0.289 | 0.2 | 0.207 | 0.204 | 0.207 | 0.214 | 0.225 | 0.231 | 0.219 | 0.217 | 0.21 | 0.209 | 0.223 | 0.229 | 0.216 | 0.226 | 0.273 | 0.275 | 0.267 | 0.228 | 0.251
0.083 | -45 IN | C | 0.213 | 0.213 | 0.201 | 0.227 | 0.206 | 0.218 | 0.216 | 0.21 | 0.205 | 0.237 | 0.204 | 0.215 | 0.327 | 0.242 | 0.214 | 0.196 | 0.202 | 0.207 | 0.217 | 0.2 | 0.215 | 0.212 | 0.237 | 0.201 | 0.221 | 0.212 | 0.205 | 0.204 | 0.221 | 0.218 | 0.204 | 0.204 | 0.209 | 0.214 | 0.204 | 0.208 | 0.215 | 0.214 | 0.219 | 0.22 | 0.214 | 0.203 | 0.215 | 0.196 | 0.222 | 0.216 | 0.204 | 0.283 | 0.267 | 0.198 | 0.205 | 0.204 | 0.204 | 0.222 | 0.218 | 0.197 | 0.217 | 0.213 | 0.21 | 0.217 | 0.211 | 0.209 | 0.223 | 0.224 | 0.264 | 0.273 | 0.228 | 0.229 | 0.22
|  | R | 0.213 | 0.203 | 0.23 | 0.227 | 0.207 | 0.218 | 0.215 | 0.205 | 0.237 | 0.207 | 0.212 | 0.206 | 0.322 | 0.208 | 0.214 | 0.211 | 0.226 | 0.205 | 0.215 | 0.199 | 0.213 | 0.211 | 0.234 | 0.2 | 0.221 | 0.204 | 0.203 | 0.193 | 0.207 | 0.208 | 0.225 | 0.21 | 0.215 | 0.206 | 0.21 | 0.217 | 0.217 | 0.221 | 0.224 | 0.215 | 0.211 | 0.208 | 0.215 | 0.205 | 0.214 | 0.213 | 0.202 | 0.298 | 0.274 | 0.229 | 0.207 | 0.204 | 0.202 | 0.224 | 0.231 | 0.252 | 0.216 | 0.214 | 0.206 | 0.224 | 0.232 | 0.213 | 0.223 | 0.224 | 0.259 | 0.274 | 0.23 | 0.252 | 0.263
A |  | L | 0.21 | 0.202 | 0.21 | 0.227 | 0.209 | 0.237 | 0.209 | 0.214 | 0.211 | 0.218 | 0.222 | 0.225 | 0.312 | 0.204 | 0.23 | 0.237 | 0.235 | 0.224 | 0.23 | 0.223 | 0.221 | 0.232 | 0.228 | 0.221 | 0.213 | 0.216 | 0.213 | 0.204 | 0.202 | 0.205 | 0.213 | 0.195 | 0.215 | 0.241 | 0.224 | 0.21 | 0.221 | 0.208 | 0.218 | 0.222 | 0.216 | 0.216 | 0.232 | 0.215 | 0.212 | 0.214 | 0.219 | 0.309 | 0.348 | 0.226 | 0.216 | 0.218 | 0.219 | 0.211 | 0.22 | 0.219 | 0.227 | 0.236 | 0.212 | 0.234 | 0.247 | 0.223 | 0.229 | 0.253 | 0.248 | 0.262 | 0.22 | 0.225 | 0.267
0.083 | -54 IN | C | 0.21 | 0.2 | 0.207 | 0.199 | 0.243 | 0.215 | 0.207 | 0.219 | 0.203 | 0.226 | 0.22 | 0.222 | 0.31 | 0.204 | 0.227 | 0.211 | 0.228 | 0.221 | 0.236 | 0.221 | 0.222 | 0.239 | 0.229 | 0.216 | 0.216 | 0.216 | 0.21 | 0.211 | 0.2 | 0.203 | 0.215 | 0.198 | 0.219 | 0.24 | 0.212 | 0.208 | 0.221 | 0.207 | 0.218 | 0.221 | 0.216 | 0.233 | 0.218 | 0.212 | 0.23 | 0.217 | 0.214 | 0.307 | 0.319 | 0.233 | 0.217 | 0.217 | 0.221 | 0.21 | 0.219 | 0.216 | 0.227 | 0.236 | 0.227 | 0.232 | 0.231 | 0.225 | 0.228 | 0.253 | 0.271 | 0.283 | 0.222 | 0.219 | 0.289
|  | R | 0.211 | 0.203 | 0.205 | 0.2 | 0.207 | 0.218 | 0.207 | 0.214 | 0.202 | 0.216 | 0.22 | 0.218 | 0.308 | 0.206 | 0.224 | 0.208 | 0.225 | 0.219 | 0.234 | 0.219 | 0.222 | 0.239 | 0.226 | 0.216 | 0.216 | 0.219 | 0.215 | 0.204 | 0.2 | 0.213 | 0.198 | 0.198 | 0.214 | 0.225 | 0.21 | 0.225 | 0.217 | 0.209 | 0.219 | 0.221 | 0.217 | 0.201 | 0.216 | 0.21 | 0.232 | 0.213 | 0.267 | 0.322 | 0.273 | 0.218 | 0.201 | 0.221 | 0.211 | 0.22 | 0.219 | 0.233 | 0.223 | 0.236 | 0.218 | 0.234 | 0.234 | 0.226 | 0.227 | 0.253 | 0.271 | 0.283 | 0.222 | 0.218 | 0.277
A | POSITION 'A' | L |  |  | 0.204 | 0.224 |  | 0.216 | 0.211 |  | 0.208 | 0.212 |  | 0.224 | 0.316 |  | 0.212 | 0.211 |  | 0.212 | 0.218 |  | 0.217 | 0.216 |  | 0.216 | 0.213 |  | 0.21 | 0.208 |  | 0.208 | 0.214 |  | 0.212 | 0.215 |  | 0.212 | 0.221 |  | 0.215 | 0.214 |  | 0.212 | 0.208 |  | 0.211 | 0.216 |  | 0.316 | 0.308 |  | 0.216 | 0.208 |  | 0.206 | 0.213 |  | 0.216 | 0.217 |  | 0.239 | 0.227 |  | 0.235 | 0.232 |  | 0.271 | 0.219
0.083 | OF THE | C |  |  | 0.213 | 0.22 |  | 0.209 | 0.215 |  | 0.208 | 0.214 |  | 0.218 | 0.314 |  | 0.218 | 0.214 |  | 0.215 | 0.223 |  | 0.218 | 0.225 |  | 0.214 | 0.214 |  | 0.205 | 0.203 |  | 0.205 | 0.226 |  | 0.218 | 0.226 |  | 0.204 | 0.214 |  | 0.207 | 0.222 |  | 0.208 | 0.213 |  | 0.218 | 0.213 |  | 0.302 | 0.313 |  | 0.216 | 0.216 |  | 0.207 | 0.227 |  | 0.222 | 0.222 |  | 0.229 | 0.223 |  | 0.226 | 0.233 |  | 0.274 | 0.226
| PRIMARIES | R |  |  | 0.213 | 0.223 |  | 0.212 | 0.215 |  | 0.211 | 0.214 |  | 0.216 | 0.311 |  | 0.221 | 0.215 |  | 0.219 | 0.225 |  | 0.216 | 0.215 |  | 0.212 | 0.209 |  | 0.203 | 0.204 |  | 0.212 | 0.221 |  | 0.216 | 0.224 |  | 0.204 | 0.214 |  | 0.207 | 0.22 |  | 0.205 | 0.224 |  | 0.217 | 0.212 |  | 0.314 | 0.322 |  | 0.213 | 0.218 |  | 0.212 | 0.21 |  | 0.222 | 0.227 |  | 0.226 | 0.215 |  | 0.238 | 0.227 |  | 0.277 | 0.231
A | POSITION 'B' | L |  |  | 0.217 | 0.228 |  | 0.212 | 0.219 |  | 0.208 | 0.218 |  | 0.205 | 0.319 |  | 0.22 | 0.207 |  | 0.213 | 0.216 |  | 0.213 | 0.208 |  | 0.21 | 0.212 |  | 0.198 | 0.204 |  | 0.206 | 0.219 |  | 0.21 | 0.206 |  | 0.212 | 0.221 |  | 0.214 | 0.213 |  | 0.202 | 0.216 |  | 0.218 | 0.214 |  | 0.309 | 0.313 |  | 0.223 | 0.214 |  | 0.207 | 0.23 |  | 0.221 | 0.218 |  | 0.247 | 0.218 |  | 0.225 | 0.217 |  | 0.271 | 0.219
0.083 | OF THE | C |  |  | 0.193 | 0.219 |  | 0.211 | 0.208 |  | 0.205 | 0.21 |  | 0.207 | 0.305 |  | 0.212 | 0.192 |  | 0.207 | 0.225 |  | 0.223 | 0.201 |  | 0.206 | 0.215 |  | 0.2 | 0.193 |  | 0.198 | 0.21 |  | 0.213 | 0.21 |  | 0.212 | 0.216 |  | 0.212 | 0.235 |  | 0.217 | 0.212 |  | 0.206 | 0.215 |  | 0.306 | 0.31 |  | 0.207 | 0.23 |  | 0.207 | 0.223 |  | 0.218 | 0.219 |  | 0.216 | 0.218 |  | 0.213 | 0.242 |  | 0.254 | 0.234
| PRIMARIES | R |  |  | 0.226 | 0.214 |  | 0.212 | 0.208 |  | 0.211 | 0.211 |  | 0.206 | 0.322 |  | 0.216 | 0.203 |  | 0.203 | 0.225 |  | 0.213 | 0.208 |  | 0.198 | 0.204 |  | 0.199 | 0.196 |  | 0.209 | 0.207 |  | 0.206 | 0.209 |  | 0.209 | 0.211 |  | 0.198 | 0.218 |  | 0.195 | 0.209 |  | 0.203 | 0.209 |  | 0.306 | 0.3 |  | 0.197 | 0.212 |  | 0.2 | 0.216 |  | 0.207 | 0.217 |  | 0.228 | 0.232 |  | 0.23 | 0.207 |  | 0.269 | 0.21
A | POSITION 'C' | L |  |  | 0.212 | 0.222 |  | 0.208 | 0.213 |  | 0.21 | 0.213 |  | 0.214 | 0.313 |  | 0.207 | 0.217 |  | 0.208 | 0.22 |  | 0.216 | 0.212 |  | 0.197 | 0.213 |  | 0.206 | 0.211 |  | 0.226 | 0.227 |  | 0.209 | 0.226 |  | 0.201 | 0.22 |  | 0.209 | 0.228 |  | 0.222 | 0.206 |  | 0.21 | 0.213 |  | 0.323 | 0.311 |  | 0.222 | 0.212 |  | 0.21 | 0.235 |  | 0.246 | 0.243 |  | 0.223 | 0.225 |  | 0.226 | 0.214 |  | 0.252 | 0.227
0.083 | OF THE | C |  |  | 0.195 | 0.205 |  | 0.199 | 0.213 |  | 0.2 | 0.21 |  | 0.218 | 0.315 |  | 0.207 | 0.217 |  | 0.21 | 0.216 |  | 0.22 | 0.209 |  | 0.204 | 0.211 |  | 0.207 | 0.211 |  | 0.211 | 0.218 |  | 0.221 | 0.222 |  | 0.209 | 0.229 |  | 0.212 | 0.22 |  | 0.221 | 0.208 |  | 0.211 | 0.218 |  | 0.312 | 0.313 |  | 0.209 | 0.225 |  | 0.214 | 0.219 |  | 0.227 | 0.241 |  | 0.228 | 0.229 |  | 0.229 | 0.212 |  | 0.244 | 0.221
| PRIMARIES | R |  |  | 0.216 | 0.194 |  | 0.203 | 0.218 |  | 0.215 | 0.21 |  | 0.21 | 0.321 |  | 0.213 | 0.21 |  | 0.204 | 0.225 |  | 0.222 | 0.205 |  | 0.21 | 0.204 |  | 0.216 | 0.218 |  | 0.223 | 0.213 |  | 0.228 | 0.218 |  | 0.214 | 0.208 |  | 0.223 | 0.218 |  | 0.218 | 0.213 |  | 0.222 | 0.218 |  | 0.315 | 0.305 |  | 0.205 | 0.214 |  | 0.212 | 0.222 |  | 0.227 | 0.245 |  | 0.227 | 0.222 |  | 0.229 | 0.208 |  | 0.266 | 0.216
A |  | L | 0.216 | 0.228 | 0.206 | 0.206 | 0.207 | 0.229 | 0.21 | 0.214 | 0.217 | 0.223 | 0.232 | 0.213 | 0.315 | 0.205 | 0.201 | 0.222 | 0.21 | 0.218 | 0.228 | 0.221 | 0.216 | 0.227 | 0.218 | 0.218 | 0.225 | 0.203 | 0.203 | 0.204 | 0.208 | 0.196 | 0.241 | 0.216 | 0.222 | 0.206 | 0.214 | 0.222 | 0.217 | 0.204 | 0.207 | 0.206 | 0.201 | 0.222 | 0.217 | 0.205 | 0.219 | 0.214 | 0.216 | 0.31 | 0.322 | 0.225 | 0.211 | 0.217 | 0.208 | 0.215 | 0.225 | 0.217 | 0.247 | 0.219 | 0.231 | 0.242 | 0.242 | 0.215 | 0.215 | 0.234 | 0.207 | 0.22 | 0.227 | 0.228 | 0.275
0.083 | -63 IN | C | 0.222 | 0.227 | 0.206 | 0.205 | 0.216 | 0.202 | 0.203 | 0.216 | 0.222 | 0.221 | 0.223 | 0.209 | 0.318 | 0.201 | 0.208 | 0.221 | 0.206 | 0.233 | 0.229 | 0.216 | 0.215 | 0.219 | 0.222 | 0.219 | 0.208 | 0.202 | 0.2 | 0.206 | 0.202 | 0.216 | 0.244 | 0.213 | 0.22 | 0.206 | 0.219 | 0.223 | 0.228 | 0.211 | 0.214 | 0.201 | 0.223 | 0.223 | 0.216 | 0.207 | 0.214 | 0.213 | 0.214 | 0.317 | 0.316 | 0.206 | 0.214 | 0.229 | 0.207 | 0.216 | 0.223 | 0.217 | 0.247 | 0.22 | 0.231 | 0.234 | 0.247 | 0.215 | 0.225 | 0.209 | 0.27 | 0.208 | 0.23 | 0.22 | 0.291
|  | R | 0.229 | 0.229 | 0.208 | 0.205 | 0.211 | 0.209 | 0.204 | 0.211 | 0.221 | 0.22 | 0.216 | 0.205 | 0.301 | 0.198 | 0.218 | 0.221 | 0.204 | 0.231 | 0.216 | 0.216 | 0.213 | 0.221 | 0.215 | 0.213 | 0.209 | 0.221 | 0.206 | 0.203 | 0.237 | 0.208 | 0.23 | 0.217 | 0.222 | 0.206 | 0.221 | 0.234 | 0.204 | 0.202 | 0.206 | 0.201 | 0.223 | 0.224 | 0.207 | 0.214 | 0.219 | 0.212 | 0.231 | 0.314 | 0.316 | 0.225 | 0.219 | 0.231 | 0.216 | 0.216 | 0.214 | 0.246 | 0.219 | 0.231 | 0.242 | 0.228 | 0.246 | 0.215 | 0.216 | 0.207 | 0.205 | 0.224 | 0.226 | 0.227 | 0.286
A |  | L | 0.217 | 0.226 | 0.237 | 0.217 | 0.208 | 0.206 | 0.232 | 0.215 | 0.219 | 0.208 | 0.213 | 0.217 | 0.201 | 0.228 | 0.203 | 0.206 | 0.204 | 0.206 | 0.214 | 0.218 | 0.211 | 0.235 | 0.232 | 0.208 | 0.221 | 0.234 | 0.22 | 0.216 | 0.22 | 0.231 | 0.21 | 0.207 | 0.22 | 0.231 | 0.223 | 0.218 | 0.217 | 0.2 | 0.206 | 0.206 | 0.206 | 0.223 | 0.2 | 0.223 | 0.21 | 0.221 | 0.221 | 0.319 | 0.319 | 0.205 | 0.231 | 0.217 | 0.202 | 0.223 | 0.222 | 0.21 | 0.237 | 0.233 | 0.215 | 0.219 | 0.216 | 0.209 | 0.238 | 0.223 | 0.258 | 0.255 | 0.221 | 0.248 | 0.281
0.083 | -72 IN | C | 0.226 | 0.224 | 0.219 | 0.204 | 0.217 | 0.207 | 0.213 | 0.207 | 0.225 | 0.208 | 0.212 | 0.226 | 0.223 | 0.212 | 0.219 | 0.207 | 0.222 | 0.207 | 0.219 | 0.22 | 0.229 | 0.225 | 0.239 | 0.205 | 0.211 | 0.219 | 0.212 | 0.215 | 0.213 | 0.212 | 0.215 | 0.213 | 0.209 | 0.23 | 0.2 | 0.204 | 0.199 | 0.192 | 0.208 | 0.204 | 0.206 | 0.22 | 0.203 | 0.21 | 0.199 | 0.211 | 0.202 | 0.314 | 0.286 | 0.22 | 0.217 | 0.198 | 0.2 | 0.219 | 0.216 | 0.221 | 0.208 | 0.221 | 0.2 | 0.222 | 0.23 | 0.197 | 0.215 | 0.209 | 0.263 | 0.254 | 0.218 | 0.282 | 0.261
|  | R | 0.206 | 0.199 | 0.226 | 0.222 | 0.215 | 0.23 | 0.224 | 0.223 | 0.213 | 0.209 | 0.208 | 0.211 | 0.218 | 0.217 | 0.232 | 0.226 | 0.207 | 0.207 | 0.208 | 0.209 | 0.21 | 0.225 | 0.226 | 0.205 | 0.219 | 0.235 | 0.195 | 0.201 | 0.208 | 0.204 | 0.218 | 0.207 | 0.224 | 0.213 | 0.211 | 0.226 | 0.205 | 0.22 | 0.208 | 0.206 | 0.222 | 0.196 | 0.196 | 0.203 | 0.207 | 0.216 | 0.216 | 0.226 | 0.209 | 0.202 | 0.216 | 0.208 | 0.218 | 0.217 | 0.219 | 0.216 | 0.223 | 0.226 | 0.215 | 0.225 | 0.211 | 0.197 | 0.227 | 0.206 | 0.272 | 0.26 | 0.277 | 0.249 | 0.279
A |  | L | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | 0.206 | 0.321 | 0.216 | 0.209 | 0.21 | 0.211 | 0.22 | 0.212 | 0.212 | 0.222 | 0.214 | 0.213 | 0.218 | 0.216 | 0.232 | 0.204 | 0.221 | 0.207 | 0.218 | 0.215 | 0.225 | 0.207 | 0.209 | 0.218 | 0.216 | 0.224 | 0.209 | 0.219 | 0.211 | 0.209 | 0.221 | 0.208 | 0.225 | 0.212 | 0.226 | 0.238 | 0.226 | 0.331 | 0.211 | 0.303 | 0.223 | 0.215 | 0.228 | 0.22 | 0.237 | 0.21 | 0.227 | 0.235 | 0.212 | 0.229 | 0.218 | 0.234 | 0.229 | 0.229 | 0.26 | 0.21 | 0.246 | 0.286
0.083 | -81 IN | C | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | 0.205 | 0.326 | 0.225 | 0.211 | 0.221 | 0.216 | 0.205 | 0.223 | 0.21 | 0.221 | 0.21 | 0.218 | 0.213 | 0.221 | 0.221 | 0.214 | 0.222 | 0.219 | 0.215 | 0.218 | 0.211 | 0.206 | 0.211 | 0.21 | 0.218 | 0.206 | 0.213 | 0.216 | 0.209 | 0.207 | 0.218 | 0.196 | 0.214 | 0.222 | 0.211 | 0.233 | 0.222 | 0.307 | 0.212 | 0.224 | 0.23 | 0.219 | 0.216 | 0.228 | 0.234 | 0.214 | 0.213 | 0.206 | 0.213 | 0.247 | 0.214 | 0.24 | 0.222 | 0.231 | 0.258 | 0.223 | 0.211 | 0.264
|  | R | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | 0.209 | 0.31 | 0.229 | 0.199 | 0.212 | 0.213 | 0.22 | 0.215 | 0.218 | 0.219 | 0.233 | 0.212 | 0.201 | 0.223 | 0.217 | 0.202 | 0.225 | 0.208 | 0.222 | 0.218 | 0.222 | 0.21 | 0.221 | 0.22 | 0.208 | 0.209 | 0.219 | 0.21 | 0.215 | 0.206 | 0.204 | 0.197 | 0.216 | 0.218 | 0.225 | 0.22 | 0.314 | 0.301 | 0.22 | 0.228 | 0.235 | 0.222 | 0.221 | 0.236 | 0.225 | 0.202 | 0.209 | 0.231 | 0.232 | 0.235 | 0.208 | 0.227 | 0.214 | 0.249 | 0.26 | 0.212 | 0.239 | 0.253
A |  | L | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | 0.226 | 0.228 | 0.229 | 0.226 | 0.224 | 0.221 | 0.224 | 0.227 | 0.21 | 0.22 | 0.206 | 0.213 | 0.216 | 0.307 | 0.297 | 0.218 | 0.227 | 0.23 | 0.228 | 0.229 | 0.232 | 0.222 | 0.235 | 0.219 | 0.223 | 0.226 | 0.235 | 0.22 | 0.221 | 0.22 | 0.262 | 0.229 | 0.23 | 0.236 | 0.259
0.083 | -90 IN | C | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | 0.217 | 0.199 | 0.21 | 0.22 | 0.213 | 0.224 | 0.209 | 0.211 | 0.196 | 0.212 | 0.199 | 0.212 | 0.22 | 0.3 | 0.3 | 0.207 | 0.225 | 0.222 | 0.214 | 0.205 | 0.211 | 0.227 | 0.227 | 0.2 | 0.217 | 0.218 | 0.218 | 0.219 | 0.218 | 0.219 | 0.232 | 0.247 | 0.216 | 0.226 | 0.253
|  | R | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | 0.217 | 0.209 | 0.215 | 0.215 | 0.219 | 0.215 | 0.216 | 0.212 | 0.211 | 0.225 | 0.218 | 0.225 | 0.218 | 0.315 | 0.301 | 0.215 | 0.217 | 0.24 | 0.221 | 0.214 | 0.215 | 0.239 | 0.226 | 0.234 | 0.204 | 0.224 | 0.217 | 0.229 | 0.222 | 0.222 | 0.228 | 0.263 | 0.242 | 0.229 | 0.256
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MIN
A | 0.001-0.083 | 0.131-0.140 | 10: OUTSIDE DIAMETER:; 23: 3; 30: INSPECTION RESULTS; 67: APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com |  |  | EXAMPLE PAPER
LEGEND | 0.084-0.100 | 0.141-0.150 | 10: TUBE MATERIAL:; 23: SA-210A1; 35: MAX. THICKNESS |  |  | RIVERDALE MILL
| 0.101-0.110 | 0.151-0.160 | 10: NOMINAL WALL:; 23: 0.203; 35: AVG. THICKNESS |  |  | TUBE WALL THICKNESS SURVEY
| 0.111-0.120 | 0.161-0.170 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS |  |  | NO. 1 RECOVERY BOILER
| 0.121-0.130 | 0.171-0.999 | 10: MILL FLAG:; 23: 0.1; 35: STD DEV.; 46: Job # H449364 P.O. # 0018342455 W.O. # N/A Date: 5/05/2025 |  |  | 05 RIGHT WALL W/ PORTS
THICKNESS
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Corrosion
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. CORROSION RATE MEASUREMENTS ARE IN MILS. | [72 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MAX
A |  | L | ND | 0.351 | 0.019 | 0.79 | 4.08 | ND | 1.51 | 3.46 | 2.69 | 1.02 | 2.2 | ND | 1.41 | 3.46 | 3.94 | 3.59 | 2.67 | 2.26 | 3.4 | 4.13 | 1.63 | 1.38 | 3.36 | 1.65 | 4.63 | 4.96 | 4.05 | 4.36 | 4.9 | ND | 3.63 | 3.22 | 2.94 | 1.96 | 3.05 | ND | 2.88 | 2.03 | 3.06 | 3.3 | 1.53 | 2.86 | 1.06 | 1.54 | 1.85 | 2.44 | 2.38 | 0.768 | 2.86 | 2.75 | 4.36 | 1.22 | 2.28 | 2.77 | 2.72 | 3.11 | 0.073 | 1.35 | 7.4 | 4.45 | 2.03 | 1.57 | 3.81 | ND | 1.73 | ND | ND | 3.55 | ND
| +16 FT 6 IN | C | ND | 2.87 | 1.64 | 0.291 | ND | ND | 0.472 | 0.472 | 0.953 | ND | ND | 1.61 | 1.56 | 3.21 | 1.98 | 2.18 | 1.54 | 1.99 | 2.77 | 3.61 | 1.55 | 0.29 | 1.94 | 2.13 | 1.5 | 3.14 | 2.43 | 2.52 | 5.49 | ND | 5.71 | 3.54 | 3.58 | 2.54 | 2.47 | ND | 1.92 | 0.599 | 2.49 | 3.11 | 3.6 | 2.01 | ND | 2.77 | 0.557 | 1.31 | 0.635 | 0.515 | 3.54 | 2.69 | 3.3 | 0.571 | 3.4 | 1.97 | 1.93 | 0.504 | ND | 1.47 | 4.45 | ND | 2.73 | 1.81 | 2.78 | 1.41 | ND | 1.83 | 2.22 | 3.89 | ND
|  | R | ND | 1.04 | 0.117 | 1.54 | 1.02 | ND | 1.19 | 1.92 | 1.24 | 0.446 | 0.589 | 2.59 | 0.638 | 4.22 | 4.23 | 3.35 | 1.04 | 0.583 | 2.4 | 2.04 | 1.89 | 2.71 | ND | 1.84 | 3.21 | 2.81 | 3.64 | 4.18 | 3.66 | 1.43 | 4.73 | 1.96 | 4.03 | 2.6 | 2.71 | 2.93 | 0.032 | 0.07 | 2.63 | 2.71 | 0.582 | 1.71 | 0.738 | 2.55 | 1.99 | 0.876 | 0.126 | 3.72 | 2.3 | 0.221 | 4.09 | 1.28 | 0.903 | 1.82 | 1.35 | ND | 1.26 | 2.14 | 4.52 | 0.884 | 3.43 | ND | 2.81 | 1.97 | 1.03 | 1.28 | 2.11 | 5.1 | ND
A |  | L | ND | ND | 2.03 | ND | 0.633 | ND | ND | 1.94 | ND | 1.25 | 1.5 | 2.73 | 2.51 | 1.9 | 3.55 | 3.86 | 2.79 | 1.32 | 0.239 | 2.56 | 2.99 | ND | 0.774 | 3.39 | 2.94 | 8.47 | 2.54 | 1.52 | 2.73 | 2.61 | 5.58 | 4.29 | ND | 1.1 | 0.846 | 6.99 | 1.01 | ND | 1.64 | 5.93 | 2.83 | 6.37 | 2.21 | 5.12 | 2.09 | 2.35 | 8.25 | 4.61 | 1.56 | 4.52 | 3.12 | 3.77 | 4.05 | 3.26 | 3.3 | 4.35 | ND | 7.11 | 2.11 | 1.28 | 0.775 | 2.16 | 2.37 | 1.86 | ND | 0.278 | 2.29 | 3.07 | ND
| +15 FT | C | ND | ND | 3.22 | ND | 0.279 | ND | ND | 0.983 | ND | ND | 1.29 | 0.455 | 1.74 | 0.345 | ND | 2.12 | 2.19 | 4.25 | 1.87 | 4.05 | 0.941 | ND | 5.53 | 2.87 | 1.03 | 5.27 | 0.838 | 1.37 | ND | 1.87 | 3.03 | 1.81 | ND | ND | 0.928 | ND | 0.453 | 3.69 | 3.76 | 2.12 | 0.602 | 0.666 | 0.931 | 1.44 | 3.23 | 2.27 | 0.855 | 2.21 | 1.61 | 2.08 | ND | 4.38 | 3.48 | 0.766 | 0.439 | 0.615 | ND | 2.25 | 0.273 | 2.76 | 2.93 | 2.56 | 0.426 | 2 | 0.325 | 0.421 | 3.26 | 7.72 | ND
|  | R | ND | ND | 0.93 | ND | 1.85 | 0.633 | 0.532 | 1.6 | ND | ND | ND | 0.909 | 0.371 | 0.185 | 1.17 | 1.38 | 1.27 | 2.45 | 1.44 | 2.16 | 0.763 | ND | 0.517 | 3.22 | 0.297 | 4.25 | 1.6 | 2.87 | 1.52 | 3.72 | 3.04 | 1.45 | ND | ND | 0.634 | 1.27 | 0.161 | 1.3 | 4.11 | 2.54 | 2.01 | 2.46 | 3.7 | 1.89 | 3.23 | 4.08 | 1.55 | 4.38 | 3.84 | 2.62 | 0.605 | 4.89 | 0.716 | 2.65 | 3.69 | 1.36 | ND | 1.35 | 0.779 | 2.38 | 2.29 | 3.18 | 1.14 | 1.36 | 5.19 | 1.99 | 4.75 | 6.34 | ND
A |  | L | ND | 0.777 | 3.41 | 1.98 | ND | ND | ND | 0.217 | ND | 3.03 | 1.21 | 0.951 | ND | 3.22 | 0.033 | 0.428 | 0.911 | 1.14 | ND | 0.225 | 1.88 | 0.6 | 1.8 | ND | ND | 0.967 | 1.1 | 3.15 | 1.72 | 6.11 | 0.918 | 4.58 | 13.1 | 1.67 | 4.53 | 1.65 | 1.78 | 3.45 | 0.358 | 0.253 | ND | 0.016 | 7.17 | ND | ND | ND | ND | 2.72 | 1.73 | 1.28 | 1.88 | 2.02 | 4.78 | 7.02 | 3.88 | 5.6 | 3.56 | 1.42 | 0.885 | ND | 1.36 | 0.934 | 4.71 | 1.25 | 2.22 | 0.598 | 6.13 | 1.39 | ND
| +13 FT 6 IN | C | ND | 2.1 | ND | 1.81 | ND | ND | ND | 0.12 | ND | 1.1 | 2.4 | ND | ND | 2.07 | ND | 1.98 | ND | 0.49 | ND | 0.118 | 0.186 | 1.84 | 1.33 | 1.16 | 0.192 | 3.74 | 0.897 | 4.93 | 2.3 | 2.52 | 1.03 | 0.526 | 2.74 | 0.381 | 1.83 | 1.19 | ND | 1.95 | 2.29 | 3.11 | 3.83 | 0.291 | 2.65 | 5.31 | 0.797 | 4.01 | 1.23 | 1.16 | 2.82 | 3.04 | 2.01 | 1.74 | 4.14 | 5.49 | 2.17 | 2.58 | 6.15 | ND | ND | ND | 5.41 | 0.518 | 1.66 | 2.33 | 2.7 | ND | 0.447 | 2.7 | ND
|  | R | ND | 3.42 | 0.68 | ND | ND | ND | 0.432 | ND | ND | ND | 0.07 | ND | 1.62 | 1.01 | ND | 0.911 | 1.27 | 0.522 | ND | ND | 0.276 | ND | ND | 1.91 | ND | 0.179 | 0.066 | 2.12 | 3.9 | 2.04 | 2.06 | 2.92 | 3.87 | 0.197 | 2.73 | 1.72 | 0.91 | 3.4 | 3.09 | 5.98 | ND | 3.28 | 3.11 | ND | 1.31 | 3.21 | 2.56 | 0.675 | 1.4 | 5.99 | 2.97 | 1.75 | 6.08 | 4.96 | 0.681 | 5.39 | 2.31 | 0.972 | ND | 2.49 | 0.922 | 2.24 | 2.33 | 3.65 | 2.65 | ND | 1.46 | ND | ND
A |  | L | ND | 0.394 | ND | ND | ND | 0.139 | ND | ND | 0.574 | ND | ND | 1.59 | ND | 7.04 | 0.406 | 2.13 | 1.5 | 1.27 | ND | 1.46 | ND | 5.4 | ND | 1.39 | 0.826 | 3.93 | 3.03 | ND | 0.508 | 2.52 | 3.19 | 1 | 3.56 | 1.03 | 0.754 | 0.468 | 3.65 | 2.47 | 4.38 | 0.855 | 3.28 | ND | 4.02 | 6.48 | ND | 3.17 | 6 | 4.98 | 0.681 | 0.386 | 2.15 | 7.94 | 4.18 | ND | 3.63 | ND | 1.93 | ND | 3.14 | ND | 0.848 | ND | 0.257 | ND | ND | ND | 1.6 | ND | 3.35
| +12 FT | C | ND | 0.523 | ND | 2.43 | 0.123 | ND | ND | 0.635 | 0.028 | ND | ND | 2.5 | ND | 7.43 | 0.4 | ND | 1.06 | 0.504 | 2.32 | 2.45 | 0.375 | 2.94 | 1.23 | ND | 1.78 | 3.85 | 1.12 | 2.43 | ND | 3.33 | 3.83 | 1.9 | 0.855 | 0.896 | 0.403 | 1.64 | 1.29 | 0.863 | 1.33 | 2.03 | 5.3 | 4.95 | 2.75 | 4.26 | 6.12 | 0.922 | 3.6 | 3.21 | 2.82 | ND | ND | 4.88 | 1.05 | 3.07 | 2.42 | 2.05 | 3.15 | 0.2 | ND | ND | ND | ND | 1.81 | 1.07 | 0.503 | 0.881 | 0.898 | 0.832 | 6.65
|  | R | 0.948 | 0.113 | ND | ND | 2.68 | 1.05 | ND | 0.495 | 1.59 | ND | 1.34 | 1.65 | ND | 8.08 | ND | ND | ND | ND | 4.04 | 0.86 | 1.45 | 4.32 | 1.37 | 1.44 | 4.21 | 2.76 | 4.01 | 0.147 | 0.573 | 1.85 | 0.84 | 0.761 | 1.97 | 0.547 | ND | 3.95 | 1.13 | 1.69 | 0.682 | ND | ND | 1.69 | 2.6 | 3.29 | 4.58 | ND | 2.89 | 2.54 | ND | 0.108 | 3.54 | 5.57 | ND | 1.71 | 4.69 | 1.6 | ND | 0.555 | 1.02 | ND | 0.261 | ND | ND | ND | 1.35 | 1.01 | 0.553 | 0.671 | 6.72
A | POSITION 'A' | L | ND | 2.78 | 1.15 | 0.568 | 3.09 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.94 | 1.18 | 2.47 | 0.672 | ND
| OF THE | C | ND | 1.99 | 1.03 | 3.35 | 2.54 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.5 | 2.34 | 1.94 | 2.34 | ND
| OB PORTS | R | ND | 2.35 | 0.296 | 1.65 | 1.83 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.24 | 2.51 | 2.74 | 0.221 | ND
A | POSITION 'B' | L | ND | 2.91 | 2.79 | 2.62 | 0.11 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.17 | 0.942 | 2.59 | 1.19 | ND
| OF THE | C | ND | 3.29 | 2.11 | 2.8 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.61 | 1.61 | 2.74 | 2.98 | ND
| OB PORTS | R | ND | 2.24 | ND | 0.651 | 0.762 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.53 | 1.72 | 4.02 | 1.56 | ND
A | POSITION 'C' | L | ND | 2.89 | 2.02 | 4.48 | 1.27 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.45 | 2.76 | 1.82 | 2.18 | ND
| OF THE | C | ND | 2.83 | 2.11 | 1.74 | 0.419 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.04 | 2.9 | 2.31 | 0.727 | ND
| OB PORTS | R | ND | 3.59 | 0.748 | 1.26 | 3.19 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.11 | 1.38 | 2.07 | ND | ND
A |  | L | ND | ND | 2.42 | ND | ND | 0.514 | ND | 1.75 | 1.83 | 2.13 | 1.5 | 0.029 | ND | 22.6 | ND | 1.64 | 2.9 | 1.84 | 2 | 3.55 | 3.2 | 2.46 | 8.66 | 5.18 | ND | ND | ND | 4.25 | 7.09 | 4.47 | 2.23 | 2.62 | 3.66 | 0.246 | ND | ND | ND | 0.836 | ND | ND | 8 | 0.602 | 4.87 | ND | ND | 2.13 | 6.73 | ND | ND | 2.52 | ND | ND | 8.88 | ND | 2.4 | 1.97 | ND | ND | 4.41 | 0.455 | ND | 1.92 | 0.247 | ND | ND | 1.24 | 3.4 | 2.93 | ND
| +10 FT 6 IN | C | ND | 1.06 | 3.23 | ND | 0.657 | ND | ND | 2.51 | 1.12 | 1.69 | ND | 0.143 | 2.15 | 1.69 | ND | 1.41 | 1.85 | ND | 2.77 | 3.73 | 2.57 | 1.09 | 3.34 | 4.14 | 4.84 | 1.65 | 0.538 | 2.4 | 0.589 | 5.67 | 3.59 | 1.49 | 1.72 | 1.15 | 1.65 | ND | 1.13 | 1.7 | 5.69 | 4.96 | 4.65 | 3.5 | 2.19 | ND | 3.96 | 1.33 | 5.56 | 1.83 | 3.21 | 1.57 | 1.7 | 2.4 | 1.66 | 2.09 | ND | ND | ND | ND | 1.3 | 1.23 | 0.102 | 0.334 | 0.27 | 0.799 | ND | ND | 3.4 | 1.51 | 1.65
|  | R | ND | 0.039 | 1.76 | 0.673 | 1.05 | ND | 0.634 | 0.548 | 2.17 | 1.89 | ND | 1.58 | 3.6 | ND | ND | 1.33 | 3.45 | 1.43 | 2.4 | ND | 2.24 | 1.16 | 3.54 | 0.759 | 2.14 | 2.04 | 2.85 | 2.56 | 3.74 | 4.92 | ND | 6.87 | 0.569 | 2.54 | ND | ND | ND | 4.32 | 9.41 | 2.87 | 4.36 | 4.39 | ND | ND | 2.15 | 5.71 | 4.71 | 3.79 | 4.63 | 5.4 | 2.25 | 1.3 | 2.92 | 6.84 | 0.85 | ND | 3.18 | 0.992 | 0.449 | 0.815 | 0.416 | 1 | 1.35 | ND | ND | 2.97 | 2.2 | 0.445 | ND
A |  | L | 5.05 | 0.349 | 2.09 | 2.05 | ND | 0.942 | 1.18 | 2.25 | 1.26 | 2.06 | 0.348 | 3.13 | 0.452 | 3.18 | 6.38 | 1.81 | 3.57 | 4.86 | 1.12 | 2.27 | 0.69 | 6.6 | ND | 3.99 | ND | ND | 1.24 | 0.974 | 0.941 | ND | ND | 3.98 | 2.96 | ND | 1.71 | 2.33 | 6.78 | 4.65 | 1.68 | 1.59 | 6.21 | ND | ND | 5.32 | 1.2 | 6.75 | ND | ND | 5.27 | 5.48 | 3.67 | 5.78 | 4.11 | 1.87 | 1.87 | ND | 0.327 | 0.744 | 0.081 | 2.08 | ND | 2.01 | ND | ND | 0.99 | 1.58 | ND | 2.78 | ND
| +9 FT | C | 1.44 | 2.07 | 3.05 | 0.904 | 1.69 | 1.3 | 2.24 | 3.43 | 2.47 | 3.2 | 1.98 | 1.53 | 0.618 | 4.32 | 4.66 | 0.057 | ND | 0.008 | 3.58 | 3.93 | 2.26 | 4.76 | ND | 1.86 | 0.463 | 2.59 | 3.89 | ND | 3.13 | 1.33 | 5.97 | 1.51 | 3.47 | 3.57 | 0.751 | 2.08 | 5.71 | 0.77 | 3.52 | 3.7 | 4.11 | ND | 4.27 | 0.94 | ND | ND | 1.37 | 0.294 | 3.63 | 1.44 | 1.88 | 5.96 | 1.6 | 2.57 | 2.72 | ND | 2.27 | 0.464 | 1.99 | ND | ND | 0.217 | ND | ND | 1.58 | 0.164 | ND | 0.919 | ND
|  | R | 0.202 | 2.63 | 1.1 | 0.477 | ND | 1.74 | 1.88 | 2.88 | 1.2 | 1.54 | 1.63 | 2.64 | 1.24 | 2.42 | 4.49 | 0.242 | 0.952 | 1.41 | 1.69 | 4.22 | 2.63 | 2.55 | 8.24 | 4.93 | 4.78 | 0.2 | 1.54 | ND | 0.368 | 1.01 | 2.77 | 0.849 | 3.14 | 2.77 | 0.786 | ND | 7.58 | 2.07 | ND | 4.04 | 4.43 | ND | 2.47 | 6.83 | ND | 1.74 | 5.35 | 0.718 | 6.41 | 7.49 | 0.678 | 4.36 | 4.2 | 4.05 | 2.01 | ND | 1.98 | 0.54 | ND | ND | 2.97 | 3.49 | ND | 0.421 | 0.247 | ND | ND | 1.38 | ND
A | POSITION 'A' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.9 | ND | 2.35 | 4.07 | 0.838 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.66 | 2.16 | 5.28 | 2.05 | 2.6 | 0.227 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4.27 | 0.328 | 3.45 | 1.47 | 3.4 | 1.19 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION 'B' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5.37 | 2.03 | ND | ND | 2.06 | 1.42 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4.65 | 2.55 | 0.486 | ND | 3.56 | 1.99 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.2 | 2.02 | 1.54 | 2.71 | 4.03 | 1.2 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION 'C' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.13 | 4.52 | 1.52 | 1.3 | 2.78 | 0.32 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.09 | 1.54 | 0.716 | 3.41 | 0.02 | 0.731 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.68 | 0.342 | 0.465 | ND | ND | 1 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION 'D' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5.93 | 2.71 | 0.798 | 2.57 | ND | 2.5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5.04 | 3.89 | 3.93 | 0.039 | 1.18 | 1.47 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.12 | ND | 4.64 | ND | 1.55 | 3.64 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION 'E' | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4.48 | 0.251 | 0.918 | 3.04 | 0.802 | 0.535 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4.62 | 4.95 | 1.53 | 3.13 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| OSCILLATOR | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.59 | ND | 0.642 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A |  | L | 2.75 | 3.17 | ND | 1.73 | ND | 0.492 | 0.951 | ND | 0.842 | 4.27 | 3.3 | ND | 0.83 | 1.22 | 2.48 | 2.63 | ND | ND | 2.87 | 2.19 | 3.1 | 2.59 | ND | ND | 1.54 | 4.45 | 5.55 | ND | 3.02 | 2.1 | 1.5 | 4.16 | 2.63 | 3.75 | 4.88 | 6.48 | 0.242 | 0.083 | 1.06 | 1.08 | 0.012 | 1.33 | 2.38 | ND | ND | ND | 8.56 | 3.5 | 2.86 | 4.28 | 0.287 | 7.63 | 4.53 | 0.295 | 4.54 | ND | 2.37 | ND | 0.566 | 1.5 | 3.15 | 0.386 | 3.64 | ND | 2.59 | 3.23 | 0.264 | 3.18 | ND
| +7 FT 6 IN | C | 5.61 | 0.811 | 0.405 | 0.47 | 2.41 | 0.507 | 1.46 | ND | 1.37 | 2.04 | 2.96 | 3.87 | 9.81 | 0.953 | 0.531 | 1.35 | 1.72 | 0.188 | 0.719 | 0.346 | 2.41 | 5.85 | ND | 4.21 | 1.84 | 3.36 | 1.97 | ND | 1.97 | 3.46 | 4.28 | 9.58 | 6.52 | 2.69 | 4.09 | 6.57 | ND | 0.676 | ND | 2.14 | 0.323 | 0.698 | 3.29 | ND | 3.16 | 1.45 | 6.59 | 0.578 | ND | ND | 0.095 | ND | 2.47 | ND | ND | 0.776 | 1.81 | ND | 1.21 | 1.45 | 1.87 | ND | 2.84 | 2.3 | 1.11 | 3.67 | 1.21 | 1.38 | 1.25
|  | R | 0.689 | 2.77 | 1.92 | 4.53 | 1.88 | 3.88 | 3.24 | ND | 0.972 | 3.52 | 2.15 | 3.34 | 0.687 | 3.01 | 2.9 | 2.09 | 3.44 | 1.96 | 3.37 | 4.18 | 4.66 | 4.86 | ND | ND | 2.27 | ND | ND | ND | 0.871 | ND | 3.64 | 6.51 | 6.71 | 4.32 | 1.79 | 8.57 | 2.04 | 4.72 | ND | 2.26 | 0.84 | 0.423 | 2.55 | ND | ND | 1.29 | 2.23 | 1.34 | ND | 2.52 | ND | 0.389 | 1.42 | ND | ND | 2.53 | ND | 0.499 | ND | 1.81 | 4.39 | 0.746 | 3.17 | 3.01 | 1.68 | 2.05 | 3.69 | 1.44 | 2.04
A |  | L | 2.66 | ND | 1.61 | 0.982 | 2.4 | 0.638 | 0.863 | 3.31 | 2.43 | 1.9 | 0.753 | 4.2 | 4.42 | ND | 2.86 | 4.69 | 4.51 | 5.03 | 2.71 | 0.034 | 4.21 | ND | ND | 3.51 | 0.839 | 0.193 | ND | ND | ND | ND | ND | ND | 5.15 | 0.838 | 5.79 | ND | 2.12 | 0.871 | ND | ND | 1.66 | 1.58 | 2.31 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.15 | 0.77 | ND | ND | 0.779 | 0.714 | ND | 0.009 | 0.711 | ND | 0.255 | 0.584 | ND | ND | ND | 0.774
| +6 FT | C | 1.39 | 1.34 | 0.128 | 3.06 | 0.04 | 0.552 | 1.94 | 0.499 | 3.31 | 1.18 | 2.81 | 2.93 | 1.57 | 1.85 | 1.52 | 4.15 | 2.01 | 0.987 | 4.67 | 2.94 | 0.684 | 5.36 | 0.038 | 6.11 | 4.31 | 1.36 | 0.342 | ND | ND | ND | ND | ND | 5.67 | 2.93 | 5.7 | ND | 0.57 | ND | ND | ND | ND | ND | 0.979 | ND | ND | ND | ND | 0.105 | 1.65 | ND | ND | ND | 0.144 | 0.813 | ND | ND | ND | 0.31 | ND | ND | 2.02 | ND | ND | 0.176 | 0.334 | 1.35 | ND | 1.97 | ND
|  | R | 0.194 | 1.94 | 0.912 | 2.98 | 0.403 | 4.4 | 2.22 | 1.34 | 2.21 | 1.35 | ND | 1.39 | 2.07 | 2.83 | 2.11 | 3.54 | 4.92 | 5.56 | ND | 9.34 | 3.3 | 6.17 | 4.19 | 4.34 | 8.03 | ND | 0.679 | ND | ND | ND | ND | ND | 7.73 | 0.843 | 4.5 | 0.341 | ND | 3.55 | ND | ND | 2.83 | ND | ND | ND | ND | ND | ND | 1.41 | 0.839 | ND | ND | ND | ND | ND | 1.35 | ND | ND | ND | ND | ND | 0.863 | ND | ND | ND | 2.07 | 0.959 | 0.281 | 0.981 | 2
A |  | L | 1.12 | 0.76 | ND | 0.532 | ND | 0.042 | 1.95 | ND | 1.68 | 2.95 | 1.53 | 7.18 | ND | ND | 4.19 | ND | 1.14 | 0.894 | 5.59 | 2.57 | ND | 3.17 | ND | 4.97 | 0.975 | 0.214 | ND | ND | ND | ND | 4.02 | 2.09 | 3.15 | 3.84 | ND | 3.65 | ND | ND | ND | ND | 2.75 | ND | 1.79 | 0.944 | ND | ND | ND | 6.61 | 2.74 | ND | 0.881 | 2.79 | 1.07 | ND | ND | 2.38 | 2.47 | 0.738 | 0.049 | ND | 2.1 | 1.61 | 0.425 | 1.43 | 3.69 | 2.87 | 1.89 | ND | 1.12
| +4 FT 6 IN | C | 2.41 | 0.184 | 0.849 | ND | 3.23 | 0.982 | 0.634 | 0.885 | 1.19 | 0.043 | 1 | 8.13 | ND | ND | 1.49 | 4.39 | ND | ND | 4.14 | ND | ND | 1.95 | 3.41 | 0.339 | 4.9 | 0.23 | 0.556 | 0.243 | 0.096 | 1.15 | 0.963 | 0.106 | ND | ND | 1.42 | 0.251 | ND | ND | ND | 0.285 | 1 | ND | 0.614 | 2.26 | 0.803 | 0.886 | 0.681 | 4.9 | 6.35 | 4.11 | 1.55 | ND | 1.78 | ND | ND | 0.746 | 2.52 | 0.128 | 1.51 | 1.5 | 1.82 | 0.221 | 2.06 | 4.11 | 1.61 | 6.12 | ND | ND | 1.9
|  | R | 4.35 | 0.796 | 0.905 | ND | 1.75 | 2.28 | 0.656 | 1.94 | 1.41 | 1.17 | 1.84 | 7.18 | ND | 0.984 | 0.416 | 3.29 | ND | 5.55 | 3.29 | ND | ND | ND | 4.76 | 3.95 | ND | ND | 0.915 | 0.271 | ND | 1.63 | 1.54 | 1.47 | ND | ND | 0.768 | 0.668 | 0.57 | ND | ND | ND | ND | ND | ND | 2.13 | ND | 0.829 | 0.808 | 5.83 | 5.19 | 3.56 | ND | 0.918 | 1.16 | ND | 0.666 | ND | 0.291 | 1.65 | ND | ND | 1.94 | ND | 2.81 | 2.01 | ND | 0.966 | 1.01 | ND | 1.48
A |  | L | 2.71 | 3.53 | ND | ND | 4.78 | ND | 3.09 | 1.29 | 1.4 | ND | 2.63 | 1.57 | 1.05 | ND | 1.25 | ND | 0.947 | ND | ND | 4.09 | ND | ND | 1 | 1.72 | 3.7 | ND | 7.18 | 3.22 | 5.75 | 3.58 | 2.48 | ND | ND | ND | ND | ND | ND | 1.19 | ND | ND | ND | ND | 1.45 | ND | 2.79 | 2.63 | 0.072 | 4.34 | 6.04 | ND | 2.62 | ND | 0.844 | 0.466 | 1.98 | ND | 0.677 | 1.87 | 1.95 | 1.17 | ND | ND | 1.34 | 2.36 | 3.38 | 1.46 | 0.945 | 0.504 | ND
| +3 FT | C | 1.69 | 5.66 | 1.46 | ND | 2.1 | ND | 1.17 | 1.47 | ND | ND | 1.37 | ND | ND | ND | ND | 0.627 | 0.364 | ND | 4.05 | 0.326 | ND | ND | ND | 3.16 | 1.75 | 2.41 | 2.96 | 1.67 | 6.6 | 0.953 | 3.77 | 10.7 | 0.775 | ND | ND | ND | ND | 0.274 | ND | ND | 0.853 | 2.82 | 0.77 | 5.53 | 3.26 | 3.57 | 3.7 | 9.98 | 8.52 | 1.3 | 1.25 | 1.57 | ND | 1.13 | 1.57 | 0.478 | 1.26 | ND | 0.725 | ND | 1.13 | ND | 1.13 | 1.87 | 1.58 | 1.99 | 1.22 | ND | 0.665
|  | R | 4.07 | 0.765 | ND | ND | ND | ND | 3.01 | 0.262 | ND | ND | 0.773 | ND | ND | ND | ND | 0.01 | 4.89 | ND | 1.07 | ND | ND | 0.658 | ND | 1.65 | ND | 2.12 | 1.39 | 3.67 | 4.63 | 0.112 | 2.15 | ND | ND | ND | ND | 0.079 | ND | 1.95 | 1.26 | 1.16 | 1.1 | ND | 2.62 | 3.66 | 1.52 | 1.05 | 5.5 | 8.29 | 8 | ND | 2.59 | ND | 0.618 | 4.4 | 3.35 | 1.11 | 0.786 | 0.835 | ND | 0.45 | 2.59 | ND | 0.816 | 2.29 | 4.55 | 4.07 | 0.711 | ND | ND
A |  | L | 0.476 | 1.19 | 2.58 | 1.48 | 2.45 | ND | ND | ND | 4.47 | 2.35 | 2.65 | ND | ND | ND | 4.14 | 3.75 | 3.55 | 2.94 | 2.6 | ND | ND | ND | ND | 0.751 | ND | ND | ND | 1.78 | 1.19 | 1.31 | 3.59 | ND | 5.42 | ND | 4.1 | ND | ND | 0.568 | 0.207 | 2.15 | 1.73 | 3.4 | 4.26 | 2.74 | 1.02 | 2.11 | 2.01 | 1.09 | ND | 7.47 | 1.11 | 2.08 | 4.23 | 3.13 | 3.11 | 2.09 | 2.3 | 5.04 | ND | ND | ND | 1.2 | 0.431 | ND | 10.8 | 8.21 | ND | 0.544 | 0.285
| +1 FT 6 IN | C | 4.04 | 4.89 | 1.83 | 1.53 | 1.89 | 2.83 | ND | 0.1 | 0.152 | 0.765 | ND | ND | ND | 3.76 | 4.93 | 1.56 | ND | 2.46 | ND | ND | ND | ND | ND | 0.972 | ND | ND | 0.025 | 1.98 | 0.474 | 4.49 | 2.66 | 3.25 | 1.28 | 2.15 | 2.1 | 3.32 | 3.13 | 0.31 | ND | 1.37 | 1.81 | 4.68 | 3.31 | 4.28 | 1.42 | 5.22 | 4.2 | 1.99 | ND | 0.865 | 1.37 | 1.34 | 1.13 | 3.34 | 1.91 | 2.86 | ND | 2.12 | 0.572 | 3.01 | 0.417 | 0.514 | ND | ND | 8.93 | 7.02 | ND | 4.97 | 0.504
|  | R | ND | 3.11 | 1.78 | 1.74 | 3.55 | 2.73 | 1 | 1.14 | ND | 3.53 | 0.468 | ND | 0.124 | 5.64 | ND | 2.7 | ND | ND | 0.44 | 1.99 | ND | ND | ND | ND | 1.52 | ND | 0.139 | 2.54 | 1.78 | 2.84 | 2.76 | 0.892 | 0.545 | 4.22 | 3.29 | 3.81 | 3.42 | 1.85 | 1.84 | 1.7 | 4.04 | 5.55 | 3.63 | 5.58 | 3.82 | 3.26 | 7.43 | 1.15 | ND | 3.89 | ND | 5.99 | 2.42 | 2.29 | 1.94 | 0.548 | ND | 2.18 | 0.315 | ND | ND | ND | 0.359 | ND | 5.16 | 6.1 | 0.804 | ND | 0.083
A |  | L | 3.3 | 5.07 | 6.76 | ND | ND | 0.637 | 2.92 | 7.95 | 4.02 | 2.75 | 5.73 | 2.59 | ND | 0.25 | 1.72 | ND | 5.3 | 3.76 | 0.818 | ND | 0.781 | 2.4 | ND | ND | 1.19 | 4.42 | 2.08 | 2.62 | 4.65 | 11.2 | 0.906 | ND | ND | ND | 1.25 | 3.19 | ND | ND | ND | ND | ND | 1.34 | 0.8 | ND | ND | 6.84 | 4.03 | 0.549 | 3.9 | 3.69 | 7.89 | ND | 3.57 | 1.22 | ND | ND | ND | ND | ND | ND | 1.78 | ND | 0.937 | ND | ND | 5.17 | ND | 2.52 | ND
| 0 REFERENCE | C | 4.57 | 5.66 | 7.13 | ND | ND | 0.823 | 1.35 | 6.7 | 3.81 | ND | 2.04 | 0.651 | ND | 5.86 | 0.806 | 0.673 | 5.86 | 2.75 | 3.16 | ND | ND | ND | 2.55 | 0.831 | 4.58 | 5.42 | 1.89 | 7.61 | 4.01 | 1.85 | ND | ND | ND | ND | 2.06 | 4.96 | 0.173 | 0.75 | ND | ND | ND | 6.06 | 2.97 | 6.03 | 4.82 | 5.84 | 0.242 | 4.09 | 2.61 | 5.57 | 4.4 | 6.87 | 3.53 | 3.43 | 1.27 | ND | ND | ND | 0.144 | ND | 1.02 | ND | 2.3 | ND | 4.75 | 10.3 | 0.968 | 6.36 | ND
|  | R | 1.28 | 6.54 | 1.18 | ND | ND | 3.4 | 4.56 | 3.14 | 0.447 | 3.56 | 2.43 | 2.92 | ND | 6.1 | ND | 0.43 | 7.37 | 1.77 | 1.78 | ND | ND | ND | 3.74 | 4.38 | 4.61 | 1.73 | 3.86 | 8.93 | 2.73 | 1.03 | ND | ND | ND | ND | 3.41 | 3.54 | ND | ND | ND | ND | ND | 4.11 | 3.97 | 5.73 | 2.01 | 4.61 | ND | ND | 3.71 | 5.88 | 8.65 | 3.39 | ND | 1.6 | ND | ND | ND | ND | ND | ND | ND | 2.55 | 1.38 | ND | 5.08 | 10.9 | ND | 8.71 | ND
A | POSITION 'A' | L | ND | 0.528 | ND | 4.09 | 3.52 | 1.17 | 1.32 | ND | ND | ND | 3.32 | 3.61 | 3.7 | 2.62 | 2.01 | 4.47 | ND | ND | 5.31 | 3.18 | 5.92 | 8.28 | 1.84 | 4.21 | ND | ND | ND | ND | ND | ND | ND | ND | 0.359 | 2.25 | 0.141 | ND | 0.895 | 1.69 | 3.45 | 3.92 | ND | 0.173 | ND | ND | ND | ND | ND | ND | 4.3 | 2.41 | 4.46 | ND | ND | 1.7 | 0.72 | 3.52 | 6.34 | 0.412 | 1.24 | ND | ND | 1.33 | 3.88 | ND | ND | ND | ND | ND | ND
| OF THE | C | ND | 1.78 | ND | 3.92 | 7.36 | 1.31 | 1.79 | ND | ND | ND | 3.48 | 1.77 | 4.95 | 3.93 | 3.82 | 4.76 | ND | ND | 5.3 | 2.16 | 12.6 | 8.07 | 3.39 | 3.73 | ND | ND | ND | ND | ND | ND | ND | 4.82 | 3.09 | 2.32 | 2.47 | ND | 1.68 | 5.8 | 4.22 | 6.47 | ND | 0.425 | ND | ND | ND | 1.72 | ND | 1.49 | 3.42 | ND | 0.849 | ND | ND | 1.83 | 2.46 | 5.58 | 4.95 | 1.61 | 3.73 | ND | ND | ND | 3.66 | ND | 7.14 | ND | ND | ND | ND
| SECONDARIES | R | ND | 1.03 | ND | 4.52 | 5.02 | 2.1 | 1.82 | ND | ND | ND | 3.9 | 5.06 | 5.09 | 2.55 | 2.24 | 2.9 | ND | ND | 3.39 | 3.09 | 10.4 | 4.7 | 2.55 | 3.6 | ND | ND | ND | ND | ND | ND | ND | 4.44 | 3.67 | 2.97 | 2.35 | ND | 0.937 | 0.861 | 7.24 | 5.81 | 0.486 | ND | ND | ND | ND | 0.062 | ND | 2.23 | ND | 0.367 | 1.29 | ND | ND | 0.921 | ND | 8.64 | 6.78 | 4.39 | 3.14 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION 'B' | L | ND | 1.32 | 2.88 | 4.66 | 2.01 | 1.57 | 3.56 | ND | ND | ND | 2.93 | 1.98 | 2.55 | 2.81 | 2.86 | 3.15 | ND | ND | 3.48 | 1.93 | 2.74 | 0.622 | 3.5 | 5.4 | ND | ND | ND | ND | ND | ND | ND | 3.5 | 1.58 | 1.49 | 1.92 | ND | 3.75 | 4.66 | 1.16 | 1.77 | ND | 1.01 | ND | ND | ND | ND | 0.297 | 3.79 | 1.95 | ND | ND | ND | ND | 2.22 | ND | 2.36 | 3.9 | 1.33 | ND | ND | ND | ND | ND | ND | ND | ND | 0.641 | ND | ND
| OF THE | C | ND | ND | 1.03 | 4.3 | 2.28 | ND | 2.95 | ND | ND | ND | 3.68 | 2.53 | ND | 1.97 | 1.66 | ND | ND | ND | 4.21 | 2.75 | 0.663 | 1.73 | ND | 3.87 | ND | ND | ND | ND | ND | ND | ND | 1.52 | 3.25 | 0.946 | ND | ND | 2.76 | 3.48 | 2.44 | 2.36 | 1.55 | ND | ND | ND | ND | ND | 0.902 | 4.72 | 2.31 | ND | 0.97 | ND | ND | 6.46 | 0.333 | 1.15 | 1.9 | ND | 2.4 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| SECONDARIES | R | ND | ND | 0.216 | 0.978 | 0.085 | ND | 4.14 | ND | ND | ND | 3.58 | 2.61 | 1.88 | 2.41 | 2.3 | 4.42 | ND | ND | 1.82 | 2.3 | 2.21 | 2.35 | 2.2 | 1.42 | ND | ND | ND | ND | ND | ND | ND | 2.6 | 3.31 | 2.24 | 4.31 | ND | 4.79 | 1.63 | 0.546 | 1.78 | ND | 3.63 | ND | ND | ND | ND | 1.25 | 3.4 | 0.439 | ND | 3.63 | ND | ND | ND | ND | 2.75 | 3.53 | 1.27 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A |  | L | 0.081 | 1.52 | 3.25 | 4.85 | 5.29 | ND | 0.486 | ND | 3.04 | ND | ND | ND | ND | ND | 1.55 | 2.46 | ND | 1.76 | 1.22 | ND | ND | ND | 0.783 | ND | 2.03 | 0.504 | ND | 0.304 | 1.35 | ND | 0.424 | ND | ND | ND | ND | 5.4 | 2.09 | ND | 1.36 | 0.537 | 1.59 | 0.688 | 11.1 | 3.21 | 1.16 | 9.43 | 3.15 | ND | ND | 3.36 | ND | 2.48 | 1.67 | 3.3 | 3.31 | ND | ND | ND | 0.433 | ND | 0.327 | ND | ND | ND | 6.68 | 9.49 | ND | ND | ND
| -9 IN | C | 2.57 | 4.56 | 3.59 | 0.169 | 5.34 | 0.364 | 0.907 | ND | 2.95 | 1.32 | ND | ND | 0.808 | ND | 0.086 | 0.925 | 1.04 | 1.76 | ND | ND | 0.545 | 1.01 | ND | ND | 0.24 | ND | 1.26 | ND | 1.25 | 1.68 | 5.22 | ND | 3.67 | 3.99 | 7.08 | 7.17 | ND | 0.914 | 2.61 | 0.313 | 0.24 | 2.11 | 11.8 | 5.17 | 2.04 | 6.9 | 2.44 | ND | ND | 6.11 | 2.77 | 2.38 | 3.91 | 6.72 | 4.41 | 0.767 | 1.34 | ND | 0.604 | ND | ND | ND | ND | 0.579 | 6.25 | 3.48 | ND | ND | 5.55
|  | R | ND | 2.74 | 1.06 | 0.915 | 2.69 | ND | 0.787 | ND | 1.81 | 1.97 | ND | 0.098 | 0.117 | ND | ND | 2.04 | ND | 1.49 | 1.11 | ND | 3.62 | ND | ND | ND | 1.67 | ND | ND | 2.56 | 3.37 | ND | 1.47 | 2.17 | 4.13 | 2.69 | 7.39 | 6.14 | 1.36 | 1.03 | 3.01 | 2.86 | 1.9 | 0.454 | 16.7 | 7.36 | 4.69 | 4.87 | 3.33 | ND | ND | 5.53 | 5.42 | 4.58 | 6.93 | 4.93 | 3.15 | 0.891 | 0.774 | ND | ND | ND | ND | ND | 0.401 | 3.6 | 6.74 | 10.3 | 0.034 | ND | ND
A | POSITION 'C' | L | ND | 1.94 | 3.55 | 5.13 | 6.31 | 2.62 | 2.71 | ND | ND | ND | 2.82 | 0.345 | 4.62 | 3.5 | 3.32 | 5.72 | ND | ND | 2.59 | 3.86 | 4.9 | 6.56 | 2.71 | 2.51 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.94 | 2.45 | ND | 0.155 | 2.34 | 4.05 | 5.53 | ND | 2.66 | ND | ND | ND | ND | ND | 2.44 | 5.64 | 0.646 | 1.58 | ND | ND | 1.06 | 0.338 | 6.01 | 4.14 | 0.925 | ND | ND | ND | ND | ND | 0.714 | ND | ND | ND | ND | ND
| OF THE | C | ND | 1.5 | 2.97 | 6.96 | 6.92 | 0.937 | 2 | ND | ND | ND | 1.68 | 1.13 | 7.35 | 1.44 | ND | 4.38 | ND | ND | 4.61 | 2.61 | 5.49 | 6.2 | 2.68 | 2.45 | ND | ND | ND | ND | ND | ND | ND | 2.23 | 4.29 | ND | ND | ND | 1.26 | 5.17 | 3.76 | 4.58 | ND | 7.38 | ND | ND | ND | ND | 1.69 | 0.533 | 4.47 | 1.14 | 1.65 | ND | ND | 0.008 | ND | 7.54 | 4.16 | 0.809 | ND | ND | ND | ND | ND | ND | ND | ND | 0.702 | ND | ND
| SECONDARIES | R | ND | 1.01 | ND | 4.02 | 6.56 | 3.34 | 3.41 | ND | ND | ND | 1.86 | 0.869 | 1.6 | 2.93 | 2.44 | 3.55 | ND | ND | 5.01 | 4.07 | 3.66 | 4.77 | 3.09 | 1.29 | ND | ND | ND | ND | ND | ND | ND | 3.34 | 3.04 | 5.22 | 1.92 | ND | ND | 2.08 | 2.85 | 6.8 | 4.37 | 3.39 | ND | ND | ND | 1.95 | 5.42 | 9.48 | 0.73 | 1.19 | ND | ND | ND | 2.26 | 4.7 | 7.5 | 4.33 | 0.782 | ND | ND | ND | ND | 3.58 | ND | ND | 2.18 | ND | ND | ND
A |  | L | 5.42 | 3.15 | 4.05 | 1 | 1.91 | ND | 0.612 | 0.223 | ND | 3.71 | ND | 2.93 | 4.11 | ND | 3.24 | 0.186 | ND | 0.449 | 1.84 | 1.34 | 2.2 | 1.29 | ND | 1.77 | 0.26 | 0.952 | ND | 1.97 | 1.39 | ND | 2.9 | 2.4 | 1.92 | ND | ND | ND | ND | 1.09 | 2.45 | 4.96 | 1.59 | 5.43 | 0.902 | 2.89 | 2.09 | 1.27 | 0.002 | 9.98 | ND | ND | 1.24 | 1.12 | ND | ND | ND | 0.697 | 1.68 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| -18 IN | C | ND | 7.32 | 4.02 | 0.798 | 1.03 | ND | ND | ND | 0.33 | 2.87 | 1.31 | 1.74 | 1.98 | ND | 2.84 | ND | 0.849 | 1.08 | 0.744 | 2.13 | ND | 1.42 | ND | 1.93 | ND | 0.346 | ND | ND | ND | 2.46 | 1.57 | 2.26 | 0.937 | ND | 0.034 | 0.508 | 1.47 | 1.21 | 1.65 | ND | ND | 1.64 | ND | ND | 0.011 | ND | ND | 3.62 | ND | 0.811 | 1.21 | ND | ND | ND | ND | 0.382 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
|  | R | 2.35 | 4.56 | 3.34 | 1.61 | 0.89 | 0.183 | 0.853 | ND | ND | 0.369 | 0.899 | ND | 1.68 | 2.2 | ND | 1.07 | 0.521 | 1.18 | 0.35 | 4.17 | ND | 0.693 | 2.25 | ND | ND | 0.485 | ND | ND | ND | ND | 0.321 | 1.62 | ND | ND | ND | 2.94 | ND | ND | 3.68 | 1.08 | ND | ND | ND | 1.31 | ND | ND | ND | 2 | ND | ND | ND | 0.946 | ND | ND | 2.49 | 1.56 | ND | ND | ND | ND | 0.448 | ND | ND | 1.34 | ND | 7.04 | ND | ND | 1.62
A |  | L | ND | ND | ND | ND | ND | 0.334 | ND | 2.08 | ND | ND | 1.89 | ND | ND | ND | 0.142 | 0.465 | 0.339 | ND | 1.74 | 0.855 | ND | 0.12 | 3.69 | 2.1 | ND | ND | 0.475 | ND | ND | 0.942 | 0.554 | 2.8 | 2.15 | 3.87 | 1.08 | 5.9 | 3.71 | 1.22 | 3.73 | 2.04 | 5.63 | 2.36 | 4.63 | ND | 0.462 | 2.8 | 1.88 | 2.53 | 9.5 | ND | 0.814 | ND | 1.07 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5.13 | ND
| -27 IN | C | 0.476 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.47 | ND | 0.116 | ND | ND | ND | ND | ND | 0.09 | ND | ND | 6.67 | 1.55 | 1.41 | ND | ND | ND | ND | ND | ND | ND | ND | 0.602 | 1.91 | ND | 1.68 | ND | 2.24 | 1.1 | ND | ND | ND | 0.524 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 3.27 | ND
|  | R | ND | ND | ND | ND | ND | ND | ND | 0.939 | ND | ND | ND | 1.92 | ND | ND | ND | 1.37 | ND | ND | 0.855 | 0.102 | 0.189 | 0.037 | 3.43 | 1.62 | ND | ND | ND | 0.363 | ND | 0.949 | 0.526 | 1.89 | 1.24 | ND | ND | 0.654 | 1.66 | 0.32 | 2.33 | 3 | ND | ND | ND | ND | ND | 1.64 | ND | 3.27 | 4.77 | ND | ND | ND | 0.329 | 0.133 | ND | ND | ND | ND | 0.455 | ND | ND | 1.25 | ND | ND | ND | 2.43 | ND | 0.512 | ND
A |  | L | ND | ND | ND | 2.51 | ND | 1.16 | 0.629 | 0.09 | ND | ND | 0.881 | 2.36 | 0.912 | 0.159 | 2.69 | ND | ND | ND | 1.55 | 0.037 | 0.092 | 0.279 | 0.269 | ND | 1.09 | ND | ND | ND | ND | 0.951 | 2.21 | ND | 2.07 | 4.72 | 1.09 | 1.78 | ND | 3.1 | 1.47 | ND | 2.75 | ND | 5.06 | 4.33 | 2.68 | 1.39 | ND | 4.09 | ND | 0.622 | 3.37 | ND | 0.889 | 1.3 | ND | 0.8 | ND | ND | 1.61 | 2.27 | ND | 0.459 | ND | 0.716 | ND | 0.692 | ND | 3.49 | ND
| -36 IN | C | ND | 0.929 | ND | 0.362 | 0.667 | ND | ND | 0.695 | ND | ND | ND | 0.445 | 0.237 | ND | 0.027 | ND | ND | ND | 4.6 | ND | ND | 2.39 | 1.94 | 0.34 | ND | ND | ND | ND | ND | ND | 1.78 | 1.23 | 1.26 | 2.6 | ND | ND | 1.99 | ND | ND | ND | ND | ND | ND | 2 | ND | ND | ND | ND | ND | ND | ND | ND | 0.558 | ND | ND | 1.68 | ND | ND | ND | 0.815 | ND | ND | 0.107 | ND | ND | ND | ND | 3.55 | ND
|  | R | ND | ND | 0.832 | 1.58 | ND | ND | ND | 0.905 | ND | 0.534 | ND | ND | 2.11 | 0.924 | ND | ND | ND | ND | 2.11 | ND | 1.21 | 2.56 | ND | 3.38 | ND | 0.727 | ND | ND | 0.758 | 2.55 | ND | 0.538 | 2.72 | ND | ND | 0.099 | 0.14 | 1.78 | ND | 0.59 | 0.246 | ND | 0.632 | 1.73 | ND | 0.042 | 1.23 | 3.4 | 5.23 | ND | 0.755 | ND | 3.39 | 1.53 | ND | ND | ND | ND | 0.532 | 3.2 | ND | ND | 2.08 | ND | ND | ND | ND | 2.47 | ND
A |  | L | ND | ND | 2.36 | 3.29 | ND | ND | ND | 0.227 | ND | ND | ND | 1.81 | ND | 1.02 | 1.05 | 0.558 | 2.02 | ND | ND | ND | 0.051 | ND | ND | 2.69 | ND | 0.283 | ND | 0.739 | 2.07 | ND | 1.68 | 0.874 | 2.36 | 4.66 | 2.94 | ND | 1.85 | 0.275 | 0.992 | ND | ND | 2.44 | 1.04 | 2.15 | ND | 1.92 | ND | 2.02 | 12.2 | 2.17 | ND | 2.34 | ND | ND | ND | ND | ND | 0.877 | 0.293 | 1.56 | ND | ND | 1.3 | ND | ND | ND | ND | ND | ND
| -45 IN | C | ND | ND | 1.95 | ND | 1.69 | ND | 1.63 | 0.739 | ND | ND | ND | ND | ND | ND | 0.262 | ND | 1.32 | 1.96 | 1.81 | 0.792 | ND | 1.89 | ND | 0.163 | ND | 0.643 | ND | ND | ND | ND | 2.35 | 0.166 | ND | 0.252 | ND | ND | ND | ND | ND | 0.669 | ND | 0.733 | ND | 0.283 | ND | 0.928 | ND | 0.196 | 14.6 | ND | 2.08 | ND | 0.68 | ND | ND | 2.92 | 3.74 | 1.68 | ND | ND | 0.31 | 0.092 | 0.212 | 5.53 | ND | 0.191 | 0.244 | ND | 10.3
|  | R | ND | 5.95 | ND | ND | 1.94 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.426 | ND | ND | 0.018 | 1.46 | 2.64 | 1.59 | 1.5 | ND | 0.584 | ND | 1.62 | 1.26 | 2.32 | 4.26 | 0.68 | ND | 2.46 | 0.522 | 1.75 | 2.34 | ND | ND | ND | ND | 2.11 | 3.16 | 0.009 | 2.89 | 1.19 | ND | 1.31 | 1.54 | 2.96 | 16.6 | ND | 0.557 | ND | 2.46 | ND | ND | ND | ND | ND | 0.103 | ND | ND | ND | ND | 9.43 | 0.556 | 0.994 | ND | ND | ND
A |  | L | ND | 0.189 | 0.345 | ND | 1.07 | ND | 1.41 | ND | ND | ND | ND | ND | 2 | 0.449 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.21 | 2.47 | ND | 2.8 | 3.43 | ND | ND | ND | 2.5 | 1.17 | 0.767 | ND | ND | ND | ND | ND | ND | 1.3 | ND | ND | 0.826 | ND | ND | ND | 1.14 | 0.899 | 0.985 | 0.128 | ND | ND | ND | ND | ND | ND | 1.2 | ND | ND | 7 | 6.18 | 0.616 | ND | 0.445
| -54 IN | C | ND | 1.41 | 0.317 | ND | ND | 1.5 | 0.553 | ND | ND | ND | ND | ND | 1.61 | ND | ND | 0.586 | ND | ND | 0.019 | ND | 0.46 | ND | ND | ND | 1.46 | ND | ND | ND | 2.16 | ND | ND | ND | ND | ND | ND | 0.512 | 1.91 | 1.59 | ND | 1.03 | ND | ND | 0.311 | 0.688 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.995 | ND | ND | ND | ND | ND | ND | ND | ND
|  | R | 1.75 | ND | 3.36 | 2.35 | 2.38 | ND | 1.55 | ND | ND | ND | ND | ND | ND | 1.47 | ND | 0.15 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.86 | 1.14 | 2.17 | 0.966 | 2.5 | 1.47 | 1.79 | 1.15 | ND | ND | ND | 0.159 | 0.65 | 0.235 | 0.136 | ND | 2.36 | ND | ND | ND | ND | ND | ND | 2.07 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
A | POSITION 'A' | L | ND | ND | 3.21 | 3.03 | ND | 1.6 | 4.23 | ND | 4.03 | 3.48 | ND | 1.58 | 2.01 | ND | 3.73 | 6.04 | ND | 1.99 | 3.93 | ND | 3.41 | 4.27 | ND | 2.91 | 4.81 | ND | 1.78 | 3.65 | ND | 1.57 | 4.36 | ND | 1.32 | 1.44 | ND | 1.77 | 2.46 | ND | 2.44 | 2.72 | ND | 1.76 | 3.71 | ND | 2.27 | 1.69 | ND | 1.61 | 4.93 | ND | 0.875 | 3.71 | ND | 3.32 | 6.15 | ND | 3.07 | 3.87 | ND | ND | 1.68 | ND | 1.27 | ND | ND | 4.73 | 3.51 | ND | ND
| OF THE | C | ND | ND | 2.42 | 1.89 | ND | 1.1 | 2.89 | ND | 0.23 | 1.82 | ND | 0.981 | 3.3 | ND | 2.92 | 4.07 | ND | 0.442 | 3.31 | ND | 1.67 | 2.43 | ND | ND | 5.74 | ND | 1.98 | 2.44 | ND | 3.64 | 1.31 | ND | 0.566 | ND | ND | 1.16 | 5.25 | ND | 3.93 | 0.969 | ND | 1.52 | 0.442 | ND | 2.22 | ND | ND | 2.57 | 4.46 | ND | 0.947 | 3.02 | ND | 3.76 | 1.19 | ND | ND | 3.48 | ND | 2.63 | 1.54 | ND | 2.04 | 0.37 | ND | 1.94 | 1.87 | ND | ND
| PRIMARIES | R | ND | ND | 3 | 1.5 | ND | 1.72 | 3.37 | ND | ND | 3.77 | ND | 2.39 | 4.42 | ND | 2.36 | 1.77 | ND | 2.11 | 1.21 | ND | 3.28 | 2.89 | ND | ND | 4.9 | ND | 2.59 | ND | ND | 4.95 | ND | ND | 0.759 | 0.51 | ND | 1.87 | 2.67 | ND | 1.93 | ND | ND | 0.422 | 0.884 | ND | 1.08 | 1.06 | ND | 3.33 | 0.736 | ND | ND | 0.038 | ND | 5.48 | 1.84 | ND | 1.41 | ND | ND | 0.74 | 1.65 | ND | 0.893 | 1.53 | ND | 1.81 | 1.74 | ND | ND
A | POSITION 'B' | L | ND | ND | 3.01 | 2.44 | ND | 0.965 | 2.95 | ND | 4.42 | 2.82 | ND | 4.55 | 2.6 | ND | 3.01 | 4.26 | ND | 0.583 | 4.18 | ND | 1.54 | 4.67 | ND | 0.829 | 4.64 | ND | 4.56 | 2.11 | ND | 1.09 | 3.91 | ND | 3.27 | 3.42 | ND | 2.82 | 1.64 | ND | 1.97 | 3.74 | ND | 2.98 | 2.77 | ND | 0.765 | 1.04 | ND | 2.3 | 4.28 | ND | 0.288 | 2.27 | ND | 2.3 | 2.2 | ND | ND | 3.05 | ND | ND | 1.58 | ND | ND | 3.99 | ND | 1.89 | 0.3 | ND | ND
| OF THE | C | ND | ND | 8.24 | 4.31 | ND | 2.55 | 4 | ND | 1.53 | 3.31 | ND | 1.62 | 3.16 | ND | 2.4 | 7.12 | ND | 0.304 | 3.07 | ND | 0.545 | 5.39 | ND | 1.85 | 2.69 | ND | 0.204 | 3.36 | ND | 2.58 | 4.17 | ND | 2.93 | 2.64 | ND | 5.45 | 1.82 | ND | 2.28 | ND | ND | 2.58 | 3.23 | ND | 3.77 | 1.33 | ND | 4.14 | 1.46 | ND | 3.29 | ND | ND | 2.93 | 2.16 | ND | 0.016 | 0.678 | ND | 1.57 | 2.12 | ND | 3.14 | ND | ND | 7.24 | ND | ND | ND
| PRIMARIES | R | ND | ND | 3.63 | 4.08 | ND | 4.14 | 2.63 | ND | 2.18 | 2.23 | ND | 3.95 | 3.52 | ND | 2.72 | 6.35 | ND | 2.29 | 1.52 | ND | 4.11 | 3.07 | ND | 3.64 | 3.76 | ND | 3.75 | 2.75 | ND | 5.77 | 3.46 | ND | 3.43 | 2.83 | ND | 0.446 | 2.25 | ND | 3.53 | 2.3 | ND | 2.23 | 1.7 | ND | 3.68 | 1.35 | ND | ND | 3.47 | ND | 3.72 | 1.01 | ND | 3.13 | 0.057 | ND | 1.67 | 2.4 | ND | ND | 2.92 | ND | ND | 3.73 | ND | 1.7 | 1.29 | ND | ND
A | POSITION 'C' | L | ND | ND | 5.51 | 4.35 | ND | 2.35 | 2.74 | ND | 4.4 | 5.06 | ND | 2.08 | 5.12 | ND | 2.69 | 4.88 | ND | 2.9 | 3.22 | ND | 4.5 | 3.53 | ND | 4.26 | 4.38 | ND | 5.23 | 5.07 | ND | 0.107 | 2.06 | ND | 5.18 | 4.24 | ND | 3.55 | 4.45 | ND | 3.8 | 5.94 | ND | ND | 2.79 | ND | 3.02 | 2.1 | ND | 0.819 | 4.37 | ND | 4.65 | 2.94 | ND | 3.18 | 1.5 | ND | ND | 1 | ND | ND | 3.71 | ND | 0.137 | 3.96 | ND | 1.94 | 0.938 | ND | ND
| OF THE | C | ND | ND | 6.82 | 5.14 | ND | 4.23 | 2.33 | ND | 5.76 | 4.01 | ND | 1.52 | 4.95 | ND | 3.98 | 4.09 | ND | 2.96 | 2.84 | ND | 3.16 | 4.28 | ND | 4.13 | 4.83 | ND | 1.98 | 1.75 | ND | 2.48 | 3.28 | ND | 2.09 | 3.61 | ND | 5.37 | 3.37 | ND | 2.9 | 3.67 | ND | ND | 4.08 | ND | 2.27 | 0.667 | ND | 0.854 | 3.36 | ND | 3.5 | ND | ND | 3.51 | 2.13 | ND | 0.719 | 0.094 | ND | ND | 1.09 | ND | 0.046 | 3.67 | ND | 5.9 | 1.73 | ND | ND
| PRIMARIES | R | ND | ND | 3.36 | 2.44 | ND | 4.18 | 2.07 | ND | 2.01 | 1.34 | ND | 2.67 | 0.965 | ND | 1.94 | 1.2 | ND | 4.03 | 0.654 | ND | 2.68 | 6.24 | ND | 3.82 | 4.9 | ND | 3.11 | 0.091 | ND | 3.46 | 4.63 | ND | 1.96 | 1.86 | ND | 1.73 | 3.15 | ND | ND | 1.95 | ND | 2.13 | 1.94 | ND | ND | 1.51 | ND | ND | 2.31 | ND | 2.83 | 0.675 | ND | 3.4 | ND | ND | 0.376 | ND | ND | 0.968 | 1.51 | ND | ND | 1.96 | ND | 1.73 | 2.67 | ND | ND
A |  | L | 1.56 | ND | 1.7 | 4.96 | 2.78 | ND | 0.908 | ND | ND | 0.634 | ND | ND | 2.98 | 3.21 | 0.186 | ND | 0.326 | 3.07 | ND | ND | 3.64 | 0.126 | ND | ND | 0.755 | 5.35 | ND | 0.735 | ND | 2.23 | ND | ND | ND | ND | ND | ND | ND | ND | 1.22 | ND | 0.371 | 0.711 | ND | ND | ND | ND | ND | 1.66 | ND | ND | 0.298 | 0.861 | 2.2 | ND | 1.13 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.1 | 4.03 | ND | ND | ND
| -63 IN | C | 1.99 | ND | 4.68 | 3.16 | 0.386 | 1.18 | 0.212 | 1.93 | ND | ND | ND | 0.738 | 3.24 | 1.98 | ND | 0.973 | ND | ND | ND | 0.744 | 0.808 | 2.04 | ND | ND | ND | 4.05 | 2.49 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.145 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.04 | ND | ND | 0.408 | ND | ND | ND | ND | 0.443 | ND | ND | ND | 2.64 | ND | ND | ND | 6.36 | ND | ND | ND
|  | R | 1.01 | ND | 3.36 | 6.03 | 1.63 | 2.17 | 3.71 | 2.06 | ND | ND | ND | 1.17 | 3.43 | 3 | 2.36 | ND | 1.44 | ND | ND | ND | ND | 1.76 | ND | ND | 2.65 | 0.571 | 1.44 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.36 | ND | ND | ND | ND | ND | ND | 1.34 | ND | ND | 0.163 | ND | ND | ND | ND | ND | 1.01 | 11.7 | 4.08 | ND | ND | ND
A |  | L | 0.401 | ND | ND | 5.2 | 4.75 | 4.35 | ND | 3.51 | 3.31 | 1.66 | 2.7 | 0.36 | 18.4 | 5.07 | 9.53 | ND | ND | 0.7 | 0.354 | ND | 5.51 | ND | 0.407 | 0.893 | 1.39 | ND | 1.54 | ND | ND | ND | 6.06 | ND | ND | ND | ND | ND | ND | ND | 1.61 | 5.38 | ND | ND | 1.27 | 0.918 | ND | ND | ND | 1.31 | ND | ND | ND | ND | 0.17 | ND | ND | 1.31 | ND | ND | ND | ND | 0.087 | ND | ND | ND | 0.023 | 3.27 | ND | ND | ND
| -72 IN | C | 0.165 | 1.63 | 2.77 | 3.91 | 1.85 | ND | 0.465 | 4.23 | 0.153 | 2.88 | 0.289 | ND | 13.4 | 3.94 | ND | 3.1 | ND | ND | ND | ND | 3.91 | 0.558 | ND | ND | 0.055 | 0.425 | 1.42 | ND | ND | ND | 1.68 | ND | ND | 0.105 | 1.6 | 1.61 | ND | 0.863 | 0.465 | 0.009 | 4.5 | ND | 1.79 | 3.25 | 4.75 | ND | ND | 0.586 | 1.74 | ND | ND | ND | ND | 0.752 | 0.523 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.939 | ND | ND | ND
|  | R | 3.68 | 0.533 | 1.97 | 8.08 | 3.41 | 4.03 | 0.475 | ND | 3.85 | 4.67 | 2.94 | 2.03 | 17.3 | 5.3 | ND | 1.98 | 0.129 | 0.222 | 2.48 | 7.01 | 1.05 | 0.388 | 0.247 | 3.76 | ND | 3.33 | ND | ND | 1.22 | 2.26 | ND | 3.66 | ND | ND | ND | ND | 3.08 | 0.775 | ND | 0.404 | ND | ND | ND | ND | 2.52 | ND | ND | 11.5 | 12.1 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.48 | 3.17 | ND | 0.836 | ND | 0.952 | ND | ND | ND
A |  | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 11.3 | 18 | 5.83 | 4.46 | 1.17 | 9.75 | 2.47 | 2.81 | 2.54 | 3.09 | 0.908 | 4.64 | 3.98 | 4.31 | 6.26 | 4.4 | 0.695 | 5.86 | ND | 0.808 | ND | 3.09 | 0.28 | ND | 0.985 | 0.358 | ND | 0.094 | 0.077 | 1.64 | ND | ND | ND | 4.05 | ND | ND | 9.59 | ND | 2.82 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 11.3 | ND | ND | ND | ND
| -81 IN | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 9.48 | 6.63 | 0.303 | 5.72 | 0.533 | ND | 3.81 | 0.854 | 1.34 | 4.82 | 1.36 | 0.781 | 2.42 | 3.61 | 1.7 | 1.71 | 0.704 | 1.17 | ND | 2.55 | 3.3 | ND | 3.35 | 1 | ND | 1.62 | 0.062 | 2.05 | ND | ND | 0.795 | 1.85 | ND | ND | ND | ND | 9.79 | 1.12 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.027 | ND | ND | 2.35 | ND | ND | 10.3 | 0.038 | ND | 11.6 | ND
|  | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 6.63 | 20.8 | ND | 3.94 | 0.03 | 0.85 | 1.37 | 0.796 | ND | ND | ND | ND | 1.39 | ND | 3.54 | 6.25 | 1.84 | 1.67 | ND | ND | ND | 0.654 | ND | ND | ND | 4.43 | ND | 3.31 | 0.391 | ND | ND | 2.87 | ND | ND | ND | ND | ND | 2.48 | 1.09 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.158 | 7.85 | 3.44 | 4.53 | ND | ND
A |  | L | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1.67 | ND | ND | ND | 0.274 | 2.64 | 2.26 | 0.583 | 1.96 | 3.92 | 1.08 | 2.56 | 1.97 | 3.1 | 0.237 | 7.01 | 1.79 | 0.248 | 0.184 | ND | ND | ND | ND | ND | ND | ND | ND | 0.746 | 0.318 | 4.24 | 4.67 | 5.87 | 11.5 | 6.07 | 1.18 | ND
| -90 IN | C | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 2.73 | 0.997 | 2.36 | 1.06 | ND | 2.36 | 1.05 | 2.74 | 1.95 | 4.68 | 2.18 | 4.56 | 3.58 | 2.99 | 0.92 | 4.85 | 9.26 | 0.44 | 0.396 | ND | 3.19 | 2.24 | ND | 2.59 | 1.8 | ND | ND | 1.64 | 2.04 | 2.46 | 2.33 | 4.12 | 5.59 | 0.342 | 2.36 | ND
|  | R | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4.05 | 0.863 | 1.6 | 0.446 | 1.24 | 0.882 | 0.989 | 1.54 | 3.68 | 1.08 | ND | 0.744 | 0.217 | 3.39 | ND | 8.27 | 6.68 | 0.066 | ND | 2.38 | 0.734 | 3.23 | ND | ND | ND | 2.82 | ND | 0.423 | 2.35 | 2.15 | ND | 8.79 | 0.874 | ND | ND | ND
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MAX
| CORROSION RATE (mpy): |  | 10: NOTE: CORROSION RATES ARE BASED ON COMPARISON OF; 30: TEST RESULTS; 67: APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | < 0 mpy (LOSS) or no data |  | 30: OVERALL CORROSION RATE (mils per year):
| 0-10 mpy (LOSS) |  | 10: 2020, 2022, 2023, 2024, 2025 |  |  | CALCULATED CORROSION RATE
| 10-20 mpy (LOSS) |  | 10: INSPECTION DATA; 30: 2.527
| > 20 mpy (LOSS) |  | 10: ND; 15: NO COMPARISON DATA
CORROSION
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Projection
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. PROJECTED THICKNESS MEASUREMENTS ARE IN INCHES. | [72 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MIN
A |  | L | RF | 0.232 | 0.234 | 0.219 | 0.197 | 0.231 | 0.223 | 0.21 | 0.203 | 0.217 | 0.205 | 0.221 | 0.325 | 0.202 | 0.199 | 0.2 | 0.21 | 0.209 | 0.201 | 0.193 | 0.211 | 0.212 | 0.192 | 0.208 | 0.19 | 0.185 | 0.191 | 0.185 | 0.176 | 0.215 | 0.192 | 0.2 | 0.196 | 0.204 | 0.195 | 0.223 | 0.198 | 0.212 | 0.193 | 0.198 | 0.202 | 0.198 | 0.206 | 0.206 | 0.21 | 0.205 | 0.198 | 0.314 | 0.3 | 0.199 | 0.186 | 0.211 | 0.21 | 0.203 | 0.201 | 0.199 | 0.22 | 0.215 | 0.162 | 0.188 | 0.205 | 0.211 | 0.194 | 0.233 | 0.246 | 0.275 | 0.24 | 0.194 | RF
0.083 | +16 FT 6 IN | C | RF | 0.21 | 0.217 | 0.223 | 0.235 | 0.23 | 0.224 | 0.224 | 0.215 | 0.24 | 0.233 | 0.212 | 0.32 | 0.203 | 0.208 | 0.206 | 0.216 | 0.206 | 0.199 | 0.202 | 0.212 | 0.223 | 0.201 | 0.203 | 0.214 | 0.203 | 0.199 | 0.203 | 0.179 | 0.226 | 0.175 | 0.192 | 0.195 | 0.202 | 0.204 | 0.231 | 0.201 | 0.221 | 0.203 | 0.2 | 0.195 | 0.203 | 0.219 | 0.202 | 0.217 | 0.207 | 0.209 | 0.316 | 0.292 | 0.204 | 0.192 | 0.219 | 0.195 | 0.206 | 0.207 | 0.218 | 0.217 | 0.216 | 0.186 | 0.226 | 0.206 | 0.214 | 0.199 | 0.222 | 0.27 | 0.255 | 0.208 | 0.188 | RF
|  | R | RF | 0.227 | 0.23 | 0.213 | 0.219 | 0.232 | 0.22 | 0.209 | 0.22 | 0.224 | 0.216 | 0.206 | 0.326 | 0.197 | 0.188 | 0.199 | 0.215 | 0.216 | 0.202 | 0.203 | 0.209 | 0.203 | 0.226 | 0.207 | 0.201 | 0.202 | 0.194 | 0.192 | 0.188 | 0.209 | 0.182 | 0.201 | 0.193 | 0.193 | 0.203 | 0.204 | 0.214 | 0.22 | 0.199 | 0.201 | 0.211 | 0.206 | 0.214 | 0.2 | 0.206 | 0.215 | 0.216 | 0.293 | 0.298 | 0.22 | 0.187 | 0.217 | 0.219 | 0.209 | 0.212 | 0.222 | 0.216 | 0.21 | 0.184 | 0.209 | 0.206 | 0.223 | 0.202 | 0.216 | 0.258 | 0.256 | 0.206 | 0.176 | RF
A |  | L | 0.287 | 0.229 | 0.21 | 0.233 | 0.219 | 0.236 | 0.238 | 0.214 | 0.229 | 0.221 | 0.219 | 0.204 | 0.313 | 0.207 | 0.197 | 0.191 | 0.201 | 0.204 | 0.214 | 0.192 | 0.195 | 0.225 | 0.203 | 0.182 | 0.191 | 0.169 | 0.196 | 0.202 | 0.188 | 0.2 | 0.167 | 0.18 | 0.219 | 0.202 | 0.209 | 0.174 | 0.202 | 0.216 | 0.202 | 0.174 | 0.19 | 0.174 | 0.195 | 0.177 | 0.204 | 0.193 | 0.156 | 0.283 | 0.296 | 0.186 | 0.19 | 0.188 | 0.189 | 0.188 | 0.194 | 0.186 | 0.226 | 0.17 | 0.202 | 0.201 | 0.206 | 0.199 | 0.198 | 0.207 | 0.261 | 0.26 | 0.212 | 0.185 | RF
0.083 | +15 FT | C | 0.287 | 0.233 | 0.207 | 0.23 | 0.223 | 0.234 | 0.229 | 0.213 | 0.23 | 0.232 | 0.217 | 0.218 | 0.313 | 0.217 | 0.225 | 0.201 | 0.2 | 0.184 | 0.2 | 0.183 | 0.206 | 0.223 | 0.169 | 0.191 | 0.207 | 0.188 | 0.21 | 0.201 | 0.21 | 0.193 | 0.192 | 0.19 | 0.227 | 0.212 | 0.209 | 0.221 | 0.205 | 0.191 | 0.183 | 0.192 | 0.207 | 0.207 | 0.21 | 0.202 | 0.193 | 0.196 | 0.205 | 0.294 | 0.296 | 0.204 | 0.209 | 0.185 | 0.193 | 0.206 | 0.214 | 0.207 | 0.232 | 0.203 | 0.215 | 0.187 | 0.2 | 0.2 | 0.218 | 0.212 | 0.257 | 0.264 | 0.201 | 0.162 | RF
|  | R | 0.269 | 0.235 | 0.22 | 0.235 | 0.212 | 0.222 | 0.223 | 0.206 | 0.233 | 0.232 | 0.229 | 0.217 | 0.322 | 0.218 | 0.211 | 0.205 | 0.207 | 0.197 | 0.208 | 0.198 | 0.205 | 0.22 | 0.206 | 0.183 | 0.207 | 0.194 | 0.203 | 0.195 | 0.206 | 0.179 | 0.193 | 0.199 | 0.218 | 0.214 | 0.21 | 0.213 | 0.206 | 0.207 | 0.188 | 0.194 | 0.198 | 0.195 | 0.19 | 0.196 | 0.188 | 0.182 | 0.197 | 0.277 | 0.281 | 0.195 | 0.208 | 0.182 | 0.211 | 0.193 | 0.188 | 0.203 | 0.231 | 0.204 | 0.213 | 0.197 | 0.205 | 0.197 | 0.207 | 0.211 | 0.226 | 0.252 | 0.195 | 0.176 | RF
A |  | L | 0.236 | 0.222 | 0.2 | 0.213 | 0.236 | 0.233 | 0.228 | 0.22 | 0.229 | 0.195 | 0.207 | 0.212 | 0.335 | 0.2 | 0.211 | 0.21 | 0.211 | 0.202 | 0.239 | 0.205 | 0.197 | 0.203 | 0.192 | 0.213 | 0.221 | 0.207 | 0.199 | 0.183 | 0.192 | 0.17 | 0.202 | 0.18 | 0.129 | 0.202 | 0.185 | 0.202 | 0.201 | 0.186 | 0.208 | 0.201 | 0.219 | 0.212 | 0.167 | 0.219 | 0.225 | 0.206 | 0.219 | 0.285 | 0.293 | 0.192 | 0.195 | 0.198 | 0.181 | 0.161 | 0.176 | 0.166 | 0.177 | 0.197 | 0.207 | 0.203 | 0.203 | 0.207 | 0.185 | 0.21 | 0.242 | 0.261 | 0.189 | 0.204 | 0.261
0.083 | +13 FT 6 IN | C | 0.245 | 0.212 | 0.227 | 0.214 | 0.233 | 0.234 | 0.234 | 0.217 | 0.232 | 0.214 | 0.192 | 0.219 | 0.335 | 0.202 | 0.225 | 0.198 | 0.216 | 0.202 | 0.233 | 0.214 | 0.207 | 0.198 | 0.196 | 0.198 | 0.208 | 0.188 | 0.204 | 0.173 | 0.189 | 0.188 | 0.202 | 0.206 | 0.196 | 0.213 | 0.201 | 0.208 | 0.22 | 0.198 | 0.194 | 0.187 | 0.176 | 0.199 | 0.193 | 0.161 | 0.197 | 0.175 | 0.197 | 0.301 | 0.282 | 0.19 | 0.191 | 0.199 | 0.187 | 0.177 | 0.196 | 0.194 | 0.168 | 0.218 | 0.221 | 0.213 | 0.18 | 0.211 | 0.201 | 0.203 | 0.248 | 0.279 | 0.225 | 0.193 | 0.268
|  | R | 0.231 | 0.205 | 0.218 | 0.229 | 0.232 | 0.226 | 0.22 | 0.222 | 0.23 | 0.232 | 0.22 | 0.232 | 0.314 | 0.206 | 0.217 | 0.207 | 0.203 | 0.206 | 0.237 | 0.225 | 0.211 | 0.217 | 0.203 | 0.194 | 0.217 | 0.214 | 0.212 | 0.193 | 0.173 | 0.194 | 0.191 | 0.182 | 0.188 | 0.211 | 0.19 | 0.204 | 0.207 | 0.19 | 0.18 | 0.16 | 0.218 | 0.181 | 0.185 | 0.214 | 0.188 | 0.176 | 0.186 | 0.301 | 0.289 | 0.159 | 0.18 | 0.198 | 0.169 | 0.179 | 0.208 | 0.171 | 0.196 | 0.207 | 0.216 | 0.2 | 0.206 | 0.199 | 0.198 | 0.196 | 0.248 | 0.279 | 0.216 | 0.222 | 0.255
A |  | L | 0.234 | 0.218 | 0.236 | 0.232 | 0.23 | 0.226 | 0.229 | 0.238 | 0.217 | 0.235 | 0.216 | 0.21 | 0.327 | 0.185 | 0.212 | 0.194 | 0.194 | 0.195 | 0.214 | 0.203 | 0.218 | 0.165 | 0.207 | 0.194 | 0.198 | 0.17 | 0.186 | 0.205 | 0.205 | 0.176 | 0.18 | 0.204 | 0.185 | 0.21 | 0.214 | 0.211 | 0.178 | 0.191 | 0.168 | 0.191 | 0.165 | 0.223 | 0.17 | 0.143 | 0.196 | 0.172 | 0.148 | 0.252 | 0.277 | 0.199 | 0.192 | 0.139 | 0.165 | 0.209 | 0.179 | 0.214 | 0.195 | 0.212 | 0.181 | 0.215 | 0.208 | 0.229 | 0.212 | 0.226 | 0.266 | 0.281 | 0.208 | 0.225 | 0.24
0.083 | +12 FT | C | 0.224 | 0.216 | 0.236 | 0.209 | 0.22 | 0.239 | 0.234 | 0.225 | 0.221 | 0.231 | 0.223 | 0.202 | 0.332 | 0.181 | 0.216 | 0.218 | 0.195 | 0.199 | 0.191 | 0.189 | 0.205 | 0.19 | 0.195 | 0.211 | 0.192 | 0.173 | 0.196 | 0.183 | 0.212 | 0.175 | 0.176 | 0.189 | 0.208 | 0.211 | 0.218 | 0.205 | 0.201 | 0.205 | 0.186 | 0.173 | 0.161 | 0.153 | 0.174 | 0.158 | 0.15 | 0.184 | 0.164 | 0.266 | 0.267 | 0.213 | 0.22 | 0.161 | 0.191 | 0.183 | 0.186 | 0.189 | 0.189 | 0.208 | 0.213 | 0.221 | 0.216 | 0.222 | 0.199 | 0.212 | 0.254 | 0.255 | 0.215 | 0.213 | 0.22
|  | R | 0.218 | 0.219 | 0.233 | 0.232 | 0.204 | 0.217 | 0.231 | 0.218 | 0.215 | 0.237 | 0.211 | 0.209 | 0.331 | 0.178 | 0.22 | 0.217 | 0.214 | 0.213 | 0.182 | 0.206 | 0.193 | 0.176 | 0.191 | 0.195 | 0.176 | 0.185 | 0.176 | 0.195 | 0.209 | 0.191 | 0.197 | 0.201 | 0.2 | 0.213 | 0.224 | 0.184 | 0.203 | 0.199 | 0.189 | 0.21 | 0.218 | 0.177 | 0.176 | 0.169 | 0.167 | 0.187 | 0.167 | 0.269 | 0.293 | 0.2 | 0.17 | 0.158 | 0.203 | 0.19 | 0.176 | 0.198 | 0.226 | 0.208 | 0.207 | 0.225 | 0.211 | 0.225 | 0.215 | 0.23 | 0.247 | 0.253 | 0.216 | 0.217 | 0.204
A | POSITION 'A' | L | 2: 0.203; 3: 0.213; 4: 0.22; 5: 0.198; 65: 0.249; 66: 0.256; 67: 0.211; 68: 0.203
0.083 | OF THE | C | 2: 0.202; 3: 0.215; 4: 0.198; 5: 0.203; 65: 0.235; 66: 0.259; 67: 0.211; 68: 0.195
| OB PORTS | R | 2: 0.204; 3: 0.222; 4: 0.211; 5: 0.207; 65: 0.244; 66: 0.257; 67: 0.202; 68: 0.212
A | POSITION 'B' | L | 2: 0.198; 3: 0.204; 4: 0.206; 5: 0.223; 65: 0.236; 66: 0.256; 67: 0.207; 68: 0.2
0.083 | OF THE | C | 2: 0.193; 3: 0.209; 4: 0.201; 5: 0.227; 65: 0.234; 66: 0.257; 67: 0.201; 68: 0.189
| OB PORTS | R | 2: 0.2; 3: 0.227; 4: 0.216; 5: 0.215; 65: 0.243; 66: 0.258; 67: 0.195; 68: 0.201
A | POSITION 'C' | L | 2: 0.201; 3: 0.215; 4: 0.195; 5: 0.215; 65: 0.237; 66: 0.244; 67: 0.216; 68: 0.188
0.083 | OF THE | C | 2: 0.196; 3: 0.209; 4: 0.213; 5: 0.221; 65: 0.253; 66: 0.251; 67: 0.208; 68: 0.207
| OB PORTS | R | 2: 0.195; 3: 0.219; 4: 0.217; 5: 0.206; 65: 0.245; 66: 0.263; 67: 0.208; 68: 0.216
A |  | L | 0.233 | 0.218 | 0.2 | 0.225 | 0.232 | 0.218 | 0.227 | 0.207 | 0.209 | 0.204 | 0.207 | 0.219 | 0.32 | 0.071 | 0.216 | 0.195 | 0.183 | 0.195 | 0.195 | 0.181 | 0.189 | 0.178 | 0.134 | 0.166 | 0.223 | 0.205 | 0.205 | 0.167 | 0.15 | 0.175 | 0.178 | 0.182 | 0.181 | 0.211 | 0.22 | 0.231 | 0.209 | 0.187 | 0.198 | 0.206 | 0.127 | 0.187 | 0.153 | 0.249 | 0.174 | 0.174 | 0.151 | 0.306 | 0.256 | 0.167 | 0.225 | 0.206 | 0.134 | 0.204 | 0.172 | 0.184 | 0.228 | 0.206 | 0.18 | 0.207 | 0.212 | 0.192 | 0.206 | 0.225 | 0.27 | 0.252 | 0.195 | 0.203 | 0.265
0.083 | +10 FT 6 IN | C | 0.225 | 0.211 | 0.197 | 0.233 | 0.215 | 0.22 | 0.225 | 0.203 | 0.212 | 0.207 | 0.221 | 0.219 | 0.305 | 0.202 | 0.21 | 0.196 | 0.191 | 0.23 | 0.189 | 0.172 | 0.187 | 0.195 | 0.186 | 0.176 | 0.167 | 0.18 | 0.194 | 0.176 | 0.198 | 0.161 | 0.178 | 0.198 | 0.2 | 0.207 | 0.206 | 0.236 | 0.193 | 0.187 | 0.147 | 0.149 | 0.153 | 0.161 | 0.169 | 0.246 | 0.152 | 0.173 | 0.15 | 0.274 | 0.228 | 0.177 | 0.181 | 0.172 | 0.18 | 0.181 | 0.229 | 0.22 | 0.217 | 0.209 | 0.193 | 0.202 | 0.212 | 0.208 | 0.211 | 0.209 | 0.265 | 0.28 | 0.193 | 0.207 | 0.243
|  | R | 0.225 | 0.22 | 0.209 | 0.222 | 0.21 | 0.224 | 0.219 | 0.216 | 0.203 | 0.206 | 0.221 | 0.211 | 0.294 | 0.213 | 0.237 | 0.2 | 0.179 | 0.199 | 0.189 | 0.225 | 0.188 | 0.195 | 0.177 | 0.194 | 0.183 | 0.186 | 0.169 | 0.179 | 0.172 | 0.165 | 0.213 | 0.156 | 0.209 | 0.195 | 0.224 | 0.236 | 0.199 | 0.172 | 0.115 | 0.163 | 0.156 | 0.152 | 0.246 | 0.241 | 0.167 | 0.147 | 0.161 | 0.262 | 0.224 | 0.15 | 0.175 | 0.19 | 0.178 | 0.148 | 0.192 | 0.207 | 0.184 | 0.197 | 0.2 | 0.206 | 0.209 | 0.204 | 0.204 | 0.219 | 0.273 | 0.239 | 0.199 | 0.21 | 0.265
A |  | L | 0.182 | 0.208 | 0.203 | 0.21 | 0.227 | 0.216 | 0.214 | 0.199 | 0.214 | 0.2 | 0.216 | 0.191 | 0.316 | 0.186 | 0.159 | 0.19 | 0.183 | 0.168 | 0.197 | 0.174 | 0.195 | 0.136 | 0.221 | 0.169 | 0.206 | 0.217 | 0.188 | 0.192 | 0.198 | 0.197 | 0.202 | 0.176 | 0.184 | 0.239 | 0.205 | 0.205 | 0.149 | 0.151 | 0.177 | 0.179 | 0.134 | 0.191 | 0.192 | 0.185 | 0.185 | 0.148 | 0.208 | 0.288 | 0.204 | 0.147 | 0.166 | 0.142 | 0.175 | 0.189 | 0.184 | 0.218 | 0.21 | 0.205 | 0.205 | 0.198 | 0.217 | 0.201 | 0.226 | 0.23 | 0.25 | 0.251 | 0.226 | 0.197 | 0.277
0.083 | +9 FT | C | 0.208 | 0.195 | 0.194 | 0.217 | 0.207 | 0.212 | 0.208 | 0.193 | 0.201 | 0.194 | 0.208 | 0.2 | 0.316 | 0.18 | 0.171 | 0.209 | 0.211 | 0.203 | 0.178 | 0.168 | 0.187 | 0.152 | 0.228 | 0.177 | 0.185 | 0.184 | 0.174 | 0.201 | 0.181 | 0.196 | 0.163 | 0.191 | 0.184 | 0.183 | 0.214 | 0.206 | 0.156 | 0.183 | 0.156 | 0.164 | 0.155 | 0.201 | 0.15 | 0.242 | 0.24 | 0.193 | 0.175 | 0.274 | 0.218 | 0.179 | 0.176 | 0.16 | 0.186 | 0.18 | 0.184 | 0.211 | 0.194 | 0.208 | 0.191 | 0.218 | 0.214 | 0.213 | 0.226 | 0.217 | 0.245 | 0.255 | 0.233 | 0.206 | 0.275
|  | R | 0.214 | 0.197 | 0.206 | 0.22 | 0.238 | 0.21 | 0.211 | 0.195 | 0.211 | 0.205 | 0.212 | 0.198 | 0.305 | 0.188 | 0.184 | 0.202 | 0.195 | 0.194 | 0.19 | 0.163 | 0.184 | 0.178 | 0.132 | 0.16 | 0.159 | 0.197 | 0.189 | 0.201 | 0.203 | 0.198 | 0.19 | 0.202 | 0.188 | 0.188 | 0.217 | 0.213 | 0.14 | 0.173 | 0.185 | 0.153 | 0.151 | 0.203 | 0.164 | 0.184 | 0.207 | 0.181 | 0.148 | 0.282 | 0.198 | 0.136 | 0.181 | 0.161 | 0.164 | 0.172 | 0.191 | 0.212 | 0.191 | 0.204 | 0.203 | 0.211 | 0.194 | 0.185 | 0.224 | 0.209 | 0.26 | 0.278 | 0.237 | 0.212 | 0.27
A | POSITION 'A' | L | 33: 0.191; 34: 0.243; 35: 0.203; 36: 0.19; 37: 0.206; 38: 0.193
0.083 | OF THE | C | 33: 0.2; 34: 0.203; 35: 0.184; 36: 0.206; 37: 0.191; 38: 0.196
| OSCILLATOR | R | 33: 0.18; 34: 0.21; 35: 0.194; 36: 0.206; 37: 0.179; 38: 0.185
A | POSITION 'B' | L | 33: 0.169; 34: 0.201; 35: 0.224; 36: 0.24; 37: 0.195; 38: 0.187
0.083 | OF THE | C | 33: 0.177; 34: 0.2; 35: 0.217; 36: 0.23; 37: 0.179; 38: 0.179
| OSCILLATOR | R | 33: 0.188; 34: 0.197; 35: 0.21; 36: 0.201; 37: 0.175; 38: 0.186
A | POSITION 'C' | L | 33: 0.192; 34: 0.177; 35: 0.205; 36: 0.222; 37: 0.184; 38: 0.188
0.083 | OF THE | C | 33: 0.192; 34: 0.198; 35: 0.217; 36: 0.202; 37: 0.201; 38: 0.182
| OSCILLATOR | R | 33: 0.19; 34: 0.207; 35: 0.22; 36: 0.229; 37: 0.211; 38: 0.192
A | POSITION 'D' | L | 33: 0.159; 34: 0.19; 35: 0.218; 36: 0.204; 37: 0.223; 38: 0.174
0.083 | OF THE | C | 33: 0.169; 34: 0.182; 35: 0.196; 36: 0.22; 37: 0.191; 38: 0.185
| OSCILLATOR | R | 33: 0.198; 34: 0.225; 35: 0.192; 36: 0.222; 37: 0.189; 38: 0.161
A | POSITION 'E' | L | 33: 0.159; 34: 0.208; 35: 0.216; 36: 0.202; 37: 0.198; 38: 0.177
0.083 | OF THE | C | 33: 0.169; 34: 0.173; 35: 0.212; 36: 0.196; 37: 0.22; 38: 0.205
| OSCILLATOR | R | 33: 0.18; 34: 0.231; 35: 0.219; 36: 0.215; 37: 0.212; 38: 0.217
A |  | L | 0.213 | 0.198 | 0.22 | 0.216 | 0.226 | 0.228 | 0.22 | 0.224 | 0.211 | 0.183 | 0.195 | 0.207 | 0.31 | 0.199 | 0.183 | 0.175 | 0.215 | 0.211 | 0.176 | 0.179 | 0.173 | 0.171 | 0.216 | 0.203 | 0.188 | 0.151 | 0.151 | 0.196 | 0.186 | 0.193 | 0.193 | 0.173 | 0.18 | 0.179 | 0.181 | 0.16 | 0.193 | 0.182 | 0.179 | 0.175 | 0.195 | 0.181 | 0.172 | 0.2 | 0.198 | 0.186 | 0.128 | 0.274 | 0.275 | 0.173 | 0.198 | 0.16 | 0.165 | 0.204 | 0.184 | 0.214 | 0.201 | 0.253 | 0.206 | 0.199 | 0.192 | 0.206 | 0.19 | 0.242 | 0.236 | 0.229 | 0.21 | 0.185 | 0.279
0.083 | +7 FT 6 IN | C | 0.181 | 0.211 | 0.218 | 0.225 | 0.204 | 0.218 | 0.211 | 0.231 | 0.205 | 0.201 | 0.198 | 0.182 | 0.224 | 0.202 | 0.198 | 0.186 | 0.189 | 0.194 | 0.195 | 0.193 | 0.175 | 0.149 | 0.199 | 0.161 | 0.171 | 0.168 | 0.177 | 0.226 | 0.196 | 0.177 | 0.173 | 0.126 | 0.15 | 0.187 | 0.177 | 0.161 | 0.199 | 0.183 | 0.191 | 0.178 | 0.181 | 0.184 | 0.172 | 0.182 | 0.173 | 0.187 | 0.156 | 0.296 | 0.3 | 0.196 | 0.194 | 0.233 | 0.188 | 0.209 | 0.214 | 0.207 | 0.205 | 0.221 | 0.196 | 0.203 | 0.198 | 0.214 | 0.195 | 0.194 | 0.248 | 0.223 | 0.201 | 0.198 | 0.232
|  | R | 0.223 | 0.2 | 0.21 | 0.196 | 0.209 | 0.193 | 0.198 | 0.232 | 0.209 | 0.19 | 0.204 | 0.18 | 0.31 | 0.184 | 0.176 | 0.179 | 0.175 | 0.186 | 0.164 | 0.163 | 0.163 | 0.156 | 0.209 | 0.203 | 0.173 | 0.218 | 0.221 | 0.213 | 0.196 | 0.228 | 0.168 | 0.149 | 0.143 | 0.174 | 0.197 | 0.139 | 0.174 | 0.152 | 0.203 | 0.175 | 0.189 | 0.185 | 0.182 | 0.186 | 0.192 | 0.183 | 0.178 | 0.279 | 0.309 | 0.182 | 0.194 | 0.197 | 0.198 | 0.205 | 0.213 | 0.202 | 0.217 | 0.21 | 0.23 | 0.204 | 0.185 | 0.204 | 0.188 | 0.193 | 0.243 | 0.234 | 0.183 | 0.194 | 0.223
A |  | L | 0.201 | 0.223 | 0.21 | 0.216 | 0.206 | 0.214 | 0.214 | 0.202 | 0.202 | 0.199 | 0.208 | 0.173 | 0.262 | 0.203 | 0.178 | 0.164 | 0.163 | 0.156 | 0.175 | 0.18 | 0.155 | 0.194 | 0.212 | 0.151 | 0.184 | 0.197 | 0.209 | 0.22 | 0.228 | 0.217 | 0.207 | 0.216 | 0.155 | 0.204 | 0.161 | 0.209 | 0.174 | 0.185 | 0.202 | 0.204 | 0.194 | 0.191 | 0.184 | 0.205 | 0.201 | 0.206 | 0.205 | 0.307 | 0.31 | 0.209 | 0.212 | 0.204 | 0.214 | 0.192 | 0.21 | 0.22 | 0.226 | 0.21 | 0.209 | 0.213 | 0.218 | 0.21 | 0.221 | 0.211 | 0.253 | 0.259 | 0.219 | 0.224 | 0.247
0.083 | +6 FT | C | 0.213 | 0.209 | 0.221 | 0.196 | 0.219 | 0.215 | 0.205 | 0.219 | 0.195 | 0.206 | 0.193 | 0.178 | 0.283 | 0.197 | 0.192 | 0.166 | 0.184 | 0.19 | 0.17 | 0.164 | 0.186 | 0.153 | 0.192 | 0.15 | 0.161 | 0.194 | 0.204 | 0.227 | 0.224 | 0.222 | 0.218 | 0.196 | 0.165 | 0.186 | 0.161 | 0.199 | 0.19 | 0.201 | 0.208 | 0.207 | 0.216 | 0.196 | 0.195 | 0.207 | 0.207 | 0.21 | 0.209 | 0.301 | 0.289 | 0.207 | 0.212 | 0.218 | 0.215 | 0.203 | 0.213 | 0.213 | 0.217 | 0.209 | 0.216 | 0.211 | 0.2 | 0.22 | 0.218 | 0.212 | 0.256 | 0.244 | 0.222 | 0.199 | 0.264
|  | R | 0.22 | 0.206 | 0.215 | 0.201 | 0.218 | 0.187 | 0.195 | 0.211 | 0.2 | 0.207 | 0.214 | 0.194 | 0.294 | 0.187 | 0.184 | 0.177 | 0.161 | 0.155 | 0.199 | 0.122 | 0.163 | 0.144 | 0.166 | 0.163 | 0.142 | 0.21 | 0.205 | 0.222 | 0.228 | 0.221 | 0.201 | 0.192 | 0.149 | 0.198 | 0.175 | 0.188 | 0.202 | 0.176 | 0.209 | 0.217 | 0.181 | 0.202 | 0.191 | 0.202 | 0.213 | 0.203 | 0.201 | 0.291 | 0.298 | 0.209 | 0.21 | 0.22 | 0.223 | 0.211 | 0.209 | 0.234 | 0.22 | 0.223 | 0.22 | 0.226 | 0.205 | 0.23 | 0.212 | 0.227 | 0.242 | 0.245 | 0.215 | 0.203 | 0.233
A |  | L | 0.212 | 0.215 | 0.233 | 0.216 | 0.226 | 0.213 | 0.206 | 0.238 | 0.205 | 0.193 | 0.199 | 0.172 | 0.305 | 0.211 | 0.17 | 0.215 | 0.187 | 0.184 | 0.143 | 0.17 | 0.191 | 0.179 | 0.205 | 0.142 | 0.173 | 0.192 | 0.203 | 0.219 | 0.221 | 0.217 | 0.187 | 0.181 | 0.185 | 0.181 | 0.21 | 0.169 | 0.2 | 0.203 | 0.208 | 0.215 | 0.192 | 0.208 | 0.193 | 0.197 | 0.206 | 0.202 | 0.215 | 0.231 | 0.284 | 0.195 | 0.206 | 0.194 | 0.202 | 0.206 | 0.217 | 0.199 | 0.202 | 0.216 | 0.205 | 0.219 | 0.205 | 0.2 | 0.211 | 0.194 | 0.216 | 0.226 | 0.196 | 0.206 | 0.249
0.083 | +4 FT 6 IN | C | 0.206 | 0.216 | 0.219 | 0.219 | 0.201 | 0.21 | 0.211 | 0.207 | 0.206 | 0.21 | 0.206 | 0.166 | 0.308 | 0.21 | 0.19 | 0.164 | 0.191 | 0.189 | 0.162 | 0.198 | 0.201 | 0.182 | 0.171 | 0.178 | 0.146 | 0.201 | 0.213 | 0.216 | 0.219 | 0.214 | 0.2 | 0.197 | 0.202 | 0.205 | 0.202 | 0.209 | 0.207 | 0.203 | 0.207 | 0.207 | 0.202 | 0.206 | 0.202 | 0.191 | 0.204 | 0.203 | 0.203 | 0.26 | 0.25 | 0.178 | 0.199 | 0.225 | 0.2 | 0.21 | 0.211 | 0.215 | 0.201 | 0.212 | 0.205 | 0.2 | 0.209 | 0.207 | 0.2 | 0.179 | 0.247 | 0.199 | 0.226 | 0.212 | 0.244
|  | R | 0.194 | 0.221 | 0.218 | 0.219 | 0.208 | 0.199 | 0.209 | 0.204 | 0.206 | 0.203 | 0.199 | 0.177 | 0.312 | 0.207 | 0.191 | 0.174 | 0.189 | 0.154 | 0.156 | 0.221 | 0.187 | 0.193 | 0.16 | 0.157 | 0.18 | 0.205 | 0.218 | 0.214 | 0.226 | 0.204 | 0.197 | 0.204 | 0.208 | 0.203 | 0.206 | 0.212 | 0.207 | 0.21 | 0.212 | 0.211 | 0.204 | 0.207 | 0.2 | 0.191 | 0.205 | 0.206 | 0.203 | 0.249 | 0.262 | 0.185 | 0.218 | 0.198 | 0.206 | 0.209 | 0.216 | 0.214 | 0.216 | 0.196 | 0.218 | 0.211 | 0.211 | 0.237 | 0.197 | 0.196 | 0.264 | 0.249 | 0.205 | 0.189 | 0.228
A |  | L | 0.199 | 0.201 | 0.226 | 0.229 | 0.187 | 0.22 | 0.201 | 0.215 | 0.202 | 0.213 | 0.197 | 0.196 | 0.315 | 0.223 | 0.204 | 0.22 | 0.182 | 0.193 | 0.206 | 0.172 | 0.19 | 0.196 | 0.186 | 0.188 | 0.177 | 0.213 | 0.162 | 0.193 | 0.167 | 0.184 | 0.198 | 0.192 | 0.203 | 0.208 | 0.212 | 0.211 | 0.208 | 0.204 | 0.222 | 0.214 | 0.211 | 0.229 | 0.195 | 0.214 | 0.199 | 0.191 | 0.206 | 0.262 | 0.241 | 0.209 | 0.186 | 0.208 | 0.208 | 0.215 | 0.205 | 0.234 | 0.206 | 0.203 | 0.202 | 0.204 | 0.212 | 0.23 | 0.203 | 0.189 | 0.228 | 0.251 | 0.208 | 0.206 | 0.279
0.083 | +3 FT | C | 0.206 | 0.183 | 0.214 | 0.227 | 0.208 | 0.218 | 0.212 | 0.218 | 0.218 | 0.215 | 0.199 | 0.21 | 0.317 | 0.22 | 0.214 | 0.201 | 0.193 | 0.198 | 0.169 | 0.189 | 0.197 | 0.207 | 0.196 | 0.179 | 0.19 | 0.183 | 0.2 | 0.204 | 0.164 | 0.213 | 0.186 | 0.14 | 0.209 | 0.211 | 0.211 | 0.207 | 0.216 | 0.21 | 0.217 | 0.214 | 0.201 | 0.185 | 0.2 | 0.161 | 0.186 | 0.18 | 0.18 | 0.209 | 0.218 | 0.197 | 0.199 | 0.195 | 0.216 | 0.203 | 0.202 | 0.209 | 0.203 | 0.21 | 0.207 | 0.208 | 0.208 | 0.214 | 0.205 | 0.195 | 0.242 | 0.249 | 0.203 | 0.213 | 0.24
|  | R | 0.188 | 0.216 | 0.23 | 0.224 | 0.222 | 0.214 | 0.202 | 0.219 | 0.231 | 0.218 | 0.203 | 0.202 | 0.315 | 0.214 | 0.224 | 0.2 | 0.164 | 0.204 | 0.19 | 0.204 | 0.195 | 0.2 | 0.19 | 0.179 | 0.201 | 0.202 | 0.212 | 0.191 | 0.182 | 0.212 | 0.195 | 0.207 | 0.216 | 0.206 | 0.216 | 0.21 | 0.212 | 0.2 | 0.209 | 0.2 | 0.198 | 0.209 | 0.183 | 0.175 | 0.198 | 0.199 | 0.165 | 0.224 | 0.215 | 0.224 | 0.187 | 0.21 | 0.215 | 0.183 | 0.187 | 0.206 | 0.207 | 0.209 | 0.215 | 0.212 | 0.2 | 0.235 | 0.203 | 0.194 | 0.222 | 0.23 | 0.21 | 0.199 | 0.258
A |  | L | 0.219 | 0.216 | 0.207 | 0.217 | 0.208 | 0.237 | 0.231 | 0.238 | 0.196 | 0.202 | 0.194 | 0.219 | 0.324 | 0.236 | 0.183 | 0.18 | 0.18 | 0.192 | 0.202 | 0.219 | 0.215 | 0.225 | 0.215 | 0.203 | 0.207 | 0.204 | 0.209 | 0.203 | 0.203 | 0.19 | 0.187 | 0.219 | 0.179 | 0.216 | 0.181 | 0.205 | 0.208 | 0.215 | 0.213 | 0.201 | 0.196 | 0.187 | 0.177 | 0.199 | 0.197 | 0.189 | 0.192 | 0.293 | 0.29 | 0.152 | 0.2 | 0.191 | 0.176 | 0.19 | 0.184 | 0.19 | 0.198 | 0.17 | 0.212 | 0.215 | 0.212 | 0.207 | 0.2 | 0.241 | 0.153 | 0.168 | 0.229 | 0.211 | 0.243
0.083 | +1 FT 6 IN | C | 0.202 | 0.186 | 0.209 | 0.214 | 0.211 | 0.205 | 0.215 | 0.219 | 0.216 | 0.218 | 0.226 | 0.217 | 0.325 | 0.197 | 0.186 | 0.198 | 0.204 | 0.195 | 0.207 | 0.21 | 0.217 | 0.223 | 0.217 | 0.21 | 0.213 | 0.209 | 0.216 | 0.2 | 0.205 | 0.183 | 0.202 | 0.196 | 0.211 | 0.197 | 0.2 | 0.183 | 0.187 | 0.212 | 0.219 | 0.202 | 0.194 | 0.172 | 0.181 | 0.178 | 0.191 | 0.161 | 0.173 | 0.272 | 0.28 | 0.192 | 0.195 | 0.195 | 0.204 | 0.195 | 0.189 | 0.184 | 0.212 | 0.19 | 0.204 | 0.191 | 0.211 | 0.216 | 0.239 | 0.224 | 0.159 | 0.183 | 0.229 | 0.181 | 0.241
|  | R | 0.224 | 0.198 | 0.211 | 0.214 | 0.194 | 0.201 | 0.215 | 0.218 | 0.228 | 0.203 | 0.215 | 0.216 | 0.317 | 0.183 | 0.209 | 0.188 | 0.206 | 0.205 | 0.211 | 0.197 | 0.205 | 0.221 | 0.216 | 0.219 | 0.204 | 0.211 | 0.215 | 0.195 | 0.199 | 0.193 | 0.201 | 0.204 | 0.214 | 0.184 | 0.19 | 0.184 | 0.184 | 0.208 | 0.191 | 0.201 | 0.18 | 0.163 | 0.171 | 0.166 | 0.164 | 0.175 | 0.15 | 0.268 | 0.288 | 0.171 | 0.215 | 0.162 | 0.188 | 0.198 | 0.188 | 0.202 | 0.218 | 0.198 | 0.211 | 0.224 | 0.216 | 0.22 | 0.2 | 0.221 | 0.193 | 0.192 | 0.198 | 0.237 | 0.234
A |  | L | 0.184 | 0.172 | 0.168 | 0.228 | 0.242 | 0.216 | 0.194 | 0.161 | 0.188 | 0.196 | 0.176 | 0.199 | 0.328 | 0.228 | 0.201 | 0.208 | 0.174 | 0.184 | 0.201 | 0.228 | 0.23 | 0.218 | 0.203 | 0.208 | 0.206 | 0.177 | 0.196 | 0.195 | 0.17 | 0.132 | 0.2 | 0.221 | 0.231 | 0.226 | 0.196 | 0.183 | 0.205 | 0.215 | 0.236 | 0.231 | 0.231 | 0.196 | 0.197 | 0.231 | 0.219 | 0.143 | 0.171 | 0.284 | 0.28 | 0.172 | 0.146 | 0.233 | 0.182 | 0.186 | 0.216 | 0.224 | 0.229 | 0.226 | 0.208 | 0.219 | 0.197 | 0.223 | 0.199 | 0.266 | 0.254 | 0.186 | 0.233 | 0.187 | 0.314
0.083 | 0 REFERENCE | C | 0.179 | 0.162 | 0.162 | 0.242 | 0.234 | 0.212 | 0.207 | 0.17 | 0.186 | 0.228 | 0.203 | 0.209 | 0.34 | 0.179 | 0.209 | 0.205 | 0.169 | 0.188 | 0.183 | 0.227 | 0.246 | 0.24 | 0.187 | 0.205 | 0.174 | 0.175 | 0.195 | 0.153 | 0.17 | 0.192 | 0.224 | 0.226 | 0.229 | 0.231 | 0.184 | 0.171 | 0.202 | 0.208 | 0.237 | 0.233 | 0.242 | 0.161 | 0.178 | 0.151 | 0.16 | 0.153 | 0.19 | 0.258 | 0.277 | 0.151 | 0.158 | 0.148 | 0.175 | 0.175 | 0.19 | 0.249 | 0.229 | 0.226 | 0.207 | 0.22 | 0.204 | 0.219 | 0.192 | 0.267 | 0.203 | 0.148 | 0.208 | 0.162 | 0.321
|  | R | 0.204 | 0.164 | 0.204 | 0.235 | 0.217 | 0.189 | 0.179 | 0.193 | 0.212 | 0.188 | 0.2 | 0.197 | 0.314 | 0.174 | 0.21 | 0.206 | 0.163 | 0.194 | 0.198 | 0.227 | 0.244 | 0.237 | 0.183 | 0.179 | 0.176 | 0.195 | 0.175 | 0.136 | 0.176 | 0.193 | 0.218 | 0.224 | 0.236 | 0.231 | 0.176 | 0.181 | 0.206 | 0.216 | 0.234 | 0.235 | 0.222 | 0.168 | 0.169 | 0.152 | 0.178 | 0.153 | 0.213 | 0.311 | 0.263 | 0.148 | 0.133 | 0.174 | 0.206 | 0.184 | 0.222 | 0.234 | 0.229 | 0.225 | 0.206 | 0.223 | 0.222 | 0.186 | 0.198 | 0.267 | 0.193 | 0.143 | 0.234 | 0.147 | 0.27
A | POSITION 'A' | L |  | 0.212 | 0.223 | 0.186 | 0.185 | 0.215 | 0.212 |  |  |  | 0.185 | 0.193 | 0.298 | 0.208 | 0.21 | 0.185 |  |  | 0.174 | 0.19 | 0.183 | 0.161 | 0.204 | 0.183 | [7 empty] | 0.244 | 0.222 | 0.198 | 0.207 |  | 0.199 | 0.199 | 0.193 | 0.188 | 0.215 | 0.201 |  |  |  | 0.216 | 0.211 | 0.299 | 0.287 | 0.176 | 0.166 |  |  | 0.192 | 0.2 | 0.179 | 0.176 | 0.204 | 0.198 |  |  | 0.194 | 0.174 | 0.212 | 0.249 | 0.224 | 0.209
0.083 | OF THE | C |  | 0.194 | 0.215 | 0.185 | 0.16 | 0.21 | 0.202 |  |  |  | 0.181 | 0.199 | 0.26 | 0.187 | 0.186 | 0.177 |  |  | 0.178 | 0.197 | 0.119 | 0.165 | 0.186 | 0.19 | [7 empty] | 0.184 | 0.201 | 0.203 | 0.188 |  | 0.192 | 0.174 | 0.187 | 0.168 | 0.203 | 0.196 |  |  |  | 0.179 | 0.218 | 0.291 | 0.28 | 0.187 | 0.192 |  |  | 0.192 | 0.177 | 0.158 | 0.187 | 0.189 | 0.187 |  |  | 0.216 | 0.177 | 0.205 | 0.156 | 0.227 | 0.207
| SECONDARIES | R |  | 0.202 | 0.215 | 0.183 | 0.183 | 0.202 | 0.203 |  |  |  | 0.179 | 0.176 | 0.281 | 0.2 | 0.201 | 0.195 |  |  | 0.189 | 0.189 | 0.138 | 0.196 | 0.192 | 0.192 | [7 empty] | 0.178 | 0.189 | 0.183 | 0.188 |  | 0.197 | 0.198 | 0.152 | 0.173 | 0.191 | 0.203 |  |  |  | 0.179 | 0.213 | 0.291 | 0.289 | 0.182 | 0.177 |  |  | 0.198 | 0.192 | 0.135 | 0.159 | 0.176 | 0.193 |  |  | 0.233 | 0.221 | 0.202 | 0.23 | 0.231 | 0.214
A | POSITION 'B' | L |  | 0.203 | 0.185 | 0.195 | 0.213 | 0.211 | 0.19 |  |  |  | 0.189 | 0.208 | 0.306 | 0.207 | 0.193 | 0.2 |  |  | 0.187 | 0.207 | 0.215 | 0.236 | 0.191 | 0.171 | [7 empty] | 0.18 | 0.203 | 0.209 | 0.197 |  | 0.178 | 0.185 | 0.219 | 0.218 | 0.219 | 0.202 |  |  |  | 0.197 | 0.198 | 0.26 | 0.305 | 0.209 | 0.21 |  |  | 0.173 | 0.189 | 0.185 | 0.197 | 0.201 | 0.226 |  |  | 0.22 | 0.22 | 0.25 | 0.237 | 0.219 | 0.21
0.083 | OF THE | C |  | 0.192 | 0.193 | 0.2 | 0.211 | 0.222 | 0.191 |  |  |  | 0.19 | 0.201 | 0.343 | 0.205 | 0.193 | 0.216 |  |  | 0.178 | 0.2 | 0.233 | 0.224 | 0.284 | 0.183 | [7 empty] | 0.204 | 0.192 | 0.213 | 0.231 |  | 0.185 | 0.191 | 0.21 | 0.209 | 0.197 | 0.201 |  |  |  | 0.181 | 0.176 | 0.273 | 0.281 | 0.188 | 0.173 |  |  | 0.15 | 0.2 | 0.218 | 0.208 | 0.217 | 0.198 |  |  | 0.207 | 0.225 | 0.24 | 0.246 | 0.213 | 0.209
| SECONDARIES | R |  | 0.201 | 0.205 | 0.224 | 0.228 | 0.211 | 0.188 |  |  |  | 0.19 | 0.198 | 0.316 | 0.203 | 0.189 | 0.184 |  |  | 0.196 | 0.208 | 0.222 | 0.219 | 0.199 | 0.203 | [7 empty] | 0.187 | 0.193 | 0.209 | 0.17 |  | 0.174 | 0.204 | 0.222 | 0.213 | 0.213 | 0.164 |  |  |  | 0.19 | 0.174 | 0.292 | 0.288 | 0.204 | 0.177 |  |  | 0.189 | 0.223 | 0.207 | 0.195 | 0.204 | 0.236 |  |  | 0.216 | 0.309 | 0.246 | 0.241 | 0.245 | 0.213
A |  | L | 0.207 | 0.197 | 0.186 | 0.179 | 0.177 | 0.22 | 0.217 | 0.223 | 0.193 | 0.233 | 0.229 | 0.236 | 0.331 | 0.225 | 0.208 | 0.195 | 0.31 | 0.195 | 0.209 | 0.2 | 0.218 | 0.219 | 0.194 | 0.206 | 0.196 | 0.194 | 0.202 | 0.193 | 0.187 | 0.224 | 0.202 | 0.207 | 0.214 | 0.222 | 0.221 | 0.158 | 0.191 | 0.203 | 0.196 | 0.205 | 0.187 | 0.188 | 0.124 | 0.181 | 0.181 | 0.138 | 0.172 | 0.301 | 0.313 | 0.177 | 0.204 | 0.182 | 0.186 | 0.172 | 0.17 | 0.222 | 0.207 | 0.22 | 0.206 | 0.201 | 0.21 | 0.227 | 0.214 | 0.219 | 0.177 | 0.155 | 0.23 | 0.222 | 0.255
0.083 | -9 IN | C | 0.191 | 0.175 | 0.178 | 0.217 | 0.176 | 0.217 | 0.211 | 0.222 | 0.196 | 0.206 | 0.23 | 0.216 | 0.315 | 0.225 | 0.208 | 0.197 | 0.198 | 0.193 | 0.216 | 0.206 | 0.208 | 0.207 | 0.2 | 0.212 | 0.199 | 0.203 | 0.194 | 0.203 | 0.181 | 0.182 | 0.172 | 0.208 | 0.176 | 0.175 | 0.147 | 0.145 | 0.205 | 0.196 | 0.185 | 0.21 | 0.197 | 0.176 | 0.113 | 0.161 | 0.17 | 0.145 | 0.172 | 0.3 | 0.318 | 0.149 | 0.17 | 0.175 | 0.166 | 0.146 | 0.161 | 0.208 | 0.208 | 0.222 | 0.207 | 0.248 | 0.218 | 0.226 | 0.214 | 0.21 | 0.174 | 0.204 | 0.232 | 0.222 | 0.205
|  | R | 0.21 | 0.186 | 0.202 | 0.216 | 0.2 | 0.221 | 0.211 | 0.222 | 0.201 | 0.203 | 0.229 | 0.213 | 0.318 | 0.223 | 0.206 | 0.191 | 0.323 | 0.196 | 0.205 | 0.199 | 0.185 | 0.232 | 0.206 | 0.202 | 0.198 | 0.204 | 0.198 | 0.172 | 0.168 | 0.213 | 0.189 | 0.181 | 0.17 | 0.185 | 0.138 | 0.15 | 0.188 | 0.188 | 0.191 | 0.187 | 0.181 | 0.186 | 0.084 | 0.147 | 0.16 | 0.155 | 0.162 | 0.31 | 0.313 | 0.162 | 0.15 | 0.162 | 0.137 | 0.158 | 0.169 | 0.212 | 0.212 | 0.224 | 0.209 | 0.244 | 0.217 | 0.233 | 0.209 | 0.19 | 0.175 | 0.142 | 0.21 | 0.221 | 0.252
A | POSITION 'C' | L |  | 0.195 | 0.185 | 0.175 | 0.17 | 0.201 | 0.201 |  |  |  | 0.196 | 0.221 | 0.271 | 0.199 | 0.198 | 0.177 |  |  | 0.197 | 0.193 | 0.183 | 0.173 | 0.2 | 0.197 | [7 empty] | 0.225 | 0.212 | 0.198 | 0.199 |  | 0.207 | 0.201 | 0.189 | 0.177 | 0.221 | 0.187 |  |  |  | 0.21 | 0.199 | 0.283 | 0.277 | 0.201 | 0.201 |  |  | 0.188 | 0.192 | 0.164 | 0.19 | 0.204 | 0.223 |  |  | 0.209 | 0.205 | 0.208 | 0.208 | 0.225 | 0.228
0.083 | OF THE | C |  | 0.194 | 0.18 | 0.162 | 0.164 | 0.212 | 0.203 |  |  |  | 0.205 | 0.213 | 0.238 | 0.211 | 0.216 | 0.177 |  |  | 0.175 | 0.203 | 0.178 | 0.176 | 0.196 | 0.197 | [7 empty] | 0.189 | 0.181 | 0.214 | 0.226 |  | 0.188 | 0.176 | 0.185 | 0.184 | 0.205 | 0.143 |  |  |  | 0.19 | 0.174 | 0.301 | 0.27 | 0.178 | 0.175 |  |  | 0.188 | 0.212 | 0.163 | 0.192 | 0.201 | 0.222 |  |  | 0.224 | 0.224 | 0.226 | 0.194 | 0.223 | 0.208
| SECONDARIES | R |  | 0.199 | 0.213 | 0.186 | 0.167 | 0.192 | 0.199 |  |  |  | 0.205 | 0.212 | 0.294 | 0.19 | 0.193 | 0.191 |  |  | 0.172 | 0.197 | 0.195 | 0.186 | 0.186 | 0.204 | [7 empty] | 0.191 | 0.195 | 0.174 | 0.173 |  | 0.201 | 0.199 | 0.196 | 0.164 | 0.166 | 0.165 |  |  |  | 0.163 | 0.149 | 0.237 | 0.284 | 0.193 | 0.201 |  |  | 0.161 | 0.154 | 0.172 | 0.186 | 0.208 | 0.211 |  |  | 0.224 | 0.201 | 0.228 | 0.239 | 0.207 | 0.214
A |  | L | 0.174 | 0.189 | 0.174 | 0.213 | 0.205 | 0.219 | 0.207 | 0.219 | 0.219 | 0.196 | 0.215 | 0.203 | 0.294 | 0.229 | 0.187 | 0.203 | 0.202 | 0.204 | 0.196 | 0.204 | 0.2 | 0.203 | 0.228 | 0.2 | 0.207 | 0.199 | 0.22 | 0.193 | 0.198 | 0.211 | 0.184 | 0.192 | 0.2 | 0.213 | 0.225 | 0.224 | 0.204 | 0.198 | 0.185 | 0.168 | 0.194 | 0.163 | 0.193 | 0.175 | 0.184 | 0.187 | 0.19 | 0.2 | 0.288 | 0.207 | 0.194 | 0.188 | 0.211 | 0.237 | 0.202 | 0.205 | 0.203 | 0.215 | 0.223 | 0.228 | 0.224 | 0.247 | 0.219 | 0.222 | 0.26 | 0.269 | 0.229 | 0.23 | 0.279
0.083 | -18 IN | C | 0.211 | 0.158 | 0.176 | 0.214 | 0.21 | 0.219 | 0.217 | 0.217 | 0.211 | 0.196 | 0.205 | 0.206 | 0.302 | 0.215 | 0.19 | 0.208 | 0.198 | 0.199 | 0.202 | 0.194 | 0.201 | 0.186 | 0.203 | 0.193 | 0.212 | 0.195 | 0.206 | 0.201 | 0.205 | 0.188 | 0.186 | 0.177 | 0.183 | 0.202 | 0.189 | 0.179 | 0.175 | 0.192 | 0.18 | 0.196 | 0.197 | 0.176 | 0.195 | 0.189 | 0.189 | 0.19 | 0.197 | 0.236 | 0.285 | 0.19 | 0.187 | 0.195 | 0.206 | 0.212 | 0.205 | 0.195 | 0.215 | 0.214 | 0.214 | 0.227 | 0.219 | 0.21 | 0.214 | 0.227 | 0.277 | 0.281 | 0.232 | 0.23 | 0.278
|  | R | 0.198 | 0.177 | 0.188 | 0.208 | 0.213 | 0.215 | 0.208 | 0.22 | 0.215 | 0.212 | 0.206 | 0.221 | 0.305 | 0.202 | 0.231 | 0.194 | 0.2 | 0.194 | 0.201 | 0.175 | 0.2 | 0.199 | 0.192 | 0.2 | 0.219 | 0.199 | 0.201 | 0.222 | 0.199 | 0.197 | 0.193 | 0.176 | 0.208 | 0.225 | 0.185 | 0.169 | 0.211 | 0.204 | 0.161 | 0.183 | 0.199 | 0.191 | 0.199 | 0.181 | 0.191 | 0.193 | 0.19 | 0.259 | 0.284 | 0.201 | 0.213 | 0.186 | 0.207 | 0.21 | 0.177 | 0.197 | 0.219 | 0.215 | 0.214 | 0.227 | 0.213 | 0.209 | 0.222 | 0.216 | 0.268 | 0.177 | 0.23 | 0.258 | 0.238
A |  | L | 0.223 | 0.222 | 0.22 | 0.221 | 0.224 | 0.22 | 0.241 | 0.205 | 0.245 | 0.238 | 0.203 | 0.238 | 0.331 | 0.216 | 0.203 | 0.211 | 0.207 | 0.214 | 0.202 | 0.207 | 0.216 | 0.211 | 0.183 | 0.197 | 0.215 | 0.214 | 0.202 | 0.193 | 0.204 | 0.198 | 0.206 | 0.187 | 0.189 | 0.184 | 0.194 | 0.161 | 0.182 | 0.202 | 0.177 | 0.192 | 0.167 | 0.176 | 0.165 | 0.202 | 0.199 | 0.175 | 0.189 | 0.288 | 0.2 | 0.211 | 0.199 | 0.217 | 0.191 | 0.211 | 0.226 | 0.213 | 0.211 | 0.227 | 0.232 | 0.225 | 0.235 | 0.21 | 0.21 | 0.225 | 0.258 | 0.252 | 0.236 | 0.185 | 0.286
0.083 | -27 IN | C | 0.208 | 0.229 | 0.22 | 0.229 | 0.221 | 0.222 | 0.223 | 0.224 | 0.244 | 0.233 | 0.202 | 0.24 | 0.323 | 0.214 | 0.202 | 0.211 | 0.21 | 0.212 | 0.209 | 0.209 | 0.214 | 0.158 | 0.194 | 0.193 | 0.213 | 0.203 | 0.204 | 0.194 | 0.203 | 0.199 | 0.207 | 0.197 | 0.195 | 0.186 | 0.2 | 0.179 | 0.197 | 0.185 | 0.19 | 0.199 | 0.202 | 0.183 | 0.187 | 0.201 | 0.211 | 0.192 | 0.31 | 0.31 | 0.293 | 0.214 | 0.205 | 0.214 | 0.201 | 0.211 | 0.212 | 0.212 | 0.211 | 0.233 | 0.233 | 0.218 | 0.23 | 0.212 | 0.21 | 0.255 | 0.273 | 0.263 | 0.235 | 0.199 | 0.287
|  | R | 0.221 | 0.214 | 0.256 | 0.23 | 0.221 | 0.225 | 0.226 | 0.213 | 0.24 | 0.231 | 0.234 | 0.201 | 0.327 | 0.215 | 0.201 | 0.201 | 0.215 | 0.21 | 0.2 | 0.206 | 0.206 | 0.2 | 0.179 | 0.192 | 0.215 | 0.201 | 0.204 | 0.193 | 0.201 | 0.186 | 0.199 | 0.177 | 0.194 | 0.216 | 0.204 | 0.184 | 0.181 | 0.196 | 0.177 | 0.178 | 0.201 | 0.184 | 0.191 | 0.201 | 0.21 | 0.18 | 0.214 | 0.268 | 0.251 | 0.217 | 0.203 | 0.215 | 0.202 | 0.207 | 0.225 | 0.226 | 0.211 | 0.221 | 0.217 | 0.221 | 0.235 | 0.202 | 0.214 | 0.25 | 0.281 | 0.254 | 0.236 | 0.214 | 0.286
A |  | L | 0.245 | 0.221 | 0.219 | 0.205 | 0.224 | 0.211 | 0.213 | 0.214 | 0.214 | 0.224 | 0.218 | 0.205 | 0.313 | 0.215 | 0.196 | 0.223 | 0.225 | 0.22 | 0.206 | 0.214 | 0.213 | 0.211 | 0.211 | 0.217 | 0.203 | 0.221 | 0.204 | 0.22 | 0.211 | 0.201 | 0.196 | 0.205 | 0.189 | 0.177 | 0.205 | 0.197 | 0.216 | 0.189 | 0.201 | 0.225 | 0.186 | 0.196 | 0.173 | 0.174 | 0.184 | 0.191 | 0.201 | 0.266 | 0.312 | 0.202 | 0.183 | 0.211 | 0.2 | 0.201 | 0.22 | 0.206 | 0.224 | 0.239 | 0.2 | 0.19 | 0.24 | 0.214 | 0.222 | 0.219 | 0.265 | 0.25 | 0.235 | 0.189 | 0.278
0.083 | -36 IN | C | 0.232 | 0.209 | 0.222 | 0.222 | 0.217 | 0.221 | 0.218 | 0.214 | 0.221 | 0.218 | 0.216 | 0.213 | 0.303 | 0.206 | 0.218 | 0.228 | 0.227 | 0.216 | 0.179 | 0.206 | 0.215 | 0.196 | 0.195 | 0.208 | 0.222 | 0.22 | 0.215 | 0.211 | 0.219 | 0.213 | 0.195 | 0.192 | 0.189 | 0.187 | 0.214 | 0.224 | 0.19 | 0.227 | 0.213 | 0.209 | 0.206 | 0.2 | 0.209 | 0.186 | 0.204 | 0.204 | 0.198 | 0.305 | 0.29 | 0.204 | 0.201 | 0.21 | 0.198 | 0.207 | 0.225 | 0.206 | 0.23 | 0.243 | 0.212 | 0.205 | 0.24 | 0.22 | 0.218 | 0.215 | 0.26 | 0.281 | 0.231 | 0.185 | 0.312
|  | R | 0.223 | 0.224 | 0.21 | 0.212 | 0.228 | 0.215 | 0.215 | 0.214 | 0.219 | 0.217 | 0.216 | 0.226 | 0.295 | 0.2 | 0.231 | 0.229 | 0.216 | 0.214 | 0.209 | 0.236 | 0.206 | 0.198 | 0.226 | 0.186 | 0.223 | 0.202 | 0.213 | 0.214 | 0.204 | 0.189 | 0.22 | 0.2 | 0.182 | 0.205 | 0.213 | 0.198 | 0.202 | 0.194 | 0.218 | 0.208 | 0.197 | 0.197 | 0.193 | 0.182 | 0.204 | 0.198 | 0.195 | 0.266 | 0.264 | 0.207 | 0.199 | 0.213 | 0.184 | 0.2 | 0.223 | 0.217 | 0.228 | 0.25 | 0.209 | 0.193 | 0.241 | 0.221 | 0.205 | 0.215 | 0.26 | 0.275 | 0.241 | 0.19 | 0.289
A |  | L | 0.226 | 0.214 | 0.195 | 0.195 | 0.229 | 0.205 | 0.215 | 0.214 | 0.208 | 0.217 | 0.212 | 0.212 | 0.32 | 0.198 | 0.209 | 0.208 | 0.203 | 0.212 | 0.229 | 0.219 | 0.216 | 0.217 | 0.234 | 0.194 | 0.228 | 0.21 | 0.213 | 0.198 | 0.186 | 0.21 | 0.201 | 0.197 | 0.195 | 0.187 | 0.195 | 0.21 | 0.204 | 0.212 | 0.208 | 0.229 | 0.216 | 0.194 | 0.209 | 0.187 | 0.221 | 0.197 | 0.237 | 0.281 | 0.203 | 0.193 | 0.207 | 0.199 | 0.207 | 0.214 | 0.225 | 0.231 | 0.219 | 0.213 | 0.21 | 0.201 | 0.223 | 0.229 | 0.209 | 0.226 | 0.273 | 0.275 | 0.267 | 0.228 | 0.251
0.083 | -45 IN | C | 0.213 | 0.213 | 0.199 | 0.227 | 0.206 | 0.218 | 0.216 | 0.21 | 0.205 | 0.237 | 0.204 | 0.215 | 0.327 | 0.242 | 0.214 | 0.196 | 0.202 | 0.196 | 0.209 | 0.2 | 0.215 | 0.201 | 0.237 | 0.201 | 0.221 | 0.21 | 0.205 | 0.204 | 0.221 | 0.218 | 0.193 | 0.2 | 0.209 | 0.208 | 0.204 | 0.208 | 0.215 | 0.214 | 0.219 | 0.212 | 0.214 | 0.197 | 0.215 | 0.196 | 0.222 | 0.205 | 0.204 | 0.283 | 0.173 | 0.198 | 0.198 | 0.204 | 0.2 | 0.222 | 0.218 | 0.187 | 0.198 | 0.211 | 0.21 | 0.217 | 0.211 | 0.209 | 0.223 | 0.194 | 0.264 | 0.272 | 0.227 | 0.229 | 0.166
|  | R | 0.213 | 0.172 | 0.23 | 0.227 | 0.206 | 0.218 | 0.215 | 0.205 | 0.237 | 0.207 | 0.212 | 0.206 | 0.322 | 0.208 | 0.212 | 0.211 | 0.226 | 0.205 | 0.207 | 0.19 | 0.201 | 0.199 | 0.234 | 0.2 | 0.221 | 0.196 | 0.2 | 0.183 | 0.188 | 0.208 | 0.225 | 0.193 | 0.214 | 0.192 | 0.189 | 0.217 | 0.217 | 0.221 | 0.224 | 0.197 | 0.183 | 0.197 | 0.194 | 0.193 | 0.214 | 0.204 | 0.196 | 0.278 | 0.17 | 0.229 | 0.204 | 0.204 | 0.191 | 0.224 | 0.231 | 0.252 | 0.216 | 0.214 | 0.206 | 0.224 | 0.232 | 0.213 | 0.223 | 0.171 | 0.258 | 0.269 | 0.23 | 0.252 | 0.263
A |  | L | 0.21 | 0.202 | 0.21 | 0.227 | 0.206 | 0.237 | 0.207 | 0.214 | 0.211 | 0.218 | 0.222 | 0.225 | 0.306 | 0.204 | 0.23 | 0.237 | 0.235 | 0.224 | 0.23 | 0.223 | 0.221 | 0.232 | 0.228 | 0.221 | 0.213 | 0.216 | 0.213 | 0.2 | 0.192 | 0.205 | 0.203 | 0.175 | 0.215 | 0.241 | 0.224 | 0.198 | 0.212 | 0.208 | 0.218 | 0.222 | 0.216 | 0.216 | 0.232 | 0.215 | 0.201 | 0.214 | 0.219 | 0.309 | 0.348 | 0.226 | 0.216 | 0.207 | 0.215 | 0.205 | 0.214 | 0.219 | 0.227 | 0.236 | 0.212 | 0.234 | 0.247 | 0.21 | 0.229 | 0.253 | 0.195 | 0.208 | 0.211 | 0.225 | 0.262
0.083 | -54 IN | C | 0.21 | 0.199 | 0.207 | 0.199 | 0.243 | 0.205 | 0.207 | 0.219 | 0.203 | 0.226 | 0.22 | 0.222 | 0.305 | 0.204 | 0.227 | 0.208 | 0.228 | 0.221 | 0.225 | 0.221 | 0.214 | 0.239 | 0.229 | 0.216 | 0.201 | 0.216 | 0.21 | 0.211 | 0.196 | 0.203 | 0.215 | 0.198 | 0.219 | 0.24 | 0.212 | 0.207 | 0.199 | 0.196 | 0.218 | 0.217 | 0.216 | 0.233 | 0.208 | 0.198 | 0.23 | 0.217 | 0.214 | 0.307 | 0.319 | 0.233 | 0.217 | 0.217 | 0.221 | 0.21 | 0.219 | 0.216 | 0.227 | 0.236 | 0.227 | 0.232 | 0.223 | 0.225 | 0.228 | 0.253 | 0.271 | 0.283 | 0.222 | 0.219 | 0.289
|  | R | 0.21 | 0.203 | 0.198 | 0.195 | 0.196 | 0.218 | 0.204 | 0.214 | 0.202 | 0.216 | 0.22 | 0.218 | 0.308 | 0.2 | 0.224 | 0.208 | 0.225 | 0.219 | 0.234 | 0.219 | 0.222 | 0.239 | 0.226 | 0.216 | 0.216 | 0.193 | 0.205 | 0.187 | 0.2 | 0.201 | 0.198 | 0.197 | 0.207 | 0.225 | 0.21 | 0.225 | 0.214 | 0.203 | 0.211 | 0.221 | 0.217 | 0.189 | 0.216 | 0.21 | 0.232 | 0.213 | 0.267 | 0.322 | 0.273 | 0.218 | 0.201 | 0.221 | 0.211 | 0.22 | 0.219 | 0.233 | 0.223 | 0.236 | 0.218 | 0.234 | 0.234 | 0.226 | 0.227 | 0.253 | 0.271 | 0.283 | 0.222 | 0.218 | 0.277
A | POSITION 'A' | L |  |  | 0.188 | 0.2 |  | 0.21 | 0.189 |  | 0.186 | 0.194 |  | 0.217 | 0.31 |  | 0.194 | 0.179 |  | 0.198 | 0.204 |  | 0.194 | 0.192 |  | 0.2 | 0.189 |  | 0.197 | 0.19 |  | 0.196 | 0.192 |  | 0.212 | 0.206 |  | 0.198 | 0.207 |  | 0.2 | 0.194 |  | 0.205 | 0.185 |  | 0.2 | 0.205 |  | 0.304 | 0.279 |  | 0.211 | 0.193 |  | 0.192 | 0.177 |  | 0.199 | 0.191 |  | 0.239 | 0.205 |  | 0.223 | 0.232 |  | 0.238 | 0.203
0.083 | OF THE | C |  |  | 0.197 | 0.211 |  | 0.206 | 0.201 |  | 0.208 | 0.206 |  | 0.215 | 0.3 |  | 0.201 | 0.187 |  | 0.208 | 0.203 |  | 0.207 | 0.209 |  | 0.214 | 0.179 |  | 0.194 | 0.193 |  | 0.181 | 0.213 |  | 0.211 | 0.226 |  | 0.201 | 0.183 |  | 0.185 | 0.215 |  | 0.196 | 0.208 |  | 0.201 | 0.213 |  | 0.292 | 0.282 |  | 0.208 | 0.205 |  | 0.193 | 0.219 |  | 0.222 | 0.201 |  | 0.211 | 0.213 |  | 0.211 | 0.23 |  | 0.262 | 0.213
| PRIMARIES | R |  |  | 0.196 | 0.216 |  | 0.202 | 0.198 |  | 0.211 | 0.192 |  | 0.204 | 0.27 |  | 0.204 | 0.199 |  | 0.198 | 0.212 |  | 0.195 | 0.196 |  | 0.212 | 0.177 |  | 0.187 | 0.204 |  | 0.179 | 0.221 |  | 0.208 | 0.209 |  | 0.195 | 0.195 |  | 0.194 | 0.22 |  | 0.202 | 0.212 |  | 0.21 | 0.211 |  | 0.299 | 0.312 |  | 0.213 | 0.218 |  | 0.183 | 0.201 |  | 0.211 | 0.227 |  | 0.217 | 0.21 |  | 0.224 | 0.216 |  | 0.264 | 0.217
A | POSITION 'B' | L |  |  | 0.192 | 0.214 |  | 0.208 | 0.2 |  | 0.184 | 0.203 |  | 0.187 | 0.306 |  | 0.198 | 0.188 |  | 0.205 | 0.192 |  | 0.204 | 0.182 |  | 0.203 | 0.188 |  | 0.179 | 0.191 |  | 0.196 | 0.193 |  | 0.19 | 0.191 |  | 0.196 | 0.21 |  | 0.203 | 0.191 |  | 0.184 | 0.205 |  | 0.209 | 0.208 |  | 0.3 | 0.289 |  | 0.216 | 0.207 |  | 0.201 | 0.215 |  | 0.221 | 0.202 |  | 0.247 | 0.213 |  | 0.225 | 0.195 |  | 0.264 | 0.218
0.083 | OF THE | C |  |  | 0.146 | 0.194 |  | 0.191 | 0.189 |  | 0.194 | 0.191 |  | 0.206 | 0.293 |  | 0.202 | 0.155 |  | 0.204 | 0.206 |  | 0.221 | 0.181 |  | 0.195 | 0.198 |  | 0.2 | 0.172 |  | 0.184 | 0.188 |  | 0.196 | 0.197 |  | 0.177 | 0.208 |  | 0.204 | 0.235 |  | 0.19 | 0.2 |  | 0.185 | 0.212 |  | 0.284 | 0.31 |  | 0.19 | 0.23 |  | 0.19 | 0.214 |  | 0.218 | 0.215 |  | 0.206 | 0.208 |  | 0.195 | 0.242 |  | 0.217 | 0.234
| PRIMARIES | R |  |  | 0.195 | 0.193 |  | 0.18 | 0.196 |  | 0.201 | 0.199 |  | 0.181 | 0.299 |  | 0.2 | 0.17 |  | 0.188 | 0.21 |  | 0.193 | 0.187 |  | 0.178 | 0.181 |  | 0.179 | 0.181 |  | 0.173 | 0.189 |  | 0.189 | 0.191 |  | 0.204 | 0.205 |  | 0.189 | 0.203 |  | 0.185 | 0.207 |  | 0.178 | 0.198 |  | 0.306 | 0.281 |  | 0.179 | 0.203 |  | 0.19 | 0.216 |  | 0.203 | 0.215 |  | 0.228 | 0.204 |  | 0.23 | 0.187 |  | 0.254 | 0.21
A | POSITION 'C' | L |  |  | 0.176 | 0.198 |  | 0.195 | 0.201 |  | 0.181 | 0.183 |  | 0.205 | 0.288 |  | 0.189 | 0.188 |  | 0.191 | 0.198 |  | 0.192 | 0.192 |  | 0.172 | 0.182 |  | 0.171 | 0.18 |  | 0.209 | 0.212 |  | 0.173 | 0.192 |  | 0.186 | 0.191 |  | 0.192 | 0.194 |  | 0.222 | 0.194 |  | 0.201 | 0.201 |  | 0.31 | 0.293 |  | 0.196 | 0.196 |  | 0.189 | 0.222 |  | 0.246 | 0.227 |  | 0.223 | 0.2 |  | 0.21 | 0.187 |  | 0.233 | 0.218
0.083 | OF THE | C |  |  | 0.157 | 0.18 |  | 0.173 | 0.2 |  | 0.167 | 0.185 |  | 0.204 | 0.291 |  | 0.185 | 0.189 |  | 0.187 | 0.198 |  | 0.201 | 0.189 |  | 0.177 | 0.175 |  | 0.201 | 0.201 |  | 0.2 | 0.197 |  | 0.202 | 0.194 |  | 0.178 | 0.196 |  | 0.206 | 0.196 |  | 0.221 | 0.186 |  | 0.195 | 0.213 |  | 0.309 | 0.293 |  | 0.199 | 0.225 |  | 0.198 | 0.209 |  | 0.218 | 0.235 |  | 0.228 | 0.22 |  | 0.216 | 0.195 |  | 0.208 | 0.211
| PRIMARIES | R |  |  | 0.197 | 0.181 |  | 0.181 | 0.199 |  | 0.203 | 0.201 |  | 0.193 | 0.309 |  | 0.201 | 0.208 |  | 0.182 | 0.218 |  | 0.208 | 0.167 |  | 0.186 | 0.17 |  | 0.196 | 0.218 |  | 0.2 | 0.191 |  | 0.21 | 0.207 |  | 0.199 | 0.186 |  | 0.223 | 0.209 |  | 0.203 | 0.199 |  | 0.222 | 0.21 |  | 0.315 | 0.3 |  | 0.19 | 0.211 |  | 0.198 | 0.222 |  | 0.22 | 0.245 |  | 0.215 | 0.209 |  | 0.229 | 0.208 |  | 0.252 | 0.201
A |  | L | 0.195 | 0.228 | 0.194 | 0.182 | 0.189 | 0.229 | 0.206 | 0.214 | 0.217 | 0.208 | 0.232 | 0.213 | 0.281 | 0.189 | 0.201 | 0.222 | 0.21 | 0.193 | 0.228 | 0.221 | 0.204 | 0.218 | 0.218 | 0.218 | 0.215 | 0.186 | 0.203 | 0.204 | 0.208 | 0.192 | 0.241 | 0.216 | 0.222 | 0.206 | 0.214 | 0.222 | 0.217 | 0.204 | 0.198 | 0.206 | 0.201 | 0.218 | 0.217 | 0.205 | 0.219 | 0.214 | 0.216 | 0.308 | 0.322 | 0.225 | 0.211 | 0.202 | 0.198 | 0.215 | 0.208 | 0.217 | 0.247 | 0.219 | 0.231 | 0.242 | 0.242 | 0.215 | 0.215 | 0.234 | 0.207 | 0.218 | 0.227 | 0.228 | 0.275
0.083 | -63 IN | C | 0.202 | 0.227 | 0.174 | 0.178 | 0.208 | 0.2 | 0.203 | 0.201 | 0.222 | 0.221 | 0.223 | 0.209 | 0.293 | 0.194 | 0.208 | 0.215 | 0.206 | 0.233 | 0.229 | 0.213 | 0.215 | 0.207 | 0.222 | 0.219 | 0.208 | 0.188 | 0.197 | 0.206 | 0.202 | 0.216 | 0.244 | 0.213 | 0.22 | 0.206 | 0.219 | 0.223 | 0.228 | 0.211 | 0.214 | 0.201 | 0.223 | 0.223 | 0.216 | 0.207 | 0.214 | 0.213 | 0.214 | 0.317 | 0.316 | 0.202 | 0.214 | 0.229 | 0.204 | 0.216 | 0.223 | 0.217 | 0.247 | 0.212 | 0.231 | 0.234 | 0.247 | 0.193 | 0.225 | 0.209 | 0.27 | 0.204 | 0.23 | 0.22 | 0.291
|  | R | 0.214 | 0.229 | 0.191 | 0.169 | 0.198 | 0.194 | 0.191 | 0.199 | 0.221 | 0.22 | 0.216 | 0.2 | 0.295 | 0.191 | 0.207 | 0.221 | 0.199 | 0.231 | 0.216 | 0.216 | 0.213 | 0.211 | 0.215 | 0.213 | 0.192 | 0.218 | 0.196 | 0.203 | 0.237 | 0.208 | 0.23 | 0.217 | 0.222 | 0.206 | 0.221 | 0.234 | 0.191 | 0.202 | 0.206 | 0.201 | 0.223 | 0.224 | 0.207 | 0.214 | 0.219 | 0.212 | 0.231 | 0.293 | 0.316 | 0.225 | 0.219 | 0.231 | 0.216 | 0.216 | 0.214 | 0.246 | 0.219 | 0.222 | 0.242 | 0.228 | 0.246 | 0.215 | 0.216 | 0.205 | 0.151 | 0.224 | 0.226 | 0.227 | 0.286
A |  | L | 0.206 | 0.226 | 0.237 | 0.171 | 0.169 | 0.179 | 0.232 | 0.195 | 0.184 | 0.198 | 0.192 | 0.211 | 0.137 | 0.196 | 0.146 | 0.206 | 0.204 | 0.2 | 0.205 | 0.218 | 0.187 | 0.235 | 0.217 | 0.208 | 0.219 | 0.234 | 0.206 | 0.216 | 0.22 | 0.231 | 0.185 | 0.207 | 0.22 | 0.231 | 0.223 | 0.218 | 0.217 | 0.2 | 0.206 | 0.182 | 0.206 | 0.223 | 0.193 | 0.213 | 0.21 | 0.221 | 0.221 | 0.285 | 0.319 | 0.205 | 0.231 | 0.217 | 0.202 | 0.223 | 0.222 | 0.209 | 0.237 | 0.233 | 0.215 | 0.219 | 0.216 | 0.209 | 0.238 | 0.223 | 0.253 | 0.223 | 0.221 | 0.248 | 0.281
0.083 | -72 IN | C | 0.213 | 0.203 | 0.195 | 0.18 | 0.191 | 0.207 | 0.204 | 0.178 | 0.212 | 0.182 | 0.203 | 0.226 | 0.172 | 0.208 | 0.219 | 0.191 | 0.222 | 0.207 | 0.219 | 0.22 | 0.198 | 0.207 | 0.239 | 0.205 | 0.211 | 0.219 | 0.201 | 0.215 | 0.213 | 0.212 | 0.21 | 0.213 | 0.209 | 0.218 | 0.197 | 0.197 | 0.199 | 0.192 | 0.208 | 0.204 | 0.184 | 0.22 | 0.19 | 0.193 | 0.177 | 0.211 | 0.202 | 0.309 | 0.28 | 0.22 | 0.217 | 0.198 | 0.2 | 0.209 | 0.208 | 0.221 | 0.208 | 0.221 | 0.2 | 0.222 | 0.23 | 0.197 | 0.215 | 0.209 | 0.263 | 0.241 | 0.218 | 0.282 | 0.261
|  | R | 0.19 | 0.199 | 0.2 | 0.162 | 0.183 | 0.185 | 0.208 | 0.223 | 0.193 | 0.181 | 0.184 | 0.201 | 0.149 | 0.186 | 0.232 | 0.204 | 0.207 | 0.207 | 0.193 | 0.17 | 0.205 | 0.212 | 0.216 | 0.187 | 0.219 | 0.203 | 0.195 | 0.201 | 0.198 | 0.197 | 0.218 | 0.189 | 0.224 | 0.213 | 0.211 | 0.226 | 0.19 | 0.213 | 0.208 | 0.206 | 0.222 | 0.196 | 0.196 | 0.203 | 0.193 | 0.216 | 0.216 | 0.215 | 0.205 | 0.202 | 0.216 | 0.208 | 0.218 | 0.217 | 0.219 | 0.216 | 0.223 | 0.226 | 0.215 | 0.225 | 0.205 | 0.188 | 0.227 | 0.205 | 0.272 | 0.243 | 0.277 | 0.249 | 0.279
A |  | L | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | 0.149 | 0.23 | 0.181 | 0.178 | 0.201 | 0.148 | 0.199 | 0.191 | 0.193 | 0.196 | 0.198 | 0.189 | 0.189 | 0.196 | 0.177 | 0.176 | 0.206 | 0.164 | 0.218 | 0.202 | 0.225 | 0.184 | 0.209 | 0.218 | 0.204 | 0.21 | 0.209 | 0.219 | 0.211 | 0.206 | 0.221 | 0.208 | 0.225 | 0.183 | 0.226 | 0.238 | 0.226 | 0.331 | 0.194 | 0.303 | 0.223 | 0.215 | 0.228 | 0.22 | 0.237 | 0.21 | 0.227 | 0.235 | 0.212 | 0.229 | 0.218 | 0.234 | 0.229 | 0.16 | 0.26 | 0.21 | 0.246 | 0.286
0.083 | -81 IN | C | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | 0.157 | 0.292 | 0.218 | 0.175 | 0.208 | 0.216 | 0.181 | 0.206 | 0.197 | 0.18 | 0.201 | 0.205 | 0.192 | 0.189 | 0.203 | 0.201 | 0.206 | 0.202 | 0.215 | 0.194 | 0.179 | 0.206 | 0.19 | 0.204 | 0.218 | 0.202 | 0.211 | 0.194 | 0.209 | 0.207 | 0.205 | 0.19 | 0.214 | 0.222 | 0.211 | 0.233 | 0.213 | 0.3 | 0.212 | 0.224 | 0.23 | 0.219 | 0.216 | 0.228 | 0.234 | 0.214 | 0.213 | 0.206 | 0.213 | 0.247 | 0.192 | 0.24 | 0.222 | 0.161 | 0.258 | 0.223 | 0.156 | 0.264
|  | R | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | 0.175 | 0.205 | 0.229 | 0.185 | 0.212 | 0.206 | 0.212 | 0.215 | 0.218 | 0.219 | 0.233 | 0.212 | 0.195 | 0.223 | 0.189 | 0.172 | 0.204 | 0.201 | 0.222 | 0.218 | 0.222 | 0.197 | 0.221 | 0.22 | 0.208 | 0.171 | 0.219 | 0.181 | 0.208 | 0.206 | 0.204 | 0.188 | 0.216 | 0.218 | 0.225 | 0.22 | 0.314 | 0.256 | 0.201 | 0.228 | 0.235 | 0.222 | 0.221 | 0.236 | 0.225 | 0.202 | 0.209 | 0.231 | 0.232 | 0.235 | 0.208 | 0.227 | 0.209 | 0.186 | 0.218 | 0.186 | 0.239 | 0.253
A |  | L | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | 0.206 | 0.226 | 0.228 | 0.229 | 0.205 | 0.199 | 0.2 | 0.202 | 0.199 | 0.175 | 0.203 | 0.184 | 0.189 | 0.184 | 0.285 | 0.257 | 0.218 | 0.211 | 0.213 | 0.228 | 0.229 | 0.232 | 0.222 | 0.235 | 0.219 | 0.223 | 0.226 | 0.214 | 0.21 | 0.183 | 0.176 | 0.216 | 0.166 | 0.178 | 0.212 | 0.259
0.083 | -90 IN | C | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | 0.193 | 0.208 | 0.179 | 0.197 | 0.22 | 0.195 | 0.207 | 0.182 | 0.192 | 0.163 | 0.188 | 0.171 | 0.18 | 0.191 | 0.279 | 0.268 | 0.159 | 0.209 | 0.207 | 0.214 | 0.181 | 0.194 | 0.227 | 0.197 | 0.191 | 0.217 | 0.218 | 0.204 | 0.196 | 0.195 | 0.19 | 0.209 | 0.212 | 0.21 | 0.201 | 0.253
|  | R | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | ST | 0.184 | 0.205 | 0.194 | 0.204 | 0.191 | 0.205 | 0.204 | 0.197 | 0.185 | 0.192 | 0.225 | 0.2 | 0.205 | 0.188 | 0.315 | 0.244 | 0.173 | 0.21 | 0.24 | 0.195 | 0.206 | 0.187 | 0.239 | 0.226 | 0.234 | 0.19 | 0.224 | 0.21 | 0.206 | 0.194 | 0.222 | 0.187 | 0.247 | 0.242 | 0.229 | 0.256
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MIN
A | 0.001-0.083 | 0.131-0.140 | 10: OUTSIDE DIAMETER:; 23: 3; 30: FUTURE PROJECTION; 67: APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | 0.084-0.100 | 0.141-0.150 | 10: TUBE MATERIAL:; 23: SA-210A1; 35: MAX. THICKNESS
| 0.101-0.110 | 0.151-0.160 | 10: NOMINAL WALL:; 23: 0.203; 35: AVG. THICKNESS |  |  | PROJECTED TUBE WALL THICKNESS - 5 YEARS
| 0.111-0.120 | 0.161-0.170 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS
| 0.121-0.130 | 0.171-0.999 | 10: MILL FLAG:; 23: 0.1; 35: STD DEV.
PROJECTION
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Retirement
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. | [70 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69
A |  | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jun 2053 | Jan 2051 | May 2055 | Nov 2053 | Nov 2047 | May 2055 | Jul 2046 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jan 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2041 | Nov 2053 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Sep 2048 | ND
+16 FT 6 IN
A |  | Year | ND | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Mar 2054 | May 2055 | Mar 2055 | May 2055 | ND | Dec 2045 | May 2055 | May 2055 | Jul 2040 | May 2055 | May 2055 | May 2055 | May 2055 | May 2045 | Jan 2053 | ND | May 2055 | May 2055 | Jun 2043 | May 2055 | May 2055 | May 2055 | Sep 2045 | May 2055 | Sep 2044 | May 2055 | Aug 2048 | May 2055 | Aug 2054 | Mar 2039 | May 2055 | May 2055 | Apr 2053 | May 2055 | Aug 2050 | May 2055 | May 2055 | May 2055 | Feb 2054 | ND | Aug 2042 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jan 2054 | Aug 2040 | ND
+15 FT
A |  | Year | ND | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Aug 2048 | Jun 2053 | Sep 2044 | May 2055 | Jul 2051 | Nov 2033 | May 2055 | Nov 2052 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2043 | Aug 2054 | May 2055 | Feb 2042 | Feb 2045 | May 2055 | Apr 2053 | May 2055 | May 2055 | May 2055 | Jan 2043 | May 2055 | May 2055 | Aug 2044 | Jun 2041 | May 2054 | Apr 2045 | Apr 2044 | May 2055 | May 2055 | May 2055 | May 2048 | May 2055 | Feb 2052 | May 2055 | May 2055 | May 2055 | Aug 2047 | May 2055 | ND
+13 FT 6 IN
A |  | Year | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | Feb 2042 | May 2055 | May 2055 | May 2055 | May 2055 | Jan 2055 | May 2055 | May 2055 | Aug 2045 | May 2055 | May 2055 | Jul 2052 | Jul 2052 | Jul 2053 | May 2055 | May 2055 | May 2055 | Sep 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2049 | May 2055 | Mar 2045 | Jul 2044 | Dec 2051 | Sep 2039 | May 2041 | May 2055 | Mar 2041 | May 2055 | May 2055 | May 2055 | Jan 2055 | Jun 2037 | Jan 2050 | May 2055 | Mar 2050 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2048
+12 FT
A | POSITION 'A' | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND
OF THE
OB PORTS
A | POSITION 'B' | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND
OF THE
OB PORTS
A | POSITION 'C' | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND
OF THE
OB PORTS
A |  | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2029 | ND | May 2055 | May 2055 | May 2055 | May 2055 | Mar 2054 | May 2055 | May 2055 | Apr 2036 | Jul 2046 | Sep 2047 | May 2055 | May 2055 | Feb 2050 | Oct 2039 | Feb 2044 | May 2055 | Jan 2041 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Dec 2050 | Oct 2033 | Oct 2043 | Nov 2035 | Mar 2046 | Oct 2044 | ND | Sep 2047 | Aug 2041 | Jul 2040 | May 2055 | May 2055 | Nov 2042 | May 2055 | May 2055 | Feb 2036 | Nov 2039 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2052 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055
+10 FT 6 IN
A |  | Year | Jan 2050 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2052 | May 2042 | May 2055 | May 2055 | Nov 2047 | May 2055 | May 2049 | May 2055 | Jun 2038 | Apr 2036 | Feb 2046 | Apr 2046 | May 2055 | Sep 2053 | May 2055 | May 2055 | May 2055 | Sep 2043 | Nov 2053 | May 2055 | May 2055 | May 2055 | May 2055 | Dec 2037 | Jan 2045 | Apr 2051 | Oct 2047 | Aug 2038 | ND | Jan 2046 | Feb 2045 | May 2055 | Jan 2040 | Aug 2042 | May 2055 | May 2048 | Jul 2037 | Jan 2053 | Jul 2040 | Sep 2049 | May 2052 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND
+9 FT
A | POSITION 'A' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Dec 2052 | May 2055 | Jun 2049 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
A | POSITION 'B' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Jun 2046 | May 2055 | May 2055 | May 2055 | Mar 2053 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
A | POSITION 'C' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | Mar 2051 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
A | POSITION 'D' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Feb 2043 | May 2055 | Dec 2053 | May 2055 | May 2055 | Dec 2051 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
A | POSITION 'E' | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Apr 2047 | Jul 2048 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
OF THE
OSCILLATOR
A |  | Year | Nov 2047 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Nov 2053 | May 2055 | May 2055 | Oct 2044 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2054 | Jul 2049 | Sep 2047 | Aug 2041 | ND | Oct 2048 | May 2055 | Sep 2045 | Aug 2042 | ND | May 2055 | May 2055 | Jul 2051 | Nov 2034 | May 2039 | Jul 2051 | May 2050 | Nov 2036 | May 2055 | Dec 2044 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | Sep 2035 | May 2055 | May 2055 | Jun 2051 | May 2055 | Jun 2040 | Jun 2048 | May 2055 | Sep 2052 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Sep 2053 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055
+7 FT 6 IN
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Dec 2051 | May 2055 | May 2055 | May 2055 | Aug 2047 | Mar 2046 | May 2043 | Feb 2049 | Jul 2034 | Aug 2047 | May 2040 | Mar 2050 | Apr 2041 | Oct 2037 | May 2055 | May 2055 | ND | ND | ND | ND | ND | Dec 2038 | May 2055 | Dec 2043 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055
+6 FT
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Aug 2040 | ND | May 2055 | Mar 2051 | Nov 2048 | May 2055 | Apr 2043 | Jan 2041 | May 2055 | ND | May 2055 | Jul 2046 | Apr 2042 | Mar 2043 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Dec 2053 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2052 | May 2055 | Jul 2053 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2053 | May 2055 | Apr 2049 | May 2055 | ND | May 2055
+4 FT 6 IN
A |  | Year | May 2055 | Feb 2048 | May 2055 | ND | Feb 2052 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | Dec 2046 | ND | Aug 2051 | Feb 2052 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jun 2041 | May 2055 | Aug 2042 | May 2055 | May 2055 | Aug 2035 | May 2055 | ND | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2044 | May 2055 | May 2055 | May 2045 | Dec 2042 | Apr 2046 | May 2055 | May 2055 | May 2055 | May 2055 | Feb 2053 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055
+3 FT
A |  | Year | May 2055 | Jun 2051 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Feb 2048 | Mar 2051 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Oct 2052 | May 2055 | May 2055 | Jan 2048 | Jun 2054 | Apr 2054 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jun 2054 | Oct 2044 | Jul 2052 | Apr 2045 | Oct 2051 | May 2045 | May 2039 | May 2055 | ND | Aug 2039 | May 2055 | Jul 2043 | May 2052 | May 2055 | May 2055 | May 2055 | May 2055 | Aug 2047 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | Nov 2036 | Oct 2040 | May 2055 | Mar 2050 | May 2055
+1 FT 6 IN
A |  | Year | Jun 2051 | Sep 2042 | Jun 2041 | ND | ND | May 2055 | Jul 2051 | Feb 2040 | May 2055 | May 2055 | Sep 2046 | May 2055 | ND | Mar 2045 | May 2055 | May 2055 | Apr 2041 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Apr 2052 | Mar 2050 | May 2047 | Mar 2054 | May 2036 | Mar 2049 | Sep 2034 | May 2055 | ND | ND | ND | May 2055 | Mar 2048 | May 2055 | May 2055 | ND | ND | ND | Mar 2043 | Jan 2052 | Sep 2041 | Apr 2046 | Feb 2039 | May 2052 | May 2055 | May 2055 | Jun 2041 | Mar 2036 | Oct 2039 | May 2055 | May 2055 | May 2055 | ND | ND | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | Jan 2052 | Nov 2035 | May 2055 | Sep 2037 | ND
0 REFERENCE
A | POSITION 'A' | Year | ND | May 2055 | ND | Jul 2052 | Oct 2040 | May 2055 | May 2055 | ND | ND | ND | Jan 2055 | Oct 2048 | May 2055 | May 2055 | May 2055 | Jan 2050 | ND | ND | Jul 2047 | May 2055 | Mar 2033 | Nov 2039 | May 2055 | Apr 2054 | ND | ND | ND | ND | ND | ND | ND | Apr 2051 | May 2055 | May 2055 | May 2055 | ND | May 2055 | Feb 2046 | Dec 2039 | Jun 2043 | May 2055 | May 2055 | ND | ND | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | Dec 2048 | ND | ND | May 2055 | May 2055 | Jun 2036 | Aug 2041 | Sep 2051 | May 2055 | ND | ND | May 2055 | Dec 2053 | ND | Jul 2040 | ND | ND | ND | ND
OF THE
SECONDARIES
A | POSITION 'B' | Year | ND | May 2055 | May 2055 | May 2054 | May 2055 | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2053 | ND | ND | Jan 2053 | May 2055 | May 2055 | May 2055 | May 2055 | Sep 2046 | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | Aug 2050 | ND | Jun 2049 | May 2052 | May 2055 | May 2055 | May 2055 | Nov 2052 | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | ND | Sep 2040 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | May 2055 | ND | ND
OF THE
SECONDARIES
A |  | Year | May 2055 | Jul 2050 | May 2055 | Feb 2050 | Oct 2047 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jul 2047 | May 2055 | Jun 2051 | May 2053 | Oct 2037 | Dec 2038 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jun 2030 | Jan 2039 | Oct 2046 | Apr 2036 | Apr 2054 | ND | ND | Apr 2041 | Oct 2042 | Aug 2047 | Mar 2038 | Oct 2039 | Mar 2048 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | Feb 2044 | Feb 2036 | May 2055 | ND | May 2052
-9 IN
A | POSITION 'C' | Year | ND | May 2055 | May 2055 | Sep 2041 | Feb 2042 | May 2055 | May 2055 | ND | ND | ND | May 2055 | May 2055 | Jul 2051 | May 2055 | May 2055 | Oct 2046 | ND | ND | Mar 2048 | May 2055 | Sep 2047 | Mar 2044 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | May 2055 | Feb 2053 | Oct 2047 | May 2055 | ND | May 2055 | Jun 2048 | May 2055 | Apr 2042 | Jul 2049 | Jul 2038 | ND | ND | ND | May 2055 | Aug 2042 | Aug 2046 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | Jul 2045 | Dec 2040 | Mar 2054 | May 2055 | ND | ND | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND
OF THE
SECONDARIES
A |  | Year | Mar 2047 | Aug 2040 | Dec 2052 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jun 2052 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | Aug 2051 | Jul 2047 | May 2055 | Jan 2045 | May 2055 | May 2055 | May 2055 | May 2055 | ND | Jan 2042 | ND | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | ND | ND | ND | May 2055 | ND | ND | May 2055 | ND | Aug 2043 | ND | ND | May 2055
-18 IN
A |  | Year | May 2055 | ND | ND | ND | ND | May 2055 | ND | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Sep 2041 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Aug 2043 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2045 | May 2055 | Mar 2048 | ND | May 2055 | May 2055 | May 2055 | May 2055 | Aug 2042 | ND | May 2055 | ND | May 2055 | May 2055 | ND | ND | ND | ND | May 2055 | ND | ND | May 2055 | ND | ND | ND | May 2055 | ND | Apr 2050 | ND
-27 IN
A |  | Year | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | May 2051 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2050 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | Feb 2048 | Jun 2051 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | ND
-36 IN
A |  | Year | ND | Jun 2045 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | Feb 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Sep 2052 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | Jul 2035 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Sep 2039 | May 2055 | May 2055 | May 2055 | ND | May 2038
-45 IN
A |  | Year | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | May 2055 | May 2055 | ND | May 2055 | ND | ND | May 2055 | ND | May 2055 | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | May 2055 | May 2055 | ND | ND | Jun 2046 | Aug 2050 | May 2055 | ND | May 2055
-54 IN
A | POSITION 'A' | Year | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | Apr 2046 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | Mar 2047 | ND | May 2055 | May 2055 | ND | Oct 2049 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | Jul 2049 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | Aug 2048 | Sep 2045 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | ND
OF THE
PRIMARIES
A | POSITION 'B' | Year | ND | ND | Dec 2037 | May 2055 | ND | Dec 2053 | May 2055 | ND | Mar 2053 | May 2055 | ND | Mar 2053 | May 2055 | ND | May 2055 | Jul 2040 | ND | May 2055 | May 2055 | ND | May 2055 | Aug 2048 | ND | May 2055 | Dec 2052 | ND | Jun 2051 | May 2055 | ND | Dec 2045 | May 2055 | ND | May 2055 | May 2055 | ND | Sep 2047 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | Nov 2048 | May 2055 | ND | ND
OF THE
PRIMARIES
A | POSITION 'C' | Year | ND | ND | Apr 2041 | May 2049 | ND | Oct 2051 | May 2055 | ND | Jan 2045 | Mar 2050 | ND | May 2055 | May 2055 | ND | May 2055 | Jan 2052 | ND | Nov 2054 | May 2055 | ND | Aug 2054 | Nov 2043 | ND | Apr 2051 | Mar 2048 | ND | Mar 2047 | Jun 2049 | ND | May 2055 | Sep 2053 | ND | Sep 2047 | May 2055 | ND | Feb 2048 | Aug 2054 | ND | May 2055 | Jan 2049 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | Sep 2054 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | ND | Jul 2051 | May 2055 | ND | ND
OF THE
PRIMARIES
A |  | Year | May 2055 | ND | Nov 2049 | Sep 2044 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | ND | May 2055 | Aug 2049 | May 2055 | May 2055 | ND | May 2055 | ND | ND | ND | ND | ND | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | ND | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | ND | ND | May 2055 | ND | ND | ND | May 2055 | ND | May 2055 | Feb 2036 | Jun 2049 | ND | ND | ND
-63 IN
A |  | Year | May 2055 | May 2055 | May 2055 | Mar 2040 | Jun 2048 | Jun 2052 | May 2055 | Dec 2052 | May 2055 | Jun 2051 | May 2055 | May 2055 | Apr 2033 | Nov 2049 | Dec 2036 | May 2055 | May 2055 | May 2055 | May 2055 | Oct 2042 | Mar 2049 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | Mar 2047 | May 2055 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Nov 2048 | Nov 2052 | ND | May 2055 | May 2055 | Feb 2050 | ND | ND | Oct 2041 | Jun 2040 | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | ND | ND | ND | ND | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | ND | ND
-72 IN
A |  | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Feb 2036 | Mar 2036 | Mar 2047 | Jun 2046 | May 2055 | Jan 2037 | May 2055 | May 2055 | May 2055 | Aug 2050 | May 2055 | Mar 2053 | May 2055 | May 2055 | May 2045 | Aug 2044 | May 2055 | Mar 2044 | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Apr 2050 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | Mar 2055 | ND | ND | Aug 2043 | May 2055 | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | ND | ND | May 2055 | ND | May 2055 | Feb 2037 | May 2055 | Jan 2053 | Aug 2036 | ND
-81 IN
A |  | Year | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | Jun 2047 | May 2055 | Oct 2049 | May 2055 | May 2055 | May 2055 | Nov 2049 | Jul 2038 | May 2055 | May 2055 | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | May 2055 | ND | May 2055 | May 2055 | Feb 2054 | Apr 2050 | Mar 2042 | Jul 2037 | Jan 2046 | May 2055 | ND
-90 IN
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69
| PROJECTED TO REACH TMIN: |  | 10: NOTE: CORROSION RATE IS BASED ON COMPARISON OF; 30: EARLIEST DATE OF PROJECTED RETIREMENT:; 67: APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | + 5 YEARS (or no data)
| WITHIN 5 YEARS |  | 10: 2020, 2022, 2023, 2024, 2025 | PROJECTED TUBE RETIREMENT DATE
| WITHIN 3 YEARS |  | 10: INSPECTION DATA; 30: October 2029
| WITHIN 1 YEAR |  | 10: ND; 15: NO COMPARISON DATA
RETIREMENT
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Low (hidden)
OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. LOW THICKNESS MEASUREMENTS ARE IN INCHES. | [72 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MIN
A |  | LOWEST | bar: 1; 69
0.083 | +16 FT 6 IN
A |  | LOWEST | bar: 69
0.083 | +15 FT
A |  | LOWEST
0.083 | +13 FT 6 IN
A |  | LOWEST
0.083 | +12 FT
A | POSITION 'A' | LOWEST
0.083 | OF THE
OB PORTS
A | POSITION 'B' | LOWEST
0.083 | OF THE
OB PORTS
A | POSITION 'C' | LOWEST
0.083 | OF THE
OB PORTS
A |  | LOWEST
0.083 | +10 FT 6 IN
A |  | LOWEST
0.083 | +9 FT
A | POSITION 'A' | LOWEST
0.083 | OF THE
OSCILLATOR
A | POSITION 'B' | LOWEST
0.083 | OF THE
OSCILLATOR
A | POSITION 'C' | LOWEST
0.083 | OF THE
OSCILLATOR
A | POSITION 'D' | LOWEST
0.083 | OF THE
OSCILLATOR
A | POSITION 'E' | LOWEST
0.083 | OF THE
OSCILLATOR
A |  | LOWEST
0.083 | +7 FT 6 IN
A |  | LOWEST
0.083 | +6 FT
A |  | LOWEST
0.083 | +4 FT 6 IN
A |  | LOWEST
0.083 | +3 FT
A |  | LOWEST
0.083 | +1 FT 6 IN
A |  | LOWEST
0.083 | 0 REFERENCE
A | POSITION 'A' | LOWEST
0.083 | OF THE
SECONDARIES
A | POSITION 'B' | LOWEST
0.083 | OF THE
SECONDARIES
A |  | LOWEST
0.083 | -9 IN
A | POSITION 'C' | LOWEST
0.083 | OF THE
SECONDARIES
A |  | LOWEST
0.083 | -18 IN
A |  | LOWEST
0.083 | -27 IN
A |  | LOWEST
0.083 | -36 IN
A |  | LOWEST
0.083 | -45 IN
A |  | LOWEST
0.083 | -54 IN
A | POSITION 'A' | LOWEST
0.083 | OF THE
PRIMARIES
A | POSITION 'B' | LOWEST
0.083 | OF THE
PRIMARIES
A | POSITION 'C' | LOWEST
0.083 | OF THE
PRIMARIES
A |  | LOWEST
0.083 | -63 IN
A |  | LOWEST
0.083 | -72 IN
A |  | LOWEST | bar: 1 to 11
0.083 | -81 IN
A |  | LOWEST | bar: 1 to 34
0.083 | -90 IN
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | AVG | MIN
A | 0.001-0.083 | 0.131-0.140 | 10: OUTSIDE DIAMETER:; 23: 3; 30: INSPECTION RESULTS; 67: APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
LEGEND | 0.084-0.100 | 0.141-0.150 | 10: TUBE MATERIAL:; 23: SA-210A1; 35: MAX. THICKNESS
| 0.101-0.110 | 0.151-0.160 | 10: NOMINAL WALL:; 23: 0.203; 35: AVG. THICKNESS |  |  | TUBE WALL THICKNESS SURVEY (LOW VALUE)
| 0.111-0.120 | 0.161-0.170 | 10: ASME MIN:; 23: 0.083; 35: MIN. THICKNESS
| 0.121-0.130 | 0.171-0.999 | 10: MILL FLAG:; 23: 0.1; 35: STD DEV.
LOW THICKNESS
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com